## Sheet1
Schedule for the work "Shifting of 17Nos 33 kV spun poles, 44Nos 11 kV poles, 3Nos LT Poles,2 No.11 kV line AB switch,27Nos DTRS& AB switches,6 Nos HT Services at Gachibowli junction to kondapur roadside under GHMC flyover construction program in WCGH division of Master plan Ranga Reddy circle under DC works."
1. D.No :LR NO..CGM/MP/GR.HYD/F.NO./D.NO. /DT. .02.2023
2. WBS No. G-2022-13-04-01-01-001
Sl.No | Estimate Quantity(Only Figures) | PARTICULARS | Work Type | Item Short Description | SWR No/APSS/Morth cl.No | Rate (INR) (Upto 2 Decimals) | UOM | Amount
Activity No : 30 Activity Description : 33kV Labour
1 | 2 | Supply of M+3 Tower (Galvanized) | Elecy | Supply | SMR11683 | 140674.3 | EA | 281348.6
2 | 4 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) | Elecy | Supply | SMR11684 | 28520.64 | EA | 114082.56
3 | 2 | Erection of M+3 Tower (Galvanized) | Elecy | Labour | SWR11850 | 64576 | EA | 129152
4 | 4 | Erection and Extension of 3Mtrs for M+3 (Galvanized) | Elecy | Labour | SWR11851 | 5067.6 | EA | 20270.4
5 | 9.44 | Earth work excavtion hard rock boulders <3cum Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) (other than SS) | Elecy | Labour | SWR10856 | 1292.5 | M3 | 12201.2
6 | 8 | Straight through joint 33kv 3x400 xlpe | Elecy | Labour | SWR10382 | 5589 | EA | 44712
7 | 1160 | Laying of 2nd Cable in Excavated Trench Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) | Elecy | Labour | SWR10988 | 200.1 | M | 232116
8 | 17 | Dismantling of Spun poles 11 Mtrs PSCC Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc. | Elecy | Labour | SWR11327 | 2112.5 | EA | 35912.5
9 | 0.85 | Dismantling of 100 Sqmm conductor SC | Elecy | Labour | SWR22063 | 8112.51 | KM | 6895.6335
10 | 1160 | Laying of DR 33KV 3x400sqmm UG Cb HG/BC/CC/BT Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. including Video shoot of cable laying works which demonstrate the UG cable trench depth and jointing works, GIS cooridinates and tagging of strating of cable, joints of cable and ending of cable. Auto CAD drawings of cable path is to be maintained and Smart RFID Markers (The Permanent marking system) at starting point, ending point and at joint if any as per field (The Permanent marking system) for Under Ground cables to identify the cable path at the time of repair/maintainance. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC. | Elecy | Labour | SWR11972 | 734.31 | M | 851799.6
11 | 6 | Making of Outdoor/Indoor End Termination-33 KV 3x400 Sqmm Cable | Elecy | Labour | SWR10387 | 2710.55 | EA | 16263.3
12 | 30 | Raising of SR 33KV 3x400sqmm UG Cb on support Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elecy | Labour | SWR11954 | 133 | M | 3990
13 | 1 | Formation of Cut point for 33 KV Single Circuit line excluding pole erection and stays | Elecy | Labour | SWR10981 | 1756 | EA | 1756
14 | 7 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Labour | SWR11230 | 1024 | DR | 7168
15 | 7 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Labour | SWR11231 | 1024 | DR | 7168
16 | 4 | Transport of Cond Drum,VCBs >10 & <20Km Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 10 Km and upto 20 Km with Lorry for each trip | Elecy | Labour | SWR11861 | 3235 | EA | 12940
17 | 15 | Supply and Erection of Smart RFID marker | Elecy | Labour | SWR25089 | 2745 | EA | 41175
Schedule Amount SubTotal 1 | [7 empty] | 1818950.7935
Activity No : 40 Activity Description : 11kV Labour
Sl.No | Estimate Quantity(Only Figures) | PARTICULARS | Work Type | Item Short Description | SWR No/APSS/Morth cl.No | Rate (INR) (Upto 2 Decimals) | UOM | Amount
1 | 200 | Lay-DR 11KV 3x300sqmm UG Cb HG/BC/CC/BT Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. including Video shoot of cable laying works which demonstrate the UG cable trench depth and jointing works, GIS cooridinates and tagging of strating of cable, joints of cable and ending of cable. Auto CAD drawings of cable path is to be maintained and Smart RFID Markers (The Permanent marking system) at starting point, ending point and at joint if any as per field (The Permanent marking system) for Under Ground cables to identify the cable path at the time of repair/maintainance. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC | Elecy | Labour | SWR11973 | 618.69 | M | 123738
2 | 200 | Laying of 2nd Cable in Excavated Trench. Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) | Elecy | Labour | SWR10988 | 200.1 | M | 40020
3 | 30 | Raise-DR 11KV 3x300sqmm UG Cb on support Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elecy | Labour | SWR12005 | 270 | M | 8100
4 | 120 | Raise-SR 11KV 3x300sqmm UG Cb on support Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elecy | Labour | SWR11955 | 141.25 | M | 16950
5 | 200 | Lay-SR 11KV 3x300sqmm UG Cb HG/BC/CC/BT Excavation & laying of UG Cable in Single Run. Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. including Video shoot of cable laying works which demonstrate the UG cable trench depth and jointing works, GIS cooridinates and tagging of strating of cable, joints of cable and ending of cable. Auto CAD drawings of cable path is to be maintained and Smart RFID Markers (The Permanent marking system) at starting point, ending point and at joint if any as per field (The Permanent marking system) for Under Ground cables to identify the cable path at the time of repair/maintainance. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road with 11 KV 3x300 Sqmm Cable. | Elecy | Labour | SWR11919 | 456.33 | M | 91266
6 | 6 | Making of Straight through joint 11kv 3x300 xlpe | Elecy | Labour | SWR10386 | 3652.4 | EA | 21914.4
7 | 34 | Making of Outdoor/Indoor End Termination end termination 11kv 3x300 xlpe | Elecy | Labour | SWR10391 | 2324.15 | EA | 79021.1
8 | 900 | Fabrication of materials including 2 coats of Red oxide painting. Fabrication of Back clamps with 50 x 6 mm MS Flat. | Elecy | Labour | SWR10320 | 15 | EA | 13500
9 | 900 | Labour for Fixing of all types of clamps | Elecy | Labour | SWR10917 | 65 | EA | 58500
10 | 500 | Supply of MS bolts & nuts and washers etc of all sizes | Elecy | Supply | SMR11487 | 91.25 | KG | 45625
11 | 140 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elecy | Labour | SWR10642 | 502.5 | EA | 70350
12 | 70 | Erection of 9/10/11Meter Box pole Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. Box pole 9/10/11 Mtr | Elecy | Labour | SWR11266 | 2591.99 | EA | 181439.3
13 | 70 | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') Excavation of pits in all soils except hard rock requiring blasting 8.0Mtrs PSCC Poles - 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | Elecy | Labour | SWR10105 | 474 | EA | 33180
14 | 73.5 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. including the cost of cement | Elecy | Labour | SWR10356 | 6450 | M3 | 474075
15 | 33 | Erection of AB Switch and aligment complete. RCC Column type DTR Plinth of size 1'X1'X13',topslab 5'x9'x9" & beam size 5'X9'X9" above 160KVA | Elecy | Labour | SWR21844 | 24600 | EA | 811800
16 | 33 | Erection of Three Phase DTRs Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc. Erection of 3 Ph DTRs upto 25KVA | Elecy | Labour | SWR10463 | 1117.6 | EA | 36880.8
17 | 33 | Supply of 11kV HG Fuse set | Elecy | Supply | SMR11608 | 1733.75 | SET | 57213.75
18 | 33 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elecy | Labour | SWR20102 | 1777.94 | EA | 58672.02
19 | 33 | Erection of 11 KV HG Fuse set including earthing | Elecy | Labour | SWR10395 | 726 | SET | 23958
20 | 27 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Elecy | Labour | SWR10674 | 1563.41 | EA | 42212.07
21 | 33 | Painting of Name Plates for any equipment | Elecy | Labour | SWR10963 | 122 | EA | 4026
22 | 27 | Erection of CT operated meters for LV side of Distribution Transformers. Erection & commissioning of CT meter along with box on LV side of DTRs including cable connections from Transformer LV to Distribution box via CT meters box | Elecy | Labour | SWR10336 | 900 | EA | 24300
23 | 6 | Construction of Plinth for 11kv CTPT 0.6x0.6x2.89m | Elecy | Labour | SWR10733 | 6760 | EA | 40560
24 | 6 | Erection of 11kv CTPT set including jumpering | Elecy | Labour | SWR10420 | 1138 | EA | 6828
25 | 6 | Arranging for Re-Commissioning of CTPT Set including alinment of GI pipe, wiring and testing | Elecy | Labour | SWR11120 | 131 | EA | 786
26 | 3 | Erection of AB Switch and aligment complete. Erection of 11KV 800A double throw AB Switches | Elecy | Labour | SWR21277 | 2134 | EA | 6402
27 | 1120 | Laying of 1Core XLPE 120Sqmm Cable | Elecy | Labour | SWR22356 | 20 | M | 22400
28 | 600 | Supply of 120 Sqmm Aluminium lugs | Elecy | Supply | SMR40132 | 12.52 | EA | 7512
29 | 39 | Dismantling of DTR plinth (Column type) | Elecy | Labour | SWR20070 | 1968.75 | EA | 76781.25
30 | 6 | Dismantling of CTPT Set | Elecy | Labour | SWR22165 | 490 | EA | 2940
31 | 30 | Dismantling of Box pole 9/10/11 Mtr | Elecy | Labour | SWR11329 | 1130 | EA | 33900
32 | 1.64 | Dismantling of 11kV 34/ 55 Sqmm SC | Elecy | Labour | SWR22065 | 4419 | KM | 7247.16
33 | 33 | Dismantling of 11kv TT type AB switch | Elecy | Labour | SWR12172 | 872.28 | EA | 28785.24
34 | 2 | Dismantling of 11KV Line AB switch. | Elecy | Labour | SWR12177 | 981.25 | EA | 1962.5
35 | 33 | Dismantling of 11 KV HG fuse set including earthing | Elecy | Labour | SWR11745 | 346.5 | SET | 11434.5
36 | 0.5 | Dismantling of 11KV AB Cable 3x185+70Sqmm | Elecy | Labour | SWR12161 | 18600 | KM | 9300
37 | 0.34 | Dismantling of LT AB Cable 3x70+1x16+1x50 | Elecy | Labour | SWR12156 | 9050 | KM | 3077
38 | 8 | Dismantle-8.0 m long PSCC pole Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc. | Elecy | Labour | SWR11319 | 491.7 | EA | 3933.6
39 | 44 | Dismantle-9.1 M long PSCC pole Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc. | Elecy | Labour | SWR11320 | 929.5 | EA | 40898
40 | 1 | Transport of Cond Drum,VCBs >10 & <20Km Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space)(excluding of loading unloading). Above 10 Km and upto 20 Km with Lorry for each trip. | Elecy | Labour | SWR11861 | 3235 | EA | 3235
41 | 1 | LOADING of Conductor drums | Elecy | Labour | SWR10191 | 202 | EA | 202
42 | 1 | UNLOADING of Conductor drums | Elecy | Labour | SWR10509 | 100 | EA | 100
43 | 1 | Transport of Cond Drum,VCBs >10 & <20Km Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space)(excluding of loading unloading). Above 10 Km and upto 20 Km with Lorry for each trip. | Elecy | Labour | SWR11861 | 3235 | EA | 3235
44 | 45 | Straight through joints of AB cable (each lead). Supply and erection of Straight line Asmbly kits | Elecy | Labour | SWR10672 | 1661 | EA | 74745
45 | 65 | Straight through joints of AB cable (each lead). Supply and erection of Angle line Assembly kits | Elecy | Labour | SWR10673 | 2124 | EA | 138060
46 | 110 | Supply of Suspension Clamp Assembly & Eye Hook-M | Elecy | Supply | SMR11492 | 65 | EA | 7150
47 | 2.2 | Stringing of HT AB cable 11 KV 3x185+70 Sqmm | Elecy | Labour | SWR10454 | 41055 | KM | 90321
48 | 1 | Stringing of LT AB cable 3x70 + 1x16 + 1x50 SQmm | Elecy | Labour | SWR10666 | 8450 | KM | 8450
49 | 270 | End Termination of AB cable (each lead) 120 Sqmm to 185 Sqmm Supply of 11KV 3x185+70sq.mm/ 3x70+70sq.mm/3x35+35sq.mm AB cable end Kits | Elecy | Supply | SMR11504 | 950 | SET | 256500
50 | 270 | End Termination of AB cable (each lead) 120 Sqmm to 185 Sqmm | Elecy | Labour | SWR10667 | 800 | EA | 216000
51 | 35 | Supply and erection of T-Branch kit | Elecy | Labour | SWR24971 | 3215 | EA | 112525
52 | 33 | Earth-11KV 3x185+1x75 AB Cb-GIStrip&Pipe | Elecy | Labour | SWR20612 | 500 | EA | 16500
53 | 1170 | Supply & Running 25x6mm GI Strip for Earthing | Elecy | Labour | SWR34252 | 110 | M | 128700
54 | 117 | ERECT. OF LINES-Providing of earthing Providing of Earthing. Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elecy | Labour | SWR10357 | 1210 | EA | 141570
55 | 117 | ERECT. OF LINES-Providing of RCC collar Providing of RCC collar to earth pit. Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elecy | Labour | SWR10359 | 386 | EA | 45162
56 | 117 | Supply&Erec of CI earth Pipe as APTRANCO Providing of earthing with various types of earth electrodes. Excavation of earth pit, supply of cast iron pipe with flange on one end (as per ISS7181/86) of nominal dia 125mm and 2.75 meters long in side the pit including supply and fixing RCC collars 0.75 meter dia (OD), 50mm thick and 0.60meters long complete as per APTRANSCO standards | Elecy | Labour | SWR10924 | 9804 | EA | 1147068
57 | 140 | LOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10204 | 76 | EA | 10640
58 | 140 | UNLOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10522 | 50 | EA | 7000
59 | 11.025 | TRANSPORT OF STEEL MATERIAL 10 TO 20KM Transport of steel including line materials such as cross arms, clamps, hardware, cable (loose) and other line materials (Including loading and unloading). Above 10 KM and upto 20 KM. | Elecy | Labour | SWR10148 | 472 | TO | 5203.8
60 | 108 | Running of 11KV jumper from Line, AB switch, HG Fuse set to DTR for 3-Phases | Elecy | Labour | SWR10407 | 412.5 | EA | 44550
61 | 99 | Removing and providing of jumpers in SS. | Elecy | Labour | SWR20785 | 64 | LS | 6336
62 | 4 | Loading of 11 KV AB Cable (XLPE) Single core upto 100 Mts. Drum (including Accessories) | Elecy | Labour | SWR12414 | 293 | DR | 1172
63 | 4 | Un loading of 11 KV AB Cable (XLPE) Single core upto 100 Mts. Drum (including Accessories) | Elecy | Labour | SWR12432 | 145 | DR | 580
64 | 2 | Transport of Cond Drum,VCBs >10 & <20Km Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space)(excluding of loading unloading). Above 10 Km and upto 20 Km with Lorry for each trip. | Elecy | Labour | SWR11861 | 3235 | EA | 6470
65 | 2 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Labour | SWR11230 | 1024 | DR | 2048
66 | 2 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Labour | SWR11231 | 1024 | DR | 2048
67 | 1 | Transport of Cond Drum,VCBs >10 & <20Km Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space)(excluding of loading unloading). Above 10 Km and upto 20 Km with Lorry for each trip. | Elecy | Labour | SWR11861 | 3235 | EA | 3235
68 | 35 | TRANSPORT OF STEEL 10 TO 20KM Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 404 | TO | 14140
69 | 0.672 | LOADING of ACSR conductor scrap | Elecy | Labour | SWR10257 | 491 | TO | 329.952
70 | 0.672 | UNLOADING of ACSR conductor scrap | Elecy | Labour | SWR10575 | 491 | TO | 329.952
71 | 9.525 | LOADING of MS Scrap | Elecy | Labour | SWR10258 | 578 | TO | 5505.45
72 | 9.525 | UNLOADING of MS Scrap | Elecy | Labour | SWR10576 | 578 | TO | 5505.45
73 | 36.5 | Sup Material for 1st coat Al. Painting. Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of substation structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elecy | Supply | SMR40009 | 2181 | TO | 79606.5
74 | 36.5 | Sup Material for 2nd coat Al. Painting. Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of substation structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elecy | Labour | SMR40010 | 1293 | TO | 47194.5
75 | 36.5 | Labour for 1st coat Al. Painting. Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of substation structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elecy | Labour | SWR10877 | 851 | TO | 31061.5
76 | 36.5 | Labour for 2nd coat Al. Painting. Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of substation structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium | Elecy | Labour | SWR10879 | 482 | TO | 17593
Schedule Amount SubTotal 2 | [7 empty] | 5301560.794
|  | Schedule Amount SubTotal 1 | 1818950.7935
|  | Schedule Amount SubTotal 2 | 5301560.794
|  | Total Schedule Amount | 7120511.5875

## Sheet2
S.No | Services Code | Services Text | Item Catagory | Quantity | Unit | Rate in Rs. | Amount in Rs.
1 | SMR11683 | S-M+3 Tower GALV | - | 2 | EA | 140674.3 | 281348.6
2 | SMR11684 | S-Mat. for Extn of M+3 Tower by 3M GALV | - | 4 | EA | 28520.64 | 114082.56
3 | SWR11850 | Erect- M+3 Tower GALV | - | 2 | EA | 64576 | 129152
4 | SWR11851 | Erect-Extn of 3M for M+3 Tower GALV | - | 4 | EA | 5067.6 | 20270.4
5 | SWR10856 | Earth work excav hard rock bould <3cum | - | 9.44 | M3 | 1292.5 | 12201.2
6 | SWR10382 | Straight through joint 33kv 3x400 xlpe | - | 8 | EA | 5589 | 44712
7 | SWR10988 | Lay-2nd Cable in Excavated Trench | - | 1160 | M | 200.1 | 232116
8 | SWR11327 | Dismantle-Spun poles 11 Mtrs PSCC | - | 17 | EA | 2112.5 | 35912.5
9 | SWR22063 | Dismantling of 100 Sqmm conductor SC | - | 0.85 | KM | 8112.51 | 6895.63
10 | SWR11972 | Lay-DR 33KV 3x400sqmm UG Cb HG/BC/CC/BT | - | 1160 | M | 734.31 | 851799.6
11 | SWR10387 | OD/Idoor end termination 33kv 3x400 xlpe | - | 6 | EA | 2710.55 | 16263.3
12 | SWR11954 | Raise-SR 33KV 3x400sqmm UG Cb on support | - | 30 | M | 133 | 3990
13 | SWR10981 | Horizontal Cut point for 33 KV line | - | 1 | EA | 1756 | 1756
14 | SWR11230 | Load-11/33KV XLPE UG Cable for all sizes | - | 7 | DR | 1024 | 7168
15 | SWR11231 | Unload-11/33KV XLPE UG Cable all sizes | - | 7 | DR | 1024 | 7168
16 | SWR11861 | Transport of Cond Drum,VCBs >10 & <20Km | - | 4 | EA | 3235 | 12940
17 | SWR25089 | S&E-Smart RFID marker | - | 15 | EA | 2745 | 41175
Service Cost | [6 empty] | 1818950.79
GST 18% | [6 empty] | 327411.14
3 % S & H Charges : | [6 empty] | 0
3 % Contingencies on materials: | [6 empty] | 0
10 % Estt. & General Charges : | [6 empty] | 0
Total : | [6 empty] | 2146361.93

## Sheet3
S.No | Services Code | Services Text | Item Catagory | Quantity | Unit | Rate in Rs. | Amount in Rs.
1 | SWR11973 | Lay-DR 11KV 3x300sqmm UG Cb HG/BC/CC/BT | - | 200 | M | 618.69 | 123738
2 | SWR10988 | Lay-2nd Cable in Excavated Trench | - | 200 | M | 200.1 | 40020
3 | SWR12005 | Raise-DR 11KV 3x300sqmm UG Cb on support | - | 30 | M | 270 | 8100
4 | SWR11955 | Raise-SR 11KV 3x300sqmm UG Cb on support | - | 120 | M | 141.25 | 16950
5 | SWR11919 | Lay-SR 11KV 3x300sqmm UG Cb HG/BC/CC/BT | - | 200 | M | 456.33 | 91266
6 | SWR10386 | Straight through joint 11kv 3x300 xlpe | - | 6 | EA | 3652.4 | 21914.4
7 | SWR10391 | OD/Idoor end termination 11kv 3x300 xlpe | - | 34 | EA | 2324.15 | 79021.1
8 | SWR10320 | Fab Back clamps with 50 x 6 mm MS Flat | - | 900 | EA | 15 | 13500
9 | SWR10917 | Labour for Fixing of all types of clamps | - | 900 | EA | 65 | 58500
10 | SMR11487 | S-MS Bolts & Nuts,Washers etc., | - | 500 | KG | 91.25 | 45625
11 | SWR10642 | Fabrication of 175x85/150x75mm RS joist | - | 140 | EA | 502.5 | 70350
12 | SWR11266 | Erection of 9/10/11Meter Box pole | - | 70 | EA | 2591.99 | 181439.3
13 | SWR10105 | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | - | 70 | EA | 474 | 33180
14 | SWR10356 | Mass concreting of supports incl. cement | - | 73.5 | M3 | 6450 | 474075
15 | SWR21844 | Column type DTR Plinth topslab 5'x5'x6" | - | 33 | EA | 24600 | 811800
16 | SWR10463 | Erection of Three Phase DTRs | - | 33 | EA | 1117.6 | 36880.8
17 | SMR11608 | S-11KV HG Fuse Set | - | 33 | SET | 1733.75 | 57213.75
18 | SWR20102 | Erection of 11kv TT type AB switch | - | 33 | EA | 1777.94 | 58672.02
19 | SWR10395 | Erect. of 11kv HG Fuseset incl earthing | - | 33 | SET | 726 | 23958
20 | SWR10674 | Erection of LT distribution box | - | 27 | EA | 1563.41 | 42212.07
21 | SWR10963 | Painting of Name Plates for any equipmen | - | 33 | EA | 122 | 4026
22 | SWR10336 | Erection of CT meter on LV side of DTRs | - | 27 | EA | 900 | 24300
23 | SWR10733 | Con of Plinth for 11kvCTPT 0.6x0.6x2.89m | - | 6 | EA | 6760 | 40560
24 | SWR10420 | Erection of 11kv CTPT set incl jumpering | - | 6 | EA | 1138 | 6828
25 | SWR11120 | Re-Commissioning of CTPT Set | - | 6 | EA | 131 | 786
26 | SWR21277 | Ere 11KV 800A double throw AB Switches | - | 3 | EA | 2134 | 6402
27 | SWR22356 | Laying of 1Core XLPE 120Sqmm Cable | - | 1120 | M | 20 | 22400
28 | SMR40132 | Supply of 120 Sqmm Aluminium lugs | - | 600 | EA | 12.52 | 7512
29 | SWR20070 | Dismantling of DTR plinth | - | 39 | EA | 1968.75 | 76781.25
30 | SWR22165 | Dismantling of CTPT Set | - | 6 | EA | 490 | 2940
31 | SWR11329 | Dismantle-Box pole 9/10/11 Mtr | - | 30 | EA | 1130 | 33900
32 | SWR22065 | Dismantling of 11kV 34/ 55 Sqmm SC | - | 1.64 | KM | 4419 | 7247.16
33 | SWR12172 | Dismantle-11KV AB Switch TT Type | - | 33 | EA | 872.28 | 28785.24
34 | SWR12177 | Dismantle-11KV Line AB Switch | - | 2 | EA | 981.25 | 1962.5
35 | SWR11745 | Dimantle-11KV HG Fuse Set incl earthing | - | 33 | SET | 346.5 | 11434.5
36 | SWR12161 | Dismantle-11KV AB Cb 3x185+70Sqmm | - | 0.5 | KM | 18600 | 9300
37 | SWR12156 | Dismantle-LT AB Cb 3x70+1x16+1x50 | - | 0.34 | KM | 9050 | 3077
38 | SWR11319 | Dismantle-8.0 m long PSCC pole | - | 8 | EA | 491.7 | 3933.6
39 | SWR11320 | Dismantle-9.1 M long PSCC pole | - | 44 | EA | 929.5 | 40898
40 | SWR11861 | Transport of Cond Drum,VCBs | - | 1 | EA | 3235 | 3235
>10 & <20Km
41 | SWR10191 | LOADING of Conductor drums | - | 1 | EA | 202 | 202
42 | SWR10509 | UNLOADING of Conductor drums | - | 1 | EA | 100 | 100
43 | SWR11861 | Transport of Cond Drum,VCBs | - | 1 | EA | 3235 | 3235
>10 & <20Km
44 | SWR10672 | Supply and ere Straight line Asmbly kits | - | 45 | EA | 1661 | 74745
45 | SWR10673 | Supply and ere Angle line Asmbly kits | - | 65 | EA | 2124 | 138060
46 | SMR11492 | S-Suspension Clamp Assembly & Eye Hook-M | - | 110 | EA | 65 | 7150
47 | SWR10454 | Stringing of AB cbl 11 KV 3x185+70 Sqmm | - | 2.2 | KM | 41055 | 90321
48 | SWR10666 | Stringing of AB cable 3x70 + 1x16 + 1x50 | - | 1 | KM | 8450 | 8450
49 | SMR11504 | S-of 11KV AB cable end kits | - | 270 | SET | 950 | 256500
50 | SWR10667 | End Termnatn of AB cable 120 to 185 Sqmm | - | 270 | EA | 800 | 216000
51 | SWR24971 | S&Erect-T-Branch kit | - | 35 | EA | 3215 | 112525
52 | SWR20612 | Earth-11KV 3x185+1x75 AB | - | 33 | EA | 500 | 16500
Cb-GIStrip&Pipe
53 | SWR34252 | S&R 25x6mm GI Strip for | - | 1170 | M | 110 | 128700
Earthing
54 | SWR10357 | ERECT. OF LINES-Providing of earthing | - | 117 | EA | 1210 | 141570
55 | SWR10359 | ERECT. OF LINES-Providing of RCC collar | - | 117 | EA | 386 | 45162
56 | SWR10924 | Supply&Erec of CI earth Pipe as APTRANCO | - | 117 | EA | 9804 | 1147068
57 | SWR10204 | LOADING of R.S. Joists 175 x 85 mm | - | 140 | EA | 76 | 10640
58 | SWR10522 | UNLOADING of R.S. Joists 175 | - | 140 | EA | 50 | 7000
x 85 mm
59 | SWR10148 | TRANSPORT OF STEEL MATERIAL 10 TO 20KM | - | 11.025 | TO | 472 | 5203.8
60 | SWR10407 | Running of 11kv jumpering to AB switch.. | - | 108 | EA | 412.5 | 44550
61 | SWR20785 | Removing and making the jumpers. | - | 99 | LS | 64 | 6336
62 | SWR12414 | LOADING of 11 KV AB Cable (XLPE) 1 Core | - | 4 | DR | 293 | 1172
63 | SWR12432 | UNLOADING of 11 KV AB | - | 4 | DR | 145 | 580
Cable (XLPE) 1 Cor
64 | SWR11861 | Transport of Cond Drum,VCBs | - | 2 | EA | 3235 | 6470
>10 & <20Km
65 | SWR11230 | Load-11/33KV XLPE UG Cable for all sizes | - | 2 | DR | 1024 | 2048
66 | SWR11231 | Unload-11/33KV XLPE UG Cable all sizes | - | 2 | DR | 1024 | 2048
67 | SWR11861 | Transport of Cond Drum,VCBs | - | 1 | EA | 3235 | 3235
>10 & <20Km
68 | SWR10132 | TRANSPORT OF STEEL 10 TO 20KM | - | 35 | TO | 404 | 14140
69 | SWR10257 | LOADING of ACSR conductor scrap | - | 0.672 | TO | 491 | 329.95
70 | SWR10575 | UNLOADING of ACSR | - | 0.672 | TO | 491 | 329.95
conductor scrap
71 | SWR10258 | LOADING of MS Scrap | - | 9.525 | TO | 578 | 5505.45
72 | SWR10576 | UNLOADING of MS Scrap | - | 9.525 | TO | 578 | 5505.45
73 | SMR40009 | Sup Material for 1st coat Al. Painting. | - | 36.5 | TO | 2181 | 79606.5
74 | SMR40010 | Sup Material for 2nd coat Al. Painting. | - | 36.5 | TO | 1293 | 47194.5
75 | SWR10877 | Labour for 1st coat Al. Painting. | - | 36.5 | TO | 851 | 31061.5
76 | SWR10879 | Labour for 2nd coat Al. Painting. | - | 36.5 | TO | 482 | 17593
Service Cost | [6 empty] | 5301560.79
GST 18% | [6 empty] | 954280.94
3 % S & H Charges : | [6 empty] | 0

## total schedule
Schedule for the work "Shifting of 17Nos 33 kV spun poles, 44Nos 11 kV poles, 3Nos LT Poles,2 No.11 kV line AB switch,27Nos DTRS& AB switches,6 Nos HT Services at Gachibowli junction to kondapur roadside under GHMC flyover construction program in WCGH division of Master plan Ranga Reddy circle under DC works."
1.Memo NO.CGM/MP/GR.HYD/F.NO./D.NO.2203 /DT.16 .02.2023
2. WBS No. G-2022-13-04-01-01-001
Sl.No | Estimate Quantity(Only Figures) | PARTICULARS | Work Type | Item Short Description | SWR No/APSS/Morth cl.No | Rate (INR) (Upto 2 Decimals) | UOM | Amount
1 | 2 | Supply of M+3 Tower (Galvanized) | Elecy | Supply | SMR11683 | 140674.3 | EA | 281348.6
2 | 4 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) | Elecy | Supply | SMR11684 | 28520.64 | EA | 114082.56
3 | 2 | Erection of M+3 Tower (Galvanized) | Elecy | Labour | SWR11850 | 64576 | EA | 129152
4 | 4 | Erection and Extension of 3Mtrs for M+3 (Galvanized) | Elecy | Labour | SWR11851 | 5067.6 | EA | 20270.4
5 | 9.44 | Earth work excavtion hard rock boulders <3cum Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) (other than SS) | Elecy | Labour | SWR10856 | 1292.5 | M3 | 12201.2
6 | 8 | Straight through joint 33kv 3x400 xlpe | Elecy | Labour | SWR10382 | 5589 | EA | 44712
7 | 1160 | Laying of 2nd Cable in Excavated Trench Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) | Elecy | Labour | SWR10988 | 200.1 | M | 232116
8 | 17 | Dismantling of Spun poles 11 Mtrs PSCC Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc. | Elecy | Labour | SWR11327 | 2112.5 | EA | 35912.5
9 | 0.85 | Dismantling of 100 Sqmm conductor SC | Elecy | Labour | SWR22063 | 8112.51 | KM | 6895.6335
10 | 1160 | Laying of DR 33KV 3x400sqmm UG Cb HG/BC/CC/BT: Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. including Video shoot of cable laying works which demonstrate the UG cable trench depth and jointing works, GIS cooridinates and tagging of strating of cable, joints of cable and ending of cable. Auto CAD drawings of cable path is to be maintained and Smart RFID Markers (The Permanent marking system) at starting point, ending point and at joint if any as per field (The Permanent marking system) for Under Ground cables to identify the cable path at the time of repair/maintainance. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC. | Elecy | Labour | SWR11972 | 734.31 | M | 851799.6
11 | 6 | Making of Outdoor/Indoor End Termination-33 KV 3x400 Sqmm Cable | Elecy | Labour | SWR10387 | 2710.55 | EA | 16263.3
12 | 30 | Raising of SR 33KV 3x400sqmm UG Cb on support: Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elecy | Labour | SWR11954 | 133 | M | 3990
13 | 1 | Formation of Cut point for 33 KV Single Circuit line excluding pole erection and stays | Elecy | Labour | SWR10981 | 1756 | EA | 1756
14 | 7 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Labour | SWR11230 | 1024 | DR | 7168
15 | 7 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Labour | SWR11231 | 1024 | DR | 7168
16 | 4 | Transport of Cond Drum,VCBs >10 & <20Km: Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 10 Km and upto 20 Km with Lorry for each trip | Elecy | Labour | SWR11861 | 3235 | EA | 12940
17 | 15 | Supply and Erection of Smart RFID marker | Elecy | Labour | SWR25089 | 2745 | EA | 41175
18 | 200 | Lay-DR 11KV 3x300sqmm UG Cb HG/BC/CC/BT: Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. including Video shoot of cable laying works which demonstrate the UG cable trench depth and jointing works, GIS cooridinates and tagging of strating of cable, joints of cable and ending of cable. Auto CAD drawings of cable path is to be maintained and Smart RFID Markers (The Permanent marking system) at starting point, ending point and at joint if any as per field (The Permanent marking system) for Under Ground cables to identify the cable path at the time of repair/maintainance. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC | Elecy | Labour | SWR11973 | 618.69 | M | 123738
19 | 200 | Laying of 2nd Cable in Excavated Trench. Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) | Elecy | Labour | SWR10988 | 200.1 | M | 40020
20 | 30 | Raise-DR 11KV 3x300sqmm UG Cb on support: Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elecy | Labour | SWR12005 | 270 | M | 8100
21 | 120 | Raise-SR 11KV 3x300sqmm UG Cb on support: Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elecy | Labour | SWR11955 | 141.25 | M | 16950
22 | 200 | Lay-SR 11KV 3x300sqmm UG Cb HG/BC/CC/BT: Excavation & laying of UG Cable in Single Run. Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. including Video shoot of cable laying works which demonstrate the UG cable trench depth and jointing works, GIS cooridinates and tagging of strating of cable, joints of cable and ending of cable. Auto CAD drawings of cable path is to be maintained and Smart RFID Markers (The Permanent marking system) at starting point, ending point and at joint if any as per field (The Permanent marking system) for Under Ground cables to identify the cable path at the time of repair/maintainance. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road with 11 KV 3x300 Sqmm Cable. | Elecy | Labour | SWR11919 | 456.33 | M | 91266
23 | 6 | Making of Straight through joint 11kv 3x300 xlpe | Elecy | Labour | SWR10386 | 3652.4 | EA | 21914.4
24 | 34 | Making of Outdoor/Indoor End Termination end termination 11kv 3x300 xlpe | Elecy | Labour | SWR10391 | 2324.15 | EA | 79021.1
25 | 900 | Fabrication of materials including 2 coats of Red oxide painting. Fabrication of Back clamps with 50 x 6 mm MS Flat. | Elecy | Labour | SWR10320 | 15 | EA | 13500
26 | 900 | Labour for Fixing of all types of clamps | Elecy | Labour | SWR10917 | 65 | EA | 58500
27 | 500 | Supply of MS bolts & nuts and washers etc of all sizes | Elecy | Supply | SMR11487 | 91.25 | KG | 45625
28 | 140 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elecy | Labour | SWR10642 | 502.5 | EA | 70350
29 | 70 | Erection of 9/10/11Meter Box pole: Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. Box pole 9/10/11 Mtr | Elecy | Labour | SWR11266 | 2591.99 | EA | 181439.3
30 | 70 | EXCAVATION OF PIT (2.6" x 2.6" x 5.0'): Excavation of pits in all soils except hard rock requiring blasting 8.0Mtrs PSCC Poles - 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | Elecy | Labour | SWR10105 | 474 | EA | 33180
31 | 73.5 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. including the cost of cement | Elecy | Labour | SWR10356 | 6450 | M3 | 474075
32 | 33 | RCC Column type DTR Plinth of size 1'X1'X13',topslab 5'x9'x9" & beam size 5'X9'X9" above 160KVA | Elecy | Labour | SWR21844 | 24600 | EA | 811800
33 | 33 | Erection of Three Phase DTRs: Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc. Erection of 3 Ph DTRs upto 25KVA | Elecy | Labour | SWR10463 | 1117.6 | EA | 36880.8
34 | 33 | Supply of 11kV HG Fuse set | Elecy | Supply | SMR11608 | 1733.75 | SET | 57213.75
35 | 33 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elecy | Labour | SWR20102 | 1777.94 | EA | 58672.02
36 | 33 | Erection of 11 KV HG Fuse set including earthing | Elecy | Labour | SWR10395 | 726 | SET | 23958
37 | 27 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Elecy | Labour | SWR10674 | 1563.41 | EA | 42212.07
38 | 33 | Painting of Name Plates for any equipment | Elecy | Labour | SWR10963 | 122 | EA | 4026
39 | 27 | Erection of CT operated meters for LV side of Distribution Transformers. Erection & commissioning of CT meter along with box on LV side of DTRs including cable connections from Transformer LV to Distribution box via CT meters box | Elecy | Labour | SWR10336 | 900 | EA | 24300
40 | 6 | Construction of Plinth for 11kv CTPT 0.6x0.6x2.89m | Elecy | Labour | SWR10733 | 6760 | EA | 40560
41 | 6 | Erection of 11kv CTPT set including jumpering | Elecy | Labour | SWR10420 | 1138 | EA | 6828
42 | 6 | Arranging for Re-Commissioning of CTPT Set including alinment of GI pipe, wiring and testing | Elecy | Labour | SWR11120 | 131 | EA | 786
43 | 3 | Erection of AB Switch and aligment complete. Erection of 11KV 800A double throw AB Switches | Elecy | Labour | SWR21277 | 2134 | EA | 6402
44 | 1120 | Laying of 1Core XLPE 120Sqmm Cable | Elecy | Labour | SWR22356 | 20 | M | 22400
45 | 600 | Supply of 120 Sqmm Aluminium lugs | Elecy | Supply | SMR40132 | 12.52 | EA | 7512
46 | 39 | Dismantling of DTR plinth (Column type) | Elecy | Labour | SWR20070 | 1968.75 | EA | 76781.25
47 | 6 | Dismantling of CTPT Set | Elecy | Labour | SWR22165 | 490 | EA | 2940
48 | 30 | Dismantling of Box pole 9/10/11 Mtr | Elecy | Labour | SWR11329 | 1130 | EA | 33900
49 | 1.64 | Dismantling of 11kV 34/ 55 Sqmm SC | Elecy | Labour | SWR22065 | 4419 | KM | 7247.16
50 | 33 | Dismantling of 11kv TT type AB switch | Elecy | Labour | SWR12172 | 872.28 | EA | 28785.24
51 | 2 | Dismantling of 11KV Line AB switch. | Elecy | Labour | SWR12177 | 981.25 | EA | 1962.5
52 | 33 | Dismantling of 11 KV HG fuse set including earthing | Elecy | Labour | SWR11745 | 346.5 | SET | 11434.5
53 | 0.5 | Dismantling of 11KV AB Cable 3x185+70Sqmm | Elecy | Labour | SWR12161 | 18600 | KM | 9300
54 | 0.34 | Dismantling of LT AB Cable 3x70+1x16+1x50 | Elecy | Labour | SWR12156 | 9050 | KM | 3077
55 | 8 | Dismantle-8.0 m long PSCC pole Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc. | Elecy | Labour | SWR11319 | 491.7 | EA | 3933.6
56 | 44 | Dismantle-9.1 M long PSCC pole: Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc. | Elecy | Labour | SWR11320 | 929.5 | EA | 40898
57 | 1 | Transport of Cond Drum,VCBs >10 & <20Km Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space)(excluding of loading unloading). Above 10 Km and upto 20 Km with Lorry for each trip. | Elecy | Labour | SWR11861 | 3235 | EA | 3235
58 | 1 | LOADING of Conductor drums | Elecy | Labour | SWR10191 | 202 | EA | 202
59 | 1 | UNLOADING of Conductor drums | Elecy | Labour | SWR10509 | 100 | EA | 100
60 | 1 | Transport of Cond Drum,VCBs >10 & <20Km Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space)(excluding of loading unloading). Above 10 Km and upto 20 Km with Lorry for each trip. | Elecy | Labour | SWR11861 | 3235 | EA | 3235
61 | 45 | Straight through joints of AB cable (each lead). Supply and erection of Straight line Asmbly kits | Elecy | Labour | SWR10672 | 1661 | EA | 74745
62 | 65 | Straight through joints of AB cable (each lead). Supply and erection of Angle line Assembly kits | Elecy | Labour | SWR10673 | 2124 | EA | 138060
63 | 110 | Supply of Suspension Clamp Assembly & Eye Hook-M | Elecy | Supply | SMR11492 | 65 | EA | 7150
64 | 2.2 | Stringing of HT AB cable 11 KV 3x185+70 Sqmm | Elecy | Labour | SWR10454 | 41055 | KM | 90321
65 | 1 | Stringing of LT AB cable 3x70 + 1x16 + 1x50 SQmm | Elecy | Labour | SWR10666 | 8450 | KM | 8450
66 | 270 | End Termination of AB cable (each lead) 120 Sqmm to 185 Sqmm Supply of 11KV 3x185+70sq.mm/ 3x70+70sq.mm/3x35+35sq.mm AB cable end Kits | Elecy | Supply | SMR11504 | 950 | SET | 256500
67 | 270 | End Termination of AB cable (each lead) 120 Sqmm to 185 Sqmm | Elecy | Labour | SWR10667 | 800 | EA | 216000
68 | 35 | Supply and erection of T-Branch kit | Elecy | Labour | SWR24971 | 3215 | EA | 112525
69 | 33 | Earth-11KV 3x185+1x75 AB Cb-GIStrip&Pipe | Elecy | Labour | SWR20612 | 500 | EA | 16500
70 | 1170 | Supply & Running 25x6mm GI Strip for Earthing | Elecy | Labour | SWR34252 | 110 | M | 128700
71 | 117 | ERECT. OF LINES-Providing of earthing Providing of Earthing. Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elecy | Labour | SWR10357 | 1210 | EA | 141570
72 | 117 | ERECT. OF LINES-Providing of RCC collar Providing of RCC collar to earth pit. Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elecy | Labour | SWR10359 | 386 | EA | 45162
73 | 117 | Supply&Erec of CI earth Pipe as APTRANCO Providing of earthing with various types of earth electrodes. Excavation of earth pit, supply of cast iron pipe with flange on one end (as per ISS7181/86) of nominal dia 125mm and 2.75 meters long in side the pit including supply and fixing RCC collars 0.75 meter dia (OD), 50mm thick and 0.60meters long complete as per APTRANSCO standards | Elecy | Labour | SWR10924 | 9804 | EA | 1147068
74 | 140 | LOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10204 | 76 | EA | 10640
75 | 140 | UNLOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10522 | 50 | EA | 7000
76 | 11.025 | TRANSPORT OF STEEL MATERIAL 10 TO 20KM Transport of steel including line materials such as cross arms, clamps, hardware, cable (loose) and other line materials (Including loading and unloading). Above 10 KM and upto 20 KM. | Elecy | Labour | SWR10148 | 472 | TO | 5203.8
77 | 108 | Running of 11KV jumper from Line, AB switch, HG Fuse set to DTR for 3-Phases | Elecy | Labour | SWR10407 | 412.5 | EA | 44550
78 | 99 | Removing and providing of jumpers in SS. | Elecy | Labour | SWR20785 | 64 | LS | 6336
79 | 4 | Loading of 11 KV AB Cable (XLPE) Single core upto 100 Mts. Drum (including Accessories) | Elecy | Labour | SWR12414 | 293 | DR | 1172
80 | 4 | Un loading of 11 KV AB Cable (XLPE) Single core upto 100 Mts. Drum (including Accessories) | Elecy | Labour | SWR12432 | 145 | DR | 580
81 | 2 | Transport of Cond Drum,VCBs >10 & <20Km Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space)(excluding of loading unloading). Above 10 Km and upto 20 Km with Lorry for each trip. | Elecy | Labour | SWR11861 | 3235 | EA | 6470
82 | 2 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Labour | SWR11230 | 1024 | DR | 2048
83 | 2 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Labour | SWR11231 | 1024 | DR | 2048
84 | 1 | Transport of Cond Drum,VCBs >10 & <20Km Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space)(excluding of loading unloading). Above 10 Km and upto 20 Km with Lorry for each trip. | Elecy | Labour | SWR11861 | 3235 | EA | 3235
85 | 35 | TRANSPORT OF STEEL 10 TO 20KM Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 404 | TO | 14140
86 | 0.672 | LOADING of ACSR conductor scrap | Elecy | Labour | SWR10257 | 491 | TO | 329.952
87 | 0.672 | UNLOADING of ACSR conductor scrap | Elecy | Labour | SWR10575 | 491 | TO | 329.952
88 | 9.525 | LOADING of MS Scrap | Elecy | Labour | SWR10258 | 578 | TO | 5505.45
89 | 9.525 | UNLOADING of MS Scrap | Elecy | Labour | SWR10576 | 578 | TO | 5505.45
90 | 36.5 | Sup Material for 1st coat Al. Painting. Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of substation structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elecy | Supply | SMR40009 | 2181 | TO | 79606.5
91 | 36.5 | Sup Material for 2nd coat Al. Painting. Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of substation structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elecy | Labour | SMR40010 | 1293 | TO | 47194.5
92 | 36.5 | Labour for 1st coat Al. Painting. Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of substation structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elecy | Labour | SWR10877 | 851 | TO | 31061.5
93 | 36.5 | Labour for 2nd coat Al. Painting. Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of substation structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium | Elecy | Labour | SWR10879 | 482 | TO | 17593
Schedule Amount | [7 empty] | 7120511.5875
(Rupees Seventy One lakhs Twenty Thousand Five Hundred Eleven and Paise Fifty Nine only)