## Dummy
Name of the work:- Laying of new 33KV XLPE UG Cable Interlinking line on 33KV Gunrock - Hakimpet Cable # II feeder from Lakdawala to 33/11KV Macha Bollaram substation for a distance of 1.91Km (i.e., 1.76Km UG + 0.15Km OH) in order to extend supply to 33/11KV Macha Bollaram substation as alternate incoming source to maintain reliable supply in Secunderabad Cantonment Division of Secunderabad Circle in Master Plan-I Division of Masterplan /Hyderabad Circle - Under T&D Improvement works.
WBS NO : T-2231-12-01-02-01-001
ESTIMATE
Sl.No | SWR Code | Item DEtailEd SpEcification DEscription | Qty | UOM | Rate | Amount
1 | SMR40051 | Supply 9mtrs tubular poles single way | 6 | EA | 13913 | 83478
2 | SWR10955 | Errection of tubular poles | 6 | EA | 1379 | 8274
3 | SMR40033 | SupCU Flexi jumper for Power T/F Neutral | 2 | EA | 4725 | 9450
4 | SWR20905 | E/r 3ph DTR inclu L&Un-L,T&C on plinth | 1 | EA | 1650 | 1650
5 | SWR24831 | Construct-DTR Plinth CRS 5x4x8', 4' thck | 1 | EA | 13750 | 13750
6 | SWR10674 | Erection of LT distribution box | 1 | EA | 1594.67 | 1594.67
7 | SWR11879 | Lay-4C/10C 2.5Sqmm Control Cable | 1700 | M | 27 | 45900
8 | SMR40045 | Supply of AC Supply panel complete | 1 | EA | 42000 | 42000
9 | SWR11893 | Erect-Contrl/Relay, AC, Announ. Panels | 1 | EA | 2122 | 2122
10 | SWR10198 | LOADING of 33 KV VCBs&Panel boards | 10 | EA | 1024 | 10240
11 | SWR10516 | UNLOADING of 33 KV VCBs&Panel boards | 10 | EA | 1044.48 | 10444.8
12 | SWR11861 | Transport of Cond Drum,VCBs >10 & <20Km | 10 | EA | 3299.7 | 32997
13 | SWR10930 | Erection of 33KV indoor switchgear panel | 10 | EA | 9847 | 98470
14 | SWR10873 | Supply,fabricati of 6mm Checkerd plates | 750 | KG | 83 | 62250
15 | SMR40068 | SupRubber mats( 6’x3’)size for indoorSS | 20 | EA | 1386 | 27720
16 | SMR12378 | S-10ft Aluminium Ladder | 1 | EA | 1654 | 1654
17 | SMR40087 | Sup TrollyMounted Co2 Cylinders(IS-2878) | 2 | EA | 9240 | 18480
18 | SMR40088 | Sup Fire Buckets Stand with Buckets | 2 | SET | 1386 | 2772
19 | SMR40089 | Sup Fire Extinguisher for Control Room | 6 | EA | 4620 | 27720
20 | SMR40071 | Supply of Safety Helmet of standard make | 4 | EA | 231 | 924
21 | SMR40066 | Sup Earth Rods (8ft) Screw & clamp type | 4 | EA | 578 | 2312
22 | SMR40067 | Supply of Hand Gloves | 4 | SET | 289 | 1156
23 | SMR40069 | Sup Stand basic cell phone with charger | 1 | EA | 1386 | 1386
24 | SMR40061 | Sup Steel almarah(61/2 X 3ft) Godrej | 1 | EA | 9818 | 9818
25 | SMR40057 | Supply of Table (3x6ft) Godrej | 1 | EA | 6050 | 6050
26 | SMR40058 | Supply of S type chairs (Godrej) | 4 | EA | 924 | 3696
27 | SMR40060 | Sup Angle racks(18x36.6inches) Godrej | 1 | EA | 1733 | 1733
28 | SMR40070 | Supply of Danger boards with clamps | 10 | EA | 116 | 1160
29 | SMR40086 | Sup 33/11kv S.S Permanent name board | 1 | EA | 10238 | 10238
30 | SMR40059 | Supply of Wall clock standard make | 1 | EA | 578 | 578
31 | SMR40063 | SupTaparia Tool kit complete as per Spec | 1 | SET | 4925 | 4925
32 | SMR40064 | Sup Rechargeable LED torch light. | 1 | EA | 1733 | 1733
33 | SMR40065 | Supply of Hack saw (12 inches) | 1 | EA | 289 | 289
34 | SMR40072 | Supply of LC Boards | 8 | EA | 116 | 928
35 | SMR40073 | Supply of Gum Boots | 2 | EA | 693 | 1386
36 | SMR40076 | Supply of Digital clamp meter. | 1 | EA | 2888 | 2888
37 | SMR40074 | Supply of 5000v megger | 1 | EA | 13860 | 13860
38 | SWR20032 | Sup &fix of board ind Switchyard layout | 1 | EA | 1654 | 1654
39 | SWR22090 | Sup& fix safety inst/SS Op. inst board | 1 | EA | 2205 | 2205
40 | SMR11594 | S-90W LED fixture set | 6 | EA | 8200 | 49200
41 | SMR11482 | S-CI Pipe earthing 100mm dia 2.75m long | 26 | EA | 3486 | 90636
42 | SMR11480 | S-GI pipe earthing 40mm dia 2m long | 2 | EA | 698 | 1396
43 | SWR10356 | Mass concreting of supports incl. cement | 7.92 | M3 | 6579 | 52105.68
44 | SWR11923 | Lay-SR LT 3.5x185sqmm UG Cb HG/BC/CC/BT | 90 | M | 377.63 | 33986.7
45 | SWR11959 | Raise-SR LT 3.5x185sqmm UG Cb on support | 10 | M | 85.43 | 854.3
46 | SMR40140 | Sup of 31/2x185Sqmm UG O/D end term kits | 2 | EA | 550 | 1100
47 | SWR10765 | OD/Idoor end termination LT 3 1/2 x 185 | 2 | EA | 968.9 | 1937.8
48 | SWR11920 | Lay-SR 11KV 3x185sqmm UG Cb HG/BC/CC/BT | 50 | M | 465.46 | 23273
49 | SWR11956 | Raise-SR 11KV 3x185sqmm UG Cb on support | 15 | M | 126.23 | 1893.45
50 | SWR10920 | Laying of earth mat,excavation 75x 8mm | 377.6 | RMT | 65 | 24544
51 | SWR10921 | Laying of earth mat,excavation 25x3mm | 416 | RMT | 68 | 28288
52 | SWR10199 | LOADING of 11 KV VCBs&Panel boards | 16 | EA | 1024 | 16384
53 | SWR10517 | UNLOADING of 11 KV VCBs&Panel boards | 16 | EA | 1044.48 | 16711.68
54 | SWR10931 | Erection of 11KV indoor switchgear panel | 16 | EA | 8894 | 142304
55 | SWR10238 | LOADING of 11 KV AB SWCH Con 200/400 A | 1 | EA | 80 | 80
56 | SWR10556 | UNLOADING of 11 KV AB SWCH Con 200/400 A | 1 | EA | 80 | 80
57 | SWR20102 | Erection of 11kv TT type AB switch | 1 | EA | 1813.49 | 1813.49
58 | SWR10231 | LOADING of 11 KV HG Fuse Sets | 1 | EA | 18 | 18
59 | SWR10549 | UNLOADING of 11 KV HG Fuse Sets | 1 | EA | 18 | 18
60 | SWR10395 | Erect. of 11kv HG Fuseset incl earthing | 1 | SET | 740.52 | 740.52
61 | SWR11166 | Loading 220 V Battery with Charger | 1 | SET | 1612 | 1612
62 | SWR11147 | Un-loading 220 V Battery with Charger | 1 | SET | 1024 | 1024
63 | SWR11772 | Erect-220V Batery with Chrgr incl all-SS | 1 | EA | 6442.58 | 6442.58
64 | SWR22088 | Fab & laying of ladder in cable trench | 2 | EA | 788 | 1576
65 | SWR10956 | Fixing of LED/Metal halide complete. | 6 | EA | 1268 | 7608
66 | SMR40009 | Sup Material for 1st coat Al. Painting. | 2.05 | TO | 2181 | 4471.05
67 | SWR10877 | Labour for 1st coat Al. Painting. | 2.05 | TO | 851 | 1744.55
68 | SMR40010 | Sup Material for 2nd coat Al. Painting. | 2.05 | TO | 1293 | 2650.65
69 | SWR10879 | Labour for 2nd coat Al. Painting. | 2.05 | TO | 482 | 988.1
70 | SWR10881 | Painting AB switch OP rods with PO red | 1 | EA | 142 | 142
71 | SWR10854 | Transport of 8MVA power transformer | 2 | EA | 21945 | 43890
72 | SWR10613 | LOADING of 8 MVA PTR | 2 | EA | 5805.84 | 11611.68
73 | SWR10627 | UNLOADING of 8 MVA PTR | 2 | EA | 5805.84 | 11611.68 | 610494.667 | 253381.17
74 | SWR21321 | Erec 33/11 KV, 8 MVA PTR as per Spec | 2 | EA | 49480.2 | 98960.4
75 | SWR10357 | ERECT. OF LINES-Providing of earthing | 26 | EA | 1234.2 | 32089.2
76 | SWR10359 | ERECT. OF LINES-Providing of RCC collar | 26 | EA | 386 | 10036 |  | 1868528.6
77 | SWR10357 | ERECT. OF LINES-Providing of earthing | 2 | EA | 1234.2 | 2468.4
78 | SWR11861 | Transport of Cond Drum,VCBs >10 & <20Km | 12 | EA | 3299.7 | 39596.4
79 | SWR10868 | Fabrication of struc.with power drilling | 2.05 | TO | 6852 | 14046.6
80 | SWR11972 | Lay-DR 33KV 3x400sqmm UG Cb HG/BC/CC/BT | 150 | M | 749 | 112350 |  | 2121909.77
81 | SWR11973 | Lay-DR 11KV 3x300sqmm UG Cb HG/BC/CC/BT | 150 | M | 631.06 | 94659
82 | SWR10387 | OD/Idoor end termination 33kv 3x400 xlpe | 4 | EA | 2764.76 | 11059.04
83 | SWR10391 | OD/Idoor end termination 11kv 3x300 xlpe | 4 | EA | 2370.63 | 9482.52
84 | SWR10390 | OD/Idoor end termination 11kv 3x185 xlpe | 2 | EA | 2370.63 | 4741.26
85 | SWR11266 | Erection of 9/10/11Meter Box pole | 3 | EA | 2643.83 | 7931.49
86 | SWR10204 | LOADING of R.S. Joists 175 x 85 mm | 6 | EA | 76 | 456
87 | SWR10522 | UNLOADING of R.S. Joists 175 x 85 mm | 6 | EA | 50 | 300
88 | SWR10640 | Painting of RS Joist(1C RO, 2C Al.Paint) | 6 | EA | 1132 | 6792
89 | SWR10206 | LOADING of MS Channel,Angles,Flats&Rods | 1.75 | TO | 221 | 386.75
90 | SWR10524 | UNLOADING of MS Channel,Angles,Flats&Rod | 1.75 | TO | 185 | 323.75
91 | SWR10132 | TRANSPORT OF STEEL 10 TO 20KM | 3.25 | TO | 412.08 | 1339.26
92 | SWR11890 | Coping & Muffing-Iron Pole | 0.279 | M3 | 3893 | 1086.147
93 | SWR20768 | Excavate-Pit in Soil except Hrd Rck | 9.27 | M3 | 345 | 3198.15
94 | SWR10988 | Lay-2nd Cable in Excavated Trench | 300 | M | 204.1 | 61230
|  | Line Labour |  |  |  | 1665154.747
1 | SWR11230 | Load-11/33KV XLPE UG Cable for all sizes | 8 | DR | 1024 | 8192
2 | SWR11231 | Unload-11/33KV XLPE UG Cable all sizes | 8 | DR | 1024 | 8192
3 | SWR11861 | Transport of Cond Drum,VCBs >10 & <20Km | 7 | EA | 3299.7 | 23097.9
4 | SWR11980 | Lay-DR 33KV 3x400sqmm UG Cb CC/BT Compsr | 480 | M | 1388.84 | 666643.2
5 | SWR11988 | Lay-DR 33KV 3x400sqmm UG Cb CC/BT RdCrsg | 100 | M | 1587.07 | 158707
6 | SWR11972 | Lay-DR 33KV 3x400sqmm UG Cb HG/BC/CC/BT | 470 | M | 749 | 352030
7 | SWR10988 | Lay-2nd Cable in Excavated Trench | 1050 | M | 204.1 | 214305
8 | SWR11001 | HDD cable with HDPE pipe in Hard rock | 210 | M | 6993 | 1468530
9 | SWR12004 | Raise-DR 33KV 3x400sqmm UG Cb on support | 75 | M | 323.85 | 24288.75
10 | SWR10387 | OD/Idoor end termination 33kv 3x400 xlpe | 16 | EA | 2764.76 | 44236.16
11 | SWR10382 | Straight through joint 33kv 3x400 xlpe | 14 | EA | 5700.78 | 79810.92
12 | SMR40077 | Supply of 250 mm Hume pipe of class NP3 | 100 | M | 363 | 36300
13 | SMR40081 | Supply of 6" B class GI pipe | 400 | M | 1044 | 417600
14 | SMR11610 | S-6" DWC pipe | 50 | M | 1012 | 50600
15 | SWR21903 | Consult charg for providng traffic diver | 1050 | M | 30 | 31500
16 | SWR10239 | LOADING of 33 KV AB SWCH Con 400/800 A | 2 | EA | 126 | 252
17 | SWR10557 | UNLOADING of 33 KV AB SWCH Con 400/800 A | 2 | EA | 79 | 158
18 | SWR10392 | Erection of 33kv ABSwitch incl earthing | 2 | EA | 4500 | 9000
19 | SWR10356 | Mass concreting of supports incl. cement | 5.25 | M3 | 6579 | 34539.75
20 | SWR11890 | Coping & Muffing-Iron Pole | 0.155 | M3 | 3893 | 603.415
21 | SWR10642 | Fabrication of 175x85/150x75mm RS joist | 10 | EA | 512.55 | 5125.5
22 | SWR11266 | Erection of 9/10/11Meter Box pole | 5 | EA | 2643.83 | 13219.15
23 | SWR10204 | LOADING of R.S. Joists 175 x 85 mm | 10 | EA | 76 | 760
24 | SWR10522 | UNLOADING of R.S. Joists 175 x 85 mm | 10 | EA | 50 | 500
25 | SWR10640 | Painting of RS Joist(1C RO, 2C Al.Paint) | 10 | EA | 1132 | 11320
26 | SWR10206 | LOADING of MS Channel,Angles,Flats&Rods | 10.325 | TO | 221 | 2281.825
27 | SWR10524 | UNLOADING of MS Channel,Angles,Flats&Rod | 10.325 | TO | 185 | 1910.125
28 | SWR10132 | TRANSPORT OF STEEL 10 TO 20KM | 12.85 | TO | 412.08 | 5295.228
29 | SWR11181 | Trans 11/12.5/12.9M Spun pole upto 50KM | 55 | EA | 858 | 47190
30 | SWR10190 | LOADING of 12.5M SPUN POLE | 55 | EA | 548 | 30140
31 | SWR10508 | UNLOADING of 12.5M SPUN POLE | 55 | EA | 363 | 19965
32 | SWR10350 | Erection of Spun pole 12.5Mt | 55 | EA | 4521.66 | 248691.3
33 | SWR10109 | EXCAVATION OF PIT(3.0" x 3.0" x 7.6") | 30 | EA | 842.78 | 25283.4
34 | SWR11041 | Exc of Hard pit w/o blast 0.92X0.92X2.3M | 25 | EA | 1466.25 | 36656.25
35 | SWR10356 | Mass concreting of supports incl. cement | 93.83 | M3 | 6579 | 617307.57
36 | SMR11683 | S-M+3 Tower GALV | 6 | EA | 140674.3 | 844045.8
37 | SWR11850 | Erect- M+3 Tower GALV | 6 | EA | 64576 | 387456
38 | SMR11684 | S-Mat. for Extn of M+3 Tower by 3M GALV | 12 | EA | 28520.64 | 342247.68
39 | SWR11851 | Erect-Extn of 3M for M+3 Tower GALV | 12 | EA | 5168.95 | 62027.4
40 | SWR12085 | Excvt Pit ext HardBlst 1.2Mx1.2Mx3.3M | 3 | EA | 1997.93 | 5993.79
41 | SWR12090 | Excvt Pit Hard w/o Blst 1.2Mx1.2Mx3.3M | 3 | EA | 3592.95 | 10778.85
42 | SWR25089 | S&E-Smart RFID marker | 15 | EA | 2745 | 41175
43 | SWR12104 | CAD Drawing per pole upto 10KM | 1 | LS | 6000 | 6000
44 | SWR10704 | Stringing 100sqmm 33/11kv Line 6 Cond DC | 2.3 | KM | 26255.98 | 60388.754
45 | SWR10466 | Formation of 33kvline vertical cutpoint | 10 | EA | 3198.72 | 31987.2
46 | SWR22065 | Dismantling of 11kV 34/ 55 Sqmm SC | 1.9 | KM | 4500 | 8550
47 | SWR11308 | Restring-55 Sqmm SC-3 Conductors | 1.9 | KM | 6616 | 12570.4
48 | SWR10191 | LOADING of Conductor drums | 5 | EA | 202 | 1010
49 | SWR10509 | UNLOADING of Conductor drums | 5 | EA | 100 | 500
50 | SWR10211 | LOADING of 33 KV Pin insulators | 252 | CRT | 3 | 756
51 | SWR10529 | UNLOADING of 33 KV Pin insulators | 252 | CRT | 3 | 756
52 | SWR12416 | LOADING of 33 & 11 KV Disc insulators | 144 | CRT | 2 | 288
53 | SWR10631 | UNLOADING of 33 & 11 KV Disc insulator | 144 | CRT | 2 | 288
54 | SWR10618 | LOADING of 33KV Metal parts-bag of 25no | 6 | BAG | 65 | 390
55 | SWR10632 | UNLOADING of 33 KV Metal parts-bagof 25 | 6 | BAG | 65 | 390
56 | SWR10148 | TRANSPORT OF STEEL MATERIAL 10 TO 20KM | 4.2 | TO | 481.44 | 2022.048
57 | SMR11486 | S-Earthing GI Wire No 8 incl mat | 50 | KG | 105 | 5250
58 | SWR12331 | AB Switch Coil Earthing GI No. 8 Wire | 2 | EA | 146.63 | 293.26
59 | SMR11488 | S-GI Bolts & Nuts,Washers etc., | 3150 | KG | 117.5 | 370125
60 | SMR11482 | S-CI Pipe earthing 100mm dia 2.75m long | 6 | EA | 3486 | 20916
61 | SWR10263 | LOADING of CI Earth pipe upto 2.7 Mtr | 6 | EA | 29 | 174
62 | SWR10581 | UNLOADING of CI Earth pipe upto 2.7 Mtr | 6 | EA | 29 | 174
63 | SMR40091 | Supply of GI pipe of 40 mm dia 2 mtrs | 12 | EA | 733 | 8796
64 | SWR10357 | ERECT. OF LINES-Providing of earthing | 12 | EA | 1234.2 | 14810.4
65 | SWR23200 | Cut-Tree Branch(LT/11/33)&Trnsprt Debris | 5000 | EA | 4 | 20000
66 | SWR10372 | Providing guarding to tel/road crossing | 100 | EA | 2310 | 231000
67 | SWR10359 | ERECT. OF LINES-Providing of RCC collar | 6 | EA | 386 | 2316
68 | SWR10357 | ERECT. OF LINES-Providing of earthing | 6 | EA | 1234.2 | 7405.2
69 | SWR10107 | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | 19 | EA | 700 | 13300
70 | SWR10356 | Mass concreting of supports incl. cement | 14.8 | M3 | 6579 | 97369.2
71 | SMR40085 | Supply of Pre-cast cable Joint markers | 25 | EA | 484 | 12100
72 | SWR11267 | Erect-12Meter Box pole | 14 | EA | 3901.37 | 54619.18
73 | SWR10204 | LOADING of R.S. Joists 175 x 85 mm | 28 | EA | 76 | 2128
74 | SWR10522 | UNLOADING of R.S. Joists 175 x 85 mm | 28 | EA | 50 | 1400
75 | SWR11890 | Coping & Muffing-Iron Pole | 0.372 | M3 | 3893.01 | 1448.1997
|  | Line Labour 11KV |  |  |  | 7377476.8047
1 | SWR11230 | Load-11/33KV XLPE UG Cable for all sizes | 2 | DR | 1024 | 2048
2 | SWR11231 | Unload-11/33KV XLPE UG Cable all sizes | 2 | DR | 1024 | 2048
3 | SWR11861 | Transport of Cond Drum,VCBs >10 & <20Km | 2 | EA | 3299.7 | 6599.4
4 | SWR10391 | OD/Idoor end termination 11kv 3x300 xlpe | 8 | EA | 2370.63 | 18965.04
5 | SWR10386 | Straight through joint 11kv 3x300 xlpe | 2 | EA | 3725.45 | 7450.9
6 | SMR40080 | Supply of 4" B class GI pipe | 150 | M | 740 | 111000
7 | SWR21903 | Consult charg for providng traffic diver | 40 | M | 30 | 1200
8 | SWR10238 | LOADING of 11 KV AB SWCH Con 200/400 A | 4 | EA | 80 | 320
9 | SWR10556 | UNLOADING of 11 KV AB SWCH Con 200/400 A | 4 | EA | 80 | 320
10 | SWR10393 | Erection of 11kv ABSwitch incl earthing | 4 | EA | 3200 | 12800
11 | SWR10107 | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | 4 | EA | 700 | 2800
12 | SWR10107 | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | 1 | EA | 700 | 700
13 | SWR11890 | Coping & Muffing-Iron Pole | 0.031 | M3 | 3893 | 120.683
14 | SWR10642 | Fabrication of 175x85/150x75mm RS joist | 2 | EA | 512.55 | 1025.1
15 | SWR11266 | Erection of 9/10/11Meter Box pole | 1 | EA | 2643.83 | 2643.83
16 | SWR10204 | LOADING of R.S. Joists 175 x 85 mm | 2 | EA | 76 | 152
17 | SWR10522 | UNLOADING of R.S. Joists 175 x 85 mm | 2 | EA | 50 | 100
18 | SWR10640 | Painting of RS Joist(1C RO, 2C Al.Paint) | 2 | EA | 1132 | 2264
19 | SWR10206 | LOADING of MS Channel,Angles,Flats&Rods | 0.45 | TO | 221 | 99.45
20 | SWR10524 | UNLOADING of MS Channel,Angles,Flats&Rod | 0.45 | TO | 185 | 83.25
21 | SMR11485 | S-Earthing GI flat 25x3 mm incl material | 50 | KG | 105 | 5250
22 | SWR12331 | AB Switch Coil Earthing GI No. 8 Wire | 4 | EA | 146.63 | 586.52
23 | SMR11482 | S-CI Pipe earthing 100mm dia 2.75m long | 6 | EA | 3486 | 20916
24 | SWR10454 | Stringing of AB cbl 11 KV 3x185+70 Sqmm | 1.25 | KM | 41876.1 | 52345.125
25 | SMR11504 | S-of 11KV AB cable end kits | 30 | SET | 950 | 28500
26 | SWR10148 | TRANSPORT OF STEEL MATERIAL 10 TO 20KM | 0.95 | TO | 481.44 | 457.368
27 | SMR11488 | S-GI Bolts & Nuts,Washers etc., | 100 | KG | 117.5 | 11750
28 | SWR10307 | FABR-Drilling of holes upto 20 mm dia 4 | 50 | EA | 4 | 200
29 | SWR10294 | Cutting Charges for MS chanl 100x50mm | 30 | EA | 10 | 300
30 | SWR10978 | Errection of 11 M long PSCC pole | 4 | EA | 4336.85 | 17347.4
31 | SWR11180 | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | 4 | EA | 431.97 | 1727.88
32 | SWR10188 | LOADING of 9.1M PSCC POLE | 4 | EA | 182 | 728
33 | SWR10506 | UNLOADING of 9.1M PSCC POLE | 4 | EA | 91 | 364
34 | SWR10357 | ERECT. OF LINES-Providing of earthing | 6 | EA | 1234.2 | 7405.2
35 | SWR10359 | ERECT. OF LINES-Providing of RCC collar | 6 | EA | 386 | 2316
36 | SWR10191 | LOADING of Conductor drums | 1 | EA | 202 | 202
37 | SWR10509 | UNLOADING of Conductor drums | 1 | EA | 100 | 100
38 | SWR10356 | Mass concreting of supports incl. cement | 5.15 | M3 | 6579 | 33881.85
39 | SWR12416 | LOADING of 33 & 11 KV Disc insulators | 18 | CRT | 2 | 36
40 | SWR10631 | UNLOADING of 33 & 11 KV Disc insulator | 18 | CRT | 2 | 36
41 | SWR12402 | LOADING of 11 KV Metal parts | 1 | BAG | 48 | 48
42 | SWR12421 | UNLOADING of 11 KV Metal parts Bag | 1 | BAG | 48 | 48
43 | SWR12025 | Lay-TR 11KV 3x300sqmm UG Cb CC/BT RdCrsg | 30 | M | 1805.4 | 54162
44 | SWR12014 | Lay-TR 11KV 3x300sqmm UG Cb HG/BC/CC/BT | 20 | M | 780.3 | 15606
45 | SWR11919 | Lay-SR 11KV 3x300sqmm UG Cb HG/BC/CC/BT | 20 | M | 465.46 | 9309.2
46 | SWR11928 | Lay-SR 11KV 3x300sqmm UG Cb CC/BT Compsr | 420 | M | 1073.94 | 451054.8
47 | SWR11937 | Lay-SR 11KV 3x300sqmm UG Cb CC/BT RdCrsg | 40 | M | 1199.4 | 47976
48 | SWR10988 | Lay-2nd Cable in Excavated Trench | 100 | M | 204.1 | 20410
49 | SWR11955 | Raise-SR 11KV 3x300sqmm UG Cb on support | 20 | M | 144.08 | 2881.6
50 | SWR10667 | End Termnatn of AB cable 120 to 185 Sqmm | 30 | EA | 800 | 24000
51 | SWR10673 | Supply and ere Angle line Asmbly kits | 15 | EA | 2124 | 31860
52 | SWR10672 | Supply and ere Straight line Asmbly kits | 32 | EA | 1661 | 53152
53 | SWR10671 | Erection of Assemble Kit for 'T' Branche | 10 | EA | 1800 | 18000
54 | SWR12099 | Erection- I Hook | 32 | EA | 55 | 1760
55 | SMR12099 | Supply- I Hook | 32 | EA | 158 | 5056
|  | Bay Extension Labour |  |  |  | 1092512.596
1 | SWR10392 | Erection of 33kv ABSwitch incl earthing | 6 | EA | 4500 | 27000
2 | SWR10396 | Erect of 33kv LA stn type incl earthing | 4 | SET | 880 | 3520
3 | SWR11918 | Lay-SR 33KV 3x400sqmm UG Cb HG/BC/CC/BT | 100 | M | 572.1 | 57210
4 | SWR11954 | Raise-SR 33KV 3x400sqmm UG Cb on support | 50 | M | 135.66 | 6783
5 | SWR10387 | OD/Idoor end termination 33kv 3x400 xlpe | 6 | EA | 2764.76 | 16588.56
6 | SWR10198 | LOADING of 33 KV VCBs&Panel boards | 2 | EA | 1024 | 2048
7 | SWR10516 | UNLOADING of 33 KV VCBs&Panel boards | 2 | EA | 1044.48 | 2088.96
8 | SWR10239 | LOADING of 33 KV AB SWCH Con 400/800 A | 6 | EA | 126 | 756
9 | SWR10557 | UNLOADING of 33 KV AB SWCH Con 400/800 A | 6 | EA | 79 | 474
10 | SWR11861 | Transport of Cond Drum,VCBs >10 & <20Km | 3 | EA | 3299.7 | 9899.1
11 | SWR10460 | Erection of 33kv VCB | 2 | EA | 12500 | 25000
12 | SWR10399 | Erection of 33kv CT s | 2 | SET | 1079 | 2158
13 | SWR20685 | Cement concrete with 40MM metal VCB plin | 7.77 | M3 | 5160 | 40093.2
14 | SMR40051 | Supply 9mtrs tubular poles single way | 3 | EA | 13913 | 41739
15 | SWR10955 | Errection of tubular poles | 3 | EA | 1379 | 4137
16 | SMR11594 | S-90W LED fixture set | 3 | EA | 8200 | 24600
17 | SWR10956 | Fixing of LED/Metal halide complete. | 3 | EA | 1268 | 3804
18 | SWR10917 | Labour for Fixing of all types of clamps | 60 | EA | 65 | 3900
19 | SWR11879 | Lay-4C/10C 2.5Sqmm Control Cable | 2600 | M | 27 | 70200
20 | SWR10356 | Mass concreting of supports incl. cement | 13.65 | M3 | 6579 | 89803.35
21 | SWR11890 | Coping & Muffing-Iron Pole | 0.403 | M3 | 3893 | 1568.879
22 | SWR10107 | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | 13 | EA | 700 | 9100
23 | SWR10642 | Fabrication of 175x85/150x75mm RS joist | 20 | EA | 512.55 | 10251
24 | SWR11266 | Erection of 9/10/11Meter Box pole | 10 | EA | 2643.83 | 26438.3
25 | SWR10204 | LOADING of R.S. Joists 175 x 85 mm | 20 | EA | 76 | 1520
26 | SWR10522 | UNLOADING of R.S. Joists 175 x 85 mm | 20 | EA | 50 | 1000
27 | SWR10640 | Painting of RS Joist(1C RO, 2C Al.Paint) | 20 | EA | 1132 | 22640
28 | SWR10206 | LOADING of MS Channel,Angles,Flats&Rods | 2.6 | TO | 221 | 574.6
29 | SWR10524 | UNLOADING of MS Channel,Angles,Flats&Rod | 2.6 | TO | 185 | 481
30 | SWR10132 | TRANSPORT OF STEEL 10 TO 20KM | 7.6 | TO | 412.08 | 3131.808
31 | SMR24910 | 33KV Bay Extn: S-Zebra Conductor | 0.095 | KM | 299369 | 28440.055
32 | SWR10884 | Conn. of equip/bus single zebra/panther | 12 | EA | 224 | 2688
33 | SMR11482 | S-CI Pipe earthing 100mm dia 2.75m long | 20 | EA | 3486 | 69720
34 | SMR24912 | 33KV Bay Extn: S-T Clamp | 18 | EA | 500 | 9000
35 | SMR24911 | 33KV Bay Extn: S-Twin Zebra Connector | 9 | EA | 600 | 5400
36 | SWR10860 | Supply & Spreading of 20mm HBG metal | 10 | M3 | 2113 | 21130
37 | SWR10357 | ERECT. OF LINES-Providing of earthing | 20 | EA | 1234.2 | 24684
38 | SWR10359 | ERECT. OF LINES-Providing of RCC collar | 20 | EA | 386 | 7720
39 | SWR12510 | L-Cable Termination to Switchgear | 200 | EA | 27 | 5400
682689.812
TOTAL : | [5 empty] | 1665154.747 | 1378748.1305
18% GST on Civil Works : | [5 empty] | 299727.85 | 248174.66
TOTAL : | [5 empty] | 1964882.597 | 1626922.7905

## 8Column Schedule (2)
Name of the work:- Erection of 33/11 KV Indoor Sub-station along with necessary lines and equipments & construction of control room and other civil works at VB City Bollaram, Turkapally Village, Alwal (M) in Master Plan Circle, Hyderabad.
WBS NO : S-1616-12-01-02-01-001 (Elect) & S-1616-12-07-01-01-001 (Civil)
S.C.H.E.D.U.L.E
Sl.No | Estimate Quantity (only Figures) | Item Detailed Specification Description | Work Type | Item Short Description ( upto 100 Characters) | APSS / Morth Cl. Number ( upto 200 Characters) | Rate (INR) ( Upto 2 Decimals ) | UOM ( upto 50 Characters) | Amount
1 | 6 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Elect | Supply | SMR40051 | 13913 | EA | 83478
2 | 6 | Erection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 8274
3 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. | Elect | Supply | SMR40033 | 4725 | EA | 9450
4 | 1 | Erection of 3 Phase DTRs 63,75 & 100 KVA including loading and Unloading DTR on the Structure/Plinth etc | Elect | Labour | SWR20905 | 1650 | EA | 1650
5 | 1 | Construction of plinth for mounting distribution transformers WITH CRS masionary (plinth size 5'x4'x8') including cost of cement, CC bed concreting of 4' thickness top and bottom and pointing. | Elect | Labour | SWR24831 | 13750 | EA | 13750
6 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Elect | Labour | SWR10674 | 1594.67 | EA | 1594.67
7 | 1700 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Elect | Labour | SWR11879 | 27 | M | 45900
8 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. | Elect | Supply | SMR40045 | 42000 | EA | 42000
9 | 1 | Erection of control/Relay panels, AC Panels, announciation panels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Elect | Labour | SWR11893 | 2122 | EA | 2122
10 | 10 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 10240
11 | 10 | Un loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 10444.8
12 | 10 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 32997
13 | 10 | Erection of 33KV indoor switch gear panel/33KV indoor PT panel / Bus section panel / Bus raiser panel | Elect | Labour | SWR10930 | 9847 | EA | 98470
14 | 750 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Elect | Labour | SWR10873 | 83 | KG | 62250
15 | 20 | Supply of Rubber mats ( 6’x3’) size for indoor SS | Elect | Supply | SMR40068 | 1386 | EA | 27720
16 | 1 | Supply of 10ft Aluminium Ladder | Elect | Supply | SMR12378 | 1654 | EA | 1654
17 | 2 | Supply of TrollyMounted Co2 Cylinders(IS-2878) | Elect | Supply | SMR40087 | 9240 | EA | 18480
18 | 2 | Supply of Fire bucket stand with 3 buckets (8 -10 ltr capacity) | Elect | Supply | SMR40088 | 1386 | SET | 2772
19 | 6 | Supply of Room fire extinguisher (2 ltrs capacity) for control room | Elect | Supply | SMR40089 | 4620 | EA | 27720
20 | 4 | Supply of Safety Helmet of standard make | Elect | Supply | SMR40071 | 231 | EA | 924
21 | 4 | Supply of Earth Rods (8ft) Screw & clamp type | Elect | Supply | SMR40066 | 578 | EA | 2312
22 | 4 | Supply of Hand Gloves | Elect | Supply | SMR40067 | 289 | SET | 1156
23 | 1 | Supply of Stand basic cell phone with charger | Elect | Supply | SMR40069 | 1386 | EA | 1386
24 | 1 | Supply Steel almarah(61/2 X 3ft) Godrej | Elect | Supply | SMR40061 | 9818 | EA | 9818
25 | 1 | Supply of Table (3x6ft) Godrej | Elect | Supply | SMR40057 | 6050 | EA | 6050
26 | 4 | Supply of S type chairs (Godrej) | Elect | Supply | SMR40058 | 924 | EA | 3696
27 | 1 | Supply Angle racks(18x36.6inches) Godrej | Elect | Supply | SMR40060 | 1733 | EA | 1733
28 | 10 | Supply of Danger boards with clamps | Elect | Supply | SMR40070 | 116 | EA | 1160
29 | 1 | Supply of 33/11kv S.S Permanent name board | Elect | Supply | SMR40086 | 10238 | EA | 10238
30 | 1 | Supply of Wall clock standard make | Elect | Supply | SMR40059 | 578 | EA | 578
31 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579-1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. | Elect | Supply | SMR40063 | 4925 | SET | 4925
32 | 1 | Supply of Rechargeable LED torch light of Standard make | Elect | Supply | SMR40064 | 1733 | EA | 1733
33 | 1 | Supply of Hack saw (12 inches) | Elect | Supply | SMR40065 | 289 | EA | 289
34 | 8 | Supply of LC Boards | Elect | Supply | SMR40072 | 116 | EA | 928
35 | 2 | Supply of Gum Boots | Elect | Supply | SMR40073 | 693 | EA | 1386
36 | 1 | Supply of Digital clamp meter. | Elect | Supply | SMR40076 | 2888 | EA | 2888
37 | 1 | Supply of 5000v megger | Elect | Supply | SMR40074 | 13860 | EA | 13860
38 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard | Elect | Labour | SWR20032 | 1654 | EA | 1654
39 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Elect | Labour | SWR22090 | 2205 | EA | 2205
40 | 6 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE /CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast lluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, verylow mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty i. 90W LED Fixture set | Elect | Supply | SMR11594 | 8200 | EA | 49200
41 | 26 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication including earthing pipe with materials | Elect | Supply | SMR11482 | 3486 | EA | 90636
42 | 2 | Supply of GI earth pipe with 40 mm dia,3mm thcikness with 2.0 M Length | Elect | Supply | SMR11480 | 698 | EA | 1396
43 | 7.92 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc including cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 52105.68
44 | 90 | LAYING OF 33KV, 11KV UG CABLE - Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road- LT 3 1/2 x 185 Sqmm Cable - Single Run | Elect | Labour | SWR11923 | 377.63 | M | 33986.7 | Full text
45 | 10 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) -LT 3 1/2 x 185 Sqmm Cable - Single Run | Elect | Labour | SWR11959 | 85.43 | M | 854.3 | Full text
46 | 2 | Supply of 31/2x185Sqmm UG O/D end term kit | Elect | Supply | SMR40140 | 550 | EA | 1100
47 | 2 | Making of Outdoor/Indoor End Termination - LT 3 1/2 x 185 Sqmm Cable | Elect | Labour | SWR10765 | 968.9 | EA | 1937.8
48 | 50 | Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.- In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-11KV 3x185 Sqmm Cable-Single Run | Elect | Labour | SWR11920 | 465.46 | M | 23273
49 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - 11 KV 3x185 Sqmm Cable -Single Run | Elect | Labour | SWR11956 | 126.23 | M | 1893.45
50 | 377.6 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication - 75x 8mm MS Flat / GI Flat. | Elect | Labour | SWR10920 | 65 | RMT | 24544
51 | 416 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication - GI Flat 25 x 3 mm (including material). | Elect | Labour | SWR10921 | 68 | RMT | 28288
52 | 16 | Loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10199 | 1024 | EA | 16384
53 | 16 | Un Loading of 11 KV VCBs along with Panel boards | Elect | Labour | SWR10517 | 1044.48 | EA | 16711.68
54 | 16 | Erection of 11KV indoor switch gear panel/indoor PT panel / Bus section panel / Bus raiser panel/Capacitor panel/Switch fuse panel for DTR. | Elect | Labour | SWR10931 | 8894 | EA | 142304
55 | 1 | LOADING of 11 KV AB SWCH Con 200/400 A | Elect | Labour | SWR10238 | 80 | EA | 80
56 | 1 | UNLOADING of 11 KV AB SWCH Con 200/400 A | Elect | Labour | SWR10556 | 80 | EA | 80
57 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR20102 | 1813.49 | EA | 1813.49
58 | 1 | LOADING of 11 KV HG Fuse Sets | Elect | Labour | SWR10231 | 18 | EA | 18
59 | 1 | UNLOADING of 11 KV HG Fuse Sets | Elect | Labour | SWR10549 | 18 | EA | 18
60 | 1 | Erection of 11 KV HG Fuse set including earthing | Elect | Labour | SWR10395 | 740.52 | SET | 740.52
61 | 1 | Loading 220 V Battery with Charger | Elect | Labour | SWR11166 | 1612 | SET | 1612
62 | 1 | Un-loading 220 V Battery with Charger | Elect | Labour | SWR11147 | 1024 | SET | 1024
63 | 1 | Erect-220V Batery with Chrgr incl all-SS | Elect | Labour | SWR11772 | 6442.58 | EA | 6442.58
64 | 2 | Fabrication and laying of ladder in cable trench | Elect | Labour | SWR22088 | 788 | EA | 1576
65 | 6 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Elect | Labour | SWR10956 | 1268 | EA | 7608
66 | 2.05 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of substation structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete - Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 4471.05
67 | 2.05 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of substation structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete- Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 1744.55
68 | 2.05 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of substation structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete - Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 2650.65
69 | 2.05 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of substation structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete - Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 988.1
70 | 1 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 142
71 | 2 | Transport of 8MVA Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading ) | Elect | Labour | SWR10854 | 21945 | EA | 43890
72 | 2 | Loading of 8MVA PTR on constructed plinth | Elect | Labour | SWR10613 | 5805.84 | EA | 11611.68
73 | 2 | Un Loading of 8MVA PTR on constructed plinth | Elect | Labour | SWR10627 | 5805.84 | EA | 11611.68
74 | 2 | Erection of 8 MVA PTR on constructed plinth | Elect | Labour | SWR21321 | 49480.2 | EA | 98960.4
75 | 26 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 32089.2
76 | 26 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 10036
77 | 2 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 2468.4
78 | 12 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) - Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 39596.4
79 | 2.05 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10868 | 6852 | TO | 14046.6
80 | 150 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC -33 KV 3x400 Sqmm Cable - Double Run | Elect | Labour | SWR11972 | 749 | M | 112350
81 | 150 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC -11 KV 3x300 Sqmm Cable - Double Run | Elect | Labour | SWR11973 | 631.06 | M | 94659
82 | 4 | Making of Outdoor/Indoor End Termination -33 KV 3x400 Sqmm Cable | Elect | Labour | SWR10387 | 2764.76 | EA | 11059.04
83 | 4 | Making of Outdoor/Indoor End Termination 11 KV 3x300 Sqmm Cable | Elect | Labour | SWR10391 | 2370.63 | EA | 9482.52
84 | 2 | Making of Outdoor/Indoor End Termination 11 KV 3x185 Sqmm Cable | Elect | Labour | SWR10390 | 2370.63 | EA | 4741.26
85 | 3 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 7931.49
86 | 6 | LOADING of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 456
87 | 6 | UNLOADING of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 300
88 | 6 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 6792
89 | 1.75 | Loading of M.S.Channels, Angles, Flats & Rods etc. | Elect | Labour | SWR10206 | 221 | TO | 386.75
90 | 1.75 | Unloading of M.S.Channels, Angles, Flats & Rods etc. | Elect | Labour | SWR10524 | 185 | TO | 323.75
91 | 3.25 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) - Above 10 KM and upto 20 KM | Elect | Labour | SWR10132 | 412.08 | TO | 1339.26
92 | 0.279 | Mass Concreting for pole - Coping & Muffling of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 1086.147
93 | 9.27 | Earth work excavation of in all soils except hard rock requiring blasting. | Elect | Labour | SWR20768 | 345 | M3 | 3198.15
94 | 300 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 61230
95 | 8 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 8192
96 | 8 | Unloading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 8192
97 | 7 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) - Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 23097.9
98 | 480 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable - Double Run. | Elect | Labour | SWR11980 | 1388.84 | M | 666643.2
99 | 100 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe)-33 KV 3x400 Sqmm Cable - Double Run. | Elect | Labour | SWR11988 | 1587.07 | M | 158707
100 | 470 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC- 33 KV 3x400 Sqmm Cable - Double Run. | Elect | Labour | SWR11972 | 749 | M | 352030
101 | 1050 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 214305
102 | 210 | HDD (Horizontal Directional Drilling) in normal soil - Laying of 33&11KV UG cable by HDD method with casing HDPE pipe of 160mm PN4 PE 80 as per IS4984 | Elect | Labour | SWR11001 | 6993 | M | 1468530
103 | 75 | Raising of double run 33 KV 3x400 Sqmm cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR12004 | 323.85 | M | 24288.75
104 | 16 | Making of Outdoor/Indoor End Termination - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR10387 | 2764.76 | EA | 44236.16
105 | 14 | UG Cables Joints - Making of Straight through joints - 33 KV 3 x 400 Sqmm XLPE Cable | Elect | Labour | SWR10382 | 5700.78 | EA | 79810.92
106 | 100 | Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | Elect | Supply | SMR40077 | 363 | M | 36300
107 | 400 | Supply of 6" B class GI pipe(5mm thck 20Kg/Mtr) including Cost of Pipes and slabs | Elect | Supply | SMR40081 | 1044 | M | 417600
108 | 50 | supply of 6" DWC pipe including Cost of Pipes and slabs | Elect | Supply | SMR11610 | 1012 | M | 50600
109 | 1050 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 31500
110 | 2 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 252
111 | 2 | Un loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 158
112 | 2 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 9000
113 | 5.25 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc including cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 34539.75
114 | 0.155 | Mass Concreting for pole - Coping & Muffing of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 603.415
115 | 10 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 5125.5
116 | 5 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 13219.15
117 | 10 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 760
118 | 10 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 500
119 | 10 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 11320
120 | 10.325 | Loading of M.S.Channels, Angles, Flats & Rods etc. | Elect | Labour | SWR10206 | 221 | TO | 2281.825
121 | 10.325 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10524 | 185 | TO | 1910.125
122 | 12.85 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) - Above 10 KM and upto 20 KM | Elect | Labour | SWR10132 | 412.08 | TO | 5295.228
123 | 55 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading) - Trans 11/12.5/12.9M Spun pole upto 50KM | Elect | Labour | SWR11181 | 858 | EA | 47190
124 | 55 | LOADING of 12.5M SPUN POLE | Elect | Labour | SWR10190 | 548 | EA | 30140
125 | 55 | UNLOADING of 12.5M SPUN POLE | Elect | Labour | SWR10508 | 363 | EA | 19965
126 | 55 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Spun poles 12.5 Mtrs / 12.9Mtrs PSCC | Elect | Labour | SWR10350 | 4521.66 | EA | 248691.3
127 | 30 | Excavation of pits in all soils except hard rock requiring blasting - 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") 1.94 cum | Elect | Labour | SWR10109 | 842.78 | EA | 25283.4
128 | 25 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") | Elect | Labour | SWR11041 | 1466.25 | EA | 36656.25
129 | 93.83 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc including cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 617307.57
130 | 6 | Supply of M+3 Tower (Galvanized) | Elect | Supply | SMR11683 | 140674.3 | EA | 844045.8
131 | 6 | Erection of M+3 Tower (Galvanized) | Elect | Labour | SWR11850 | 64576 | EA | 387456
132 | 12 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) | Elect | Supply | SMR11684 | 28520.64 | EA | 342247.68
133 | 12 | Erection of Extension of 3Mtrs for M+3 (Galvanized) | Elect | Labour | SWR11851 | 5168.95 | EA | 62027.4
134 | 3 | Excavation of pits in all soils except hard rock requiring blasting - M-Type Tower (1.2M x 1.2M x 3.3M ) 4.752cum | Elect | Labour | SWR12085 | 1997.93 | EA | 5993.79
135 | 3 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) M-Type Tower (1.2M x 1.2M x 3.3M ) 4.752cum | Elect | Labour | SWR12090 | 3592.95 | EA | 10778.85
136 | 15 | S&E-Smart RFID marker Smart RFID markers SM1500 Power RFID based Electronic cable/pipe marker | Elect | Labour | SWR25089 | 2745 | EA | 41175
137 | 1 | Submission of auto CAD Drawing as per pole schedule (Detailed survey and sketch) - up to 10 KM | Elect | Labour | SWR12104 | 6000 | LS | 6000
138 | 2.3 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location - 100 Sqmm Double Circuit (6 Conductors) | Elect | Labour | SWR10704 | 26255.98 | KM | 60388.754
139 | 10 | Formation of Cut point for 33 KV Double circuit line excluding pole erection and stays | Elect | Labour | SWR10466 | 3198.72 | EA | 31987.2
140 | 1.9 | Dismantling of 11KV 34/55 sqmm SC | Elect | Labour | SWR22065 | 4500 | KM | 8550
141 | 1.9 | Restringing of existing loose Lines by removing the pin-binding and jumpers, Providing of temporary stays, providing stiffners pieces, replacement of damaged insulators, alignment of cross arms, pin binding and jumpering after tensioning and removing of the temporary stays complete - with 55 Sqmm single ckt 3 cond | Elect | Labour | SWR11308 | 6616 | KM | 12570.4
142 | 5 | LOADING of Conductor drums | Elect | Labour | SWR10191 | 202 | EA | 1010
143 | 5 | UNLOADING of Conductor drums | Elect | Labour | SWR10509 | 100 | EA | 500
144 | 252 | LOADING of 33 KV Pin insulators | Elect | Labour | SWR10211 | 3 | CRT | 756
145 | 252 | UNLOADING of 33 KV Pin insulators | Elect | Labour | SWR10529 | 3 | CRT | 756
146 | 144 | LOADING of 33 & 11 KV Disc insulators | Elect | Labour | SWR12416 | 2 | CRT | 288
147 | 144 | UNLOADING of 33 & 11 KV Disc insulator | Elect | Labour | SWR10631 | 2 | CRT | 288
148 | 6 | LOADING of 33KV Metal parts-bag of 25no | Elect | Labour | SWR10618 | 65 | BAG | 390
149 | 6 | UNLOADING of 33 KV Metal parts-bagof 25 | Elect | Labour | SWR10632 | 65 | BAG | 390
150 | 4.2 | Transport of steel including line materials such as cross arms, clamps, hardware, cable (loose) and other line materials (Including loading and unloading) - Above 10 KM and upto 20 KM | Elect | Labour | SWR10148 | 481.44 | TO | 2022.048
151 | 50 | Supply of GI wire No 8 Including cost of Earthing pipe and materials | Elect | Supply | SMR11486 | 105 | KG | 5250
152 | 2 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 293.26
153 | 3150 | Supply of GI Bolts & Nuts,Washers etc.,including earthing pipe with materials | Elect | Supply | SMR11488 | 117.5 | KG | 370125
154 | 6 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication including earthing pipe with materials | Elect | Supply | SMR11482 | 3486 | EA | 20916
155 | 6 | Loading of CI earth pipe 100 mm dia, 2.75 mt long | Elect | Labour | SWR10263 | 29 | EA | 174
156 | 6 | Unloading of CI earth pipe 100 mm dia, 2.75 mt long | Elect | Labour | SWR10581 | 29 | EA | 174
157 | 12 | Earthing of Substation - Supply of GI pipe 40 mm dia, 2 mtrs, 3mm thickness with bolts and nuts | Elect | Supply | SMR40091 | 733 | EA | 8796
158 | 12 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 14810.4
159 | 5000 | Cut-Tree Branch(LT/11/33)&Trnsprt Debris | Elect | Labour | SWR23200 | 4 | EA | 20000
160 | 100 | Providing of guarding to the telephone line / Electrical Line /road crossings including fixing the cross arms, providing protective guard in complete shape | Elect | Labour | SWR10372 | 2310 | EA | 231000
161 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 2316
162 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 7405.2
163 | 19 | Excavation of pits in all soils except hard rock requiring blasting - 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Elect | Labour | SWR10107 | 700 | EA | 13300
164 | 14.8 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc including cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 97369.2
165 | 25 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 12100
166 | 14 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 12 Mtr | Elect | Labour | SWR11267 | 3901.37 | EA | 54619.18
167 | 28 | LOADING of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 2128
168 | 28 | UNLOADING of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 1400
169 | 0.372 | Mass Concreting for pole - Coping & Muffing of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 1448.196
170 | 2 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 2048
171 | 2 | Unloading of 11KV/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 2048
172 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) - Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 6599.4
173 | 8 | Making of Outdoor/Indoor End Termination - 11 KV 3x300 Sqmm Cable | Elect | Labour | SWR10391 | 2370.63 | EA | 18965.04
174 | 2 | UG Cable joints - Making of Straight through joints - 11 KV 3x300 Sqmm Cable | Elect | Labour | SWR10386 | 3725.45 | EA | 7450.9
175 | 150 | Supply of 4" B class GI pipe (3.65 mm thck 12.2 Kg/Mtr) including cost of pipes and slabs | Elect | Supply | SMR40080 | 740 | M | 111000
176 | 40 | Hard Rock Cutting 11KV - Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 1200
177 | 4 | LOADING of 11 KV AB SWCH Con 200/400 A | Elect | Labour | SWR10238 | 80 | EA | 320
178 | 4 | UNLOADING of 11 KV AB SWCH Con 200/400 A | Elect | Labour | SWR10556 | 80 | EA | 320
179 | 4 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR10393 | 3200 | EA | 12800
180 | 4 | Excavation of pits in all soils except hard rock requiring blasting - 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Elect | Labour | SWR10107 | 700 | EA | 2800
181 | 1 | Excavation of pits in all soils except hard rock requiring blasting 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Elect | Labour | SWR10107 | 700 | EA | 700
182 | 0.031 | Mass Concreting for pole - Coping & Muffing of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 120.683
183 | 2 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 1025.1
184 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2643.83 | EA | 2643.83
185 | 2 | LOADING of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 152
186 | 2 | UNLOADING of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 100
187 | 2 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 2264
188 | 0.45 | Loading of M.S.Channels, Angles, Flats & Rods etc. | Elect | Labour | SWR10206 | 221 | TO | 99.45
189 | 0.45 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10524 | 185 | TO | 83.25
190 | 50 | Supply of earthing pipe with materials - Supply of GI Flat 25X3 mm | Elect | Supply | SMR11485 | 105 | KG | 5250
191 | 4 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 586.52
192 | 6 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication including earthing pipe with materials | Elect | Supply | SMR11482 | 3486 | EA | 20916
193 | 1.25 | Stringing of HT AB Cable- 11 KV 3x185+70 Sqmm AB Cable with GI Metal Parts | Elect | Labour | SWR10454 | 41876.1 | KM | 52345.125
194 | 30 | End Termination of AB cable (each lead): Supply of 11KV 3x185+70sq.mm/ 3x70+70sq.mm/3x35+35sq.mm AB cable end Kits | Elect | Supply | SMR11504 | 950 | SET | 28500
195 | 0.95 | Transport of steel including line materials such as cross arms, clamps, hardware, cable (loose) and other line materials (Including loading and unloading) - Above 10 KM and upto 20 KM | Elect | Labour | SWR10148 | 481.44 | TO | 457.368
196 | 100 | S-GI Bolts & Nuts,Washers etc.,including earthing pipe with materials | Elect | Supply | SMR11488 | 117.5 | KG | 11750
197 | 50 | Drilling of holes upto 20 mm dia using power drills - MS Channel, Angles and flat | Elect | Labour | SWR10307 | 4 | EA | 200
198 | 30 | Cutting charges for MS Sections - MS Channel 100 x 50 mm | Elect | Labour | SWR10294 | 10 | EA | 300
199 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - 11 Mtrs PSCC poles | Elect | Labour | SWR10978 | 4336.85 | EA | 17347.4
200 | 4 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading) - 11 Mtrs long PSCC Poles | Elect | Labour | SWR11180 | 431.97 | EA | 1727.88
201 | 4 | LOADING of 9.1M PSCC POLE | Elect | Labour | SWR10188 | 182 | EA | 728
202 | 4 | UNLOADING of 9.1M PSCC POLE | Elect | Labour | SWR10506 | 91 | EA | 364
203 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 7405.2
204 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 2316
205 | 1 | LOADING of Conductor drums | Elect | Labour | SWR10191 | 202 | EA | 202
206 | 1 | UNLOADING of Conductor drums | Elect | Labour | SWR10509 | 100 | EA | 100
207 | 5.15 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc including cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 33881.85
208 | 18 | LOADING of 33 & 11 KV Disc insulators | Elect | Labour | SWR12416 | 2 | CRT | 36
209 | 18 | UNLOADING of 33 & 11 KV Disc insulator | Elect | Labour | SWR10631 | 2 | CRT | 36
210 | 1 | LOADING of 11 KV Metal parts | Elect | Labour | SWR12402 | 48 | BAG | 48
211 | 1 | UNLOADING of 11 KV Metal parts Bag | Elect | Labour | SWR12421 | 48 | BAG | 48
212 | 30 | Laying of XLPE UG cable Triple or more Run including excavation of trench of size 1000mm wide to 750mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) -11 KV 3x300 Sqmm Cable - Triple Run | Elect | Labour | SWR12025 | 1805.4 | M | 54162
213 | 20 | Laying of XLPE UG cable Triple or more Run including excavation of trench of size 1000mm wide to 750mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC -11 KV 3x300 Sqmm Cable - Triple Run. | Elect | Labour | SWR12014 | 780.3 | M | 15606
214 | 20 | Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road - 11 KV 3x300 Sqmm Cable - Single Run | Elect | Labour | SWR11919 | 465.46 | M | 9309.2
215 | 420 | Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - Along the CC / BT multi layer road requiring compressor - 11 KV 3x300 Sqmm Cable -Single Run | Elect | Labour | SWR11928 | 1073.94 | M | 451054.8
216 | 40 | Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtr - Across the CC/ BT road crossing multi layer road requiring compressor wih hume pipe (cxcluding the cost of Hume Pipe) - 11 KV 3x300 Sqmm Cable -Single Run | Elect | Labour | SWR11937 | 1199.4 | M | 47976
217 | 100 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 20410
218 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - 11 KV 3x300 Sqmm Cable -Single Run | Elect | Labour | SWR11955 | 144.08 | M | 2881.6
219 | 30 | End Termination of AB cable (each lead):120 Sqmm to 185 Sqmm | Elect | Labour | SWR10667 | 800 | EA | 24000
220 | 15 | Straight through joints of AB cable (each lead) - Supply and erection Angle line Asmbly kits | Elect | Labour | SWR10673 | 2124 | EA | 31860
221 | 32 | Straight through joints of AB cable (each lead) - Supply and erection Straight line Asmbly kits | Elect | Labour | SWR10672 | 1661 | EA | 53152
222 | 10 | Erection of Assemble Kit for 'T' Branche | Elect | Labour | SWR10671 | 1800 | EA | 18000
223 | 32 | Erection of I Hook | Elect | Labour | SWR12099 | 55 | EA | 1760
224 | 32 | Supply of I Hook | Elect | Supply | SMR12099 | 158 | EA | 5056
225 | 6 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 27000
226 | 4 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 3520
227 | 100 | Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road - 33 KV 3x400 Sqmm Cable- Single Run | Elect | Labour | SWR11918 | 572.1 | M | 57210
228 | 50 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - 33 KV 3x400 Sqmm Cable - Single Run | Elect | Labour | SWR11954 | 135.66 | M | 6783
229 | 6 | Making of Outdoor/Indoor End Termination - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR10387 | 2764.76 | EA | 16588.56
230 | 2 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 2048
231 | 2 | Unloading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 2088.96
232 | 6 | LOADING of 33 KV AB SWCH Con 400/800 A | Elect | Labour | SWR10239 | 126 | EA | 756
233 | 6 | UNLOADING of 33 KV AB SWCH Con 400/800 A | Elect | Labour | SWR10557 | 79 | EA | 474
234 | 3 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) - Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 9899.1
235 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc - Erection of 33 KV VCB with Control Panel | Elect | Labour | SWR10460 | 12500 | EA | 25000
236 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc - Erection of 33 KV CTs | Elect | Labour | SWR10399 | 1079 | SET | 2158
237 | 7.77 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Elect | Labour | SWR20685 | 5160 | M3 | 40093.2
238 | 3 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Elect | Supply | SMR40051 | 13913 | EA | 41739
239 | 3 | Erection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 4137
240 | 3 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast lluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, verylow mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty - 90W LED Fixture set | Elect | Supply | SMR11594 | 8200 | EA | 24600
241 | 3 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Elect | Labour | SWR10956 | 1268 | EA | 3804
242 | 60 | Labour for Fixing of all types of clamps | Elect | Labour | SWR10917 | 65 | EA | 3900
243 | 2600 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Elect | Labour | SWR11879 | 27 | M | 70200
244 | 13.65 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc including cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 89803.35
245 | 0.403 | Mass Concreting for pole - Coping & Muffing of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 1568.879
246 | 13 | Excavation of pits in all soils except hard rock requiring blasting - 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Elect | Labour | SWR10107 | 700 | EA | 9100
247 | 20 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 10251
248 | 10 | Erection of in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr pole | Elect | Labour | SWR11266 | 2643.83 | EA | 26438.3
249 | 20 | LOADING of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1520
250 | 20 | UNLOADING of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 1000
251 | 20 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 22640
252 | 2.6 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10206 | 221 | TO | 574.6
253 | 2.6 | Unloading of M.S.Channels, Angles, Flats & Rods etc., | Elect | Labour | SWR10524 | 185 | TO | 481
254 | 7.6 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) - Above 10 KM and upto 20 KM | Elect | Labour | SWR10132 | 412.08 | TO | 3131.808
255 | 0.095 | Extention of 33KV Bay at 132/33KV Sub-station - Supply of Zebra conductor | Elect | Supply | SMR24910 | 299369.05 | KM | 28440.0598
256 | 12 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Elect | Labour | SWR10884 | 224 | EA | 2688
257 | 20 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication including earthing pipe with materials | Elect | Supply | SMR11482 | 3486 | EA | 69720
258 | 18 | Extention of 33KV Bay Extn: Supply of T Clamps | Elect | Supply | SMR24912 | 500 | EA | 9000
259 | 9 | Extention of 33KV Bay Extn: Supply of Twin Zebra Connector | Elect | Supply | SMR24911 | 600 | EA | 5400
260 | 10 | Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | Elect | Labour | SWR10860 | 2113 | M3 | 21130
261 | 20 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 24684
262 | 20 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elect | Labour | SWR10359 | 386 | EA | 7720
263 | 200 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR12510 | 27 | EA | 5400
Civil
1 | 14.8 | Earth work excavation in hard rock boulders more than 3 M3 size by using chijlling,benching,wedging and boring in rock complete for finished item of work | Civil | Labour | SWR33018 | 855 | M3 | 12654
2 | 728.57 | Earth work excavation and depositing on bank with initial lead of 10m and initial lift of 3m in Loamy & Clayey Soils like BC Soils, Red Earth & Ordinary Gravelly Soils ( SS 20-B) including all operational incidental labour charges such as shoring, strutting, sheeting, planking and dewatering including cost of hire charges of T & P, labour charges etc., complete for finished item of work including seignerage charges excluding dewatering charges etc., complete for Foundation of Building.(APSS No. 308) | Civil | Labour | SWR33015 | 464 | M3 | 338056.48
3 | 183.96 | Filling with already available Earthwork in basement with 150mm thick layers incldg cost & conveyance all materials watering,consolidation etc complete for finished item of work. | Civil | Labour | SWR33055 | 38 | M3 | 6990.48
4 | 81.55 | Plain Cement contrete (1:4:8) using 40mm Plain Cement contrete (1:4:8) using 40 mm metal with concrete Mixture. All work upto Plinth level including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete. | Civil | Labour | SWR33028 | 4593 | M3 | 374559.15
5 | 38.67 | RCC M - 20 (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work. a) Column Footings | Civil | Labour | SWR33098 | 9237 | M3 | 357194.79
6 | 23.34 | RCC M - 20 (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all material as directed by Engineer incharge of the work. b) Columns" | Civil | Labour | SWR33100 | 12824 | M3 | 299312.16
7 | 6.32 | RCC M - 20 (1:1.5:3) Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work c)Plinth Beams | Civil | Labour | SWR33099 | 11980 | M3 | 75713.6
8 | 14.51 | RCC M - 20 (1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all mater as directed by Engineer incharge of the work. d)Roof Beams" | Civil | Labour | SWR33121 | 11897 | M3 | 172625.47
9 | 1.63 | RCC M - 20 (1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work e)Lintels | Civil | Labour | SWR33107 | 12653 | M3 | 20624.39
10 | 20.25 | RCC M - 20 (1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete but excluding cost of steel and its fabrication charges for finished item of work, but excluding centering, shuttering as directed by Engineer incharge of the work e)Sunshades | Civil | Labour | SWR33114 | 1327 | M2 | 26871.75
11 | 54.21 | RCC M - 20 (1:1.5:3)Nominal mix (Cement:fine aggregate: coarse aggregate) corresponding to Table 9 of IS 456 using 20mm size graded machine crushed hard granite metal (coarse aggregae) from approved quarry including cost and conveyance of all material as directed by Engineer incharge of the work. / h) Roofslab & Staircase "150mm | Civil | Labour | SWR33128 | 11381 | M3 | 616964.01
12 | 17 | Supplying, fitting and placing HYSD bar reinforcement in foundation complete as per drawings and technical specifications for Bars below 36 mm dia including over laps and wastage, where they are not welded,complete as directed by Engineer incharge of the work. | Civil | Labour | SWR33144 | 80322 | TON | 1365474
13 | 176.49 | Coursed rubble stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33041 | 4714 | M3 | 831973.86
14 | 96.55 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 118 | M2 | 11392.9
15 | 119.13 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for finished item of work - Ground Floor | Civil | Labour | SWR33068 | 8102 | M3 | 965191.26
16 | 475.6 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification as directed by Engineer incharge of the work. | Civil | Labour | SWR33052 | 257 | M3 | 122229.2
17 | 1525.98 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33163 | 532 | M2 | 811821.36
18 | 290.72 | Providng impervious coat to exposed RCC roof slab surface with CM(1:3), 20 mm thick with 1kg of water proof compound per bag of cement laid over roof when it is green including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33156 | 555 | M2 | 161349.6
19 | 9.9 | RCM Drop wall 50mm CM (1:2) facia 4cm thick for drop walls, fins with rabbit wire mesh & nominal reinforcemet as directed by Engineer-in-change with dubara sponge finishing, including cost & conveyance of all materials to site, seigniorage charges, sales & incidental, cost and conveyance of cement, wire mesh, water to work site, centering, scaffolding and form work, lift changes etc., complete for finished items of work but excluding cost of steel & its fabrication charges, for finished item of work. (APSS No.403 & 903). | Civil | Labour | SWR33203 | 2892 | M2 | 28630.8
20 | 54.12 | Supply & fixing Aluminimum Anodised Two/Three Track Sliding Windows as per approved drawing with aluminium anodised sections of Series C Jindal sections and outer frame top horizontals & both verticals of 8774 of size 62 x 29.5 mm and bottom horizontal - two track frame of 8773 of size 62 x 29.5 mm, Shutter frame top, bottom and verticals of 8304 of size 50 mm x 20 mm and Weather interlocking frame of 8306 of size 50 x 20 with plain clear float glass 5mm thick fixed including Supply & fixing aluminium handles of 100 mm for each shutter, nylon rollers assembly and all labour charges for fixing the fixtures with required no. of screws, bolts and nuts and includingt labour charges for fixing the frame in position, fixing shutter to frame etc. completed for finished item of work | Civil | Labour | SWR33277 | 3472 | M2 | 187904.64
21 | 54.12 | Supply & fixing of ms grill to windows with outer frame of ISA2525 of 25mm thick , horizontal and vertical square rods of 10x10mm and paintng with synthetic enamel paint per (0.3 x 1.2 )sqm. | Civil | Labour | SWR33310 | 2913 | M2 | 157651.56
22 | 26.65 | Supplying & fixing collapsible steel shutters with vertical, double channel of 20 x10x2 mm of 100 mm centre ,Bracers with flat iron 40x40x6 mm with 38 mm dia steel pulleys, the top, bottom and side vertical frames of the collapsible gate with 65x65mmx8mm MS Angle and middle guide rail at site height with 65mmx8mm MS flat for the pulleys to guide and fixed with necessary hold fasts, bolts, nuts, rivets, locking arrangements, stoppers, handles, all accessories all fixtures and painted with one coat of approved steel primer etc., complete for finished item of work as per special spn 1105. | Civil | Labour | SWR33411 | 3876 | M2 | 103295.4
23 | 6.05 | Flush type Doors with 35mm Thick Flush Shutters with Bondwood solied Block Board Type Faced on Both the sides with Commercial Type Plywood (Schedule Item No. 301.) complete for finished item of work. | Civil | Labour | SWR33264 | 7040 | M2 | 42592
24 | 15.94 | Flooring with cermic tiles of set over base coat of cement mortar (1:8) 12 mm thick over CC bed already laid or RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, sand, water and tiles etc., complete, including seigniorage charges, etc., complete for finished item of work . | Civil | Labour | SWR33224 | 886 | M2 | 14122.84
25 | 202.82 | Flooring with polished shahabad stones 15 to 18mm thick set over base coat of CM (1:8) over already laid CC bed /RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed with neat cement to full depth including cost of all materials like cement, sand, and water and flooring stones etc., complete, including seigniorage charges, labour charges for dresing of flooring stones etc., complete for finished item of work . | Civil | Labour | SWR33219 | 763 | M2 | 154751.66
26 | 20.37 | Flooring with decorated white back ground glazed tiles, set over base coat of cement mortar (1:6) 12 mm thick over CC bed already laid or RCC Roof Slab, including neat cement slurry of honey like consistency spread @ 3.3 kgs per sqm. & jointed neatly with white cement paste mixed with pigment of matching shadeto full depth, including cost of all materials like cement, sand, water and tiles etc., complete, including seigniorage charges, etc., complete for finished item of work . | Civil | Labour | SWR33226 | 903 | M2 | 18394.11
27 | 21.75 | Providing skirting to internal walls to 15 cm height/risers of steps with ...mm thick polished Shahabad stone length equal to polished stones, set over base coat of CM (1:3) 12 mm thick with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointed with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like Shahabad stone, cement, sand and water etc., complete, including seigniorage charges, etc., complete for finished item of work as directed by Engineer incharge of the work. | Civil | Labour | SWR33236 | 849 | M2 | 18465.75
28 | 686.1 | Painting to new walls with 2 coats of ready mixed oil bound wahsable distemper of approved brand and shade over a base coat of appropriate primer of approved brand, making 3 coats in all to give an even shade after thourughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, incidental, labour charges etc. complete for finished item of work as per SS 911 for internal walls as directed by Engineer incharge of the work | Civil | Labour | SWR33333 | 140 | M2 | 96054
29 | 1000.36 | Paint-Plastic Emulsn 2Coats-Extrnl GFlr | Civil | Labour | SWR33356 | 202 | M2 | 202072.72
30 | 22.27 | Supplying and fixing Alluminium glazed door cum fixed window or door using anodised alluminium extruded sections and mat finish for frames sites and Handle/knib,locking arrangements and 4.0mm plain glass fixed to the frame with beeding and qasket with all required item of work. | Civil | Labour | SWR33272 | 5919 | M2 | 131816.13
31 | 19.67 | Plain Cement contrete (1:2:4) Nominal Mix using 20 mm metal using concrete mixer including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete. | Civil | Labour | SWR33030 | 6008 | M3 | 118177.36
32 | 7730 | Supply and fabrication of Structural steel angles,chanales and beams etc. including labour charges complete for the finished item of work. | Civil | Labour | SWR33145 | 125 | KG | 966250
33 | 365 | Supply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 118 | M | 43070
34 | 1 | Supply & fixing 4 way TPN Distribution board with IP-42 protection suitable for 3 phase 40A FP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 12Nos as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 10804 | EA | 10804
35 | 20 | Supply & fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 160 | EA | 3200
36 | 16 | Supply & fixing of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 470 | EA | 7520
37 | 74 | Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A modular type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 648 | EA | 47952
38 | 48 | Supply & Fixing of 28W T5 fluorescent tube. Makes : Crompton / Bajaj / Phillips / Surya / Havells with copper choke,starter etc.,incuding 1No 40W tube etc., complete. | Civil | Labour | SWR33558 | 139 | EA | 6672
39 | 16 | Supply of 12" (300mm)ISI, 900 RPM Light duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 1838 | EA | 29408
40 | 375 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 70 | M | 26250
41 | 400 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 97 | M | 38800
42 | 20 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 137 | EA | 2740
43 | 12 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2571 | EA | 30852
44 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 3695 | EA | 3695
45 | 20 | Supplying, laying, jointing and testing 101.4 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 740 | M | 14800
46 | 4 | Constructing 457.2 mm x 457.2 mm (1'6"x1'6") brick in CM 1:6 prop. Masonry. Inspection chamber up to 914.4 mm (3'0") and fitted with light weight 457.2 mm x 457.2 mm (1'6"x1'6") C.I frame and cover of 20 Kg. | Civil | Labour | SWR34296 | 8607 | EA | 34428
47 | 4 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 123 | EA | 492
48 | 4 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 96 | EA | 384
49 | 10 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 451 | M | 4510
50 | 10 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 402 | M | 4020
51 | 2 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 738 | EA | 1476
52 | 1 | Supplying and Fixing European Water Closet of 1st quality conforming to IS:2556-Part-2-1973 of Hindustan / Neycer or Parryware make white glazed with 'S' trap | Civil | Labour | SWR34314 | 2021 | EA | 2021
53 | 1 | Supplying and Fixing best Indian make plastic seat and lid for European water closets with rubber or plastic Buffers as per IS 2548-1996 | Civil | Labour | SWR34315 | 1278 | EA | 1278
54 | 2 | Supply & fixing 12.7 mm NP stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 696 | EA | 1392
55 | 2 | S&F 12.7 mm N.P bib tap Indian make 400 grams Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 287 | EA | 574
56 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1666 | EA | 1666
57 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 271 | EA | 542
58 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 129 | EA | 258
59 | 1 | Supplying & Fixing low down Plastic flushing tank 10 Lit Capacity Hindustan Sanitary ware/ parry/ Neycer with internal components | Civil | Labour | SWR34376 | 1974 | EA | 1974
60 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 9 | L | 9000
61 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality complete for finished item of work | Civil | Labour | SWR34426 | 31 | EA | 62
62 | 5 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 206 | M | 1030
63 | 60 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 241 | M | 14460
64 | 175 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 281 | M | 49175
65 | 35 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 449 | EA | 15715
66 | 2 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 319 | EA | 638
67 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 421 | EA | 421
68 | 1 | Supply & fixing NP soap dish heavy type with NP screws | Civil | Labour | SWR34429 | 601 | EA | 601
69 | 12 | Clearing of site by hiring JCB, complete for the finished item of work. | Civil | Labour | SWR34179 | 920 | H | 11040
70 | 3.05 | S&F of Glow sign board size 10' x 3' including lettering, labour charges, fitting charges cost of all materials and complete for finished item. | Civil | Labour | SWR33422 | 3553 | M2 | 10836.65
71 | 7500 | Design and submisiion of 2 sets of structural design drawings with soft copy complete finished item of work | Civil | Labour | SWR33426 | 4 | FT2 | 30000
72 | 2 | Providing contour surveying maps with total station including preparation of boundary and contour levels with 2 No.s hard copies and soft copies complete for finished items of work. | Civil | Labour | SWR33427 | 5500 | EA | 11000
73 | 17.5 | Supply and fixing of AC sheets including cost of material labour conveyence etc complete for finished item of work as directed by the engineer in charge. | Civil | Labour | SWR33400 | 375 | M2 | 6562.5
74 | 1 | Making drainage connection in the existing inspection chamber including all repairs. | Civil | Labour | SWR34438 | 235 | EA | 235
75 | 130.3 | Carting away of excavated soils Complete for finished item of work | Civil | Labour | SWR34151 | 280 | M3 | 36484
76 | 14.53 | Dismantling of Brick work including stacking of serviceable materials and disposal of unserviceable materials with 100 metres lead including all operational, incidental, labour charges etc. complete for finished item of work | Civil | Labour | SWR33001 | 300 | M3 | 4359
77 | 1 | Geophysical Investgation charges for water point by Geologist as directed by Engineer in chargecomplete for the finished item of work. | Civil | Labour | SWR33608 | 2500 | EA | 2500
78 | 285 | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete 0 to 90M | Civil | Labour | SWR33609 | 336 | M | 95760
79 | 35 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 787 | M | 27545
80 | 1 | Supply and erecting, ISI mark submersible 3.0HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33627 | 32221 | EA | 32221
81 | 185 | Supply and fixing of HDPE pipe 40mm dia of 6Kg/cSqm including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 245 | M | 45325
82 | 1 | Supply and erecting D.O.L Starter 250V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33644 | 1559 | EA | 1559
83 | 225 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 106 | M | 23850
84 | 15.77 | Supply&Spreading 20mm HBG metal including labour, transport charges complete for finished item of the work. | Civil | Labour | SWR33057 | 1431 | M3 | 22566.87
85 | 246.97 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | M3 | 9878.8
86 | 446 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | M3 | 43485
87 | 475.6 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | M3 | 14268
88 | 40.82 | Plain Cement contrete (1:3:6) Nominal Mix using 40 mm metal using concrete mixer including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete. | Civil | Labour | SWR33029 | 4895 | M3 | 199813.9
89 | 42.5 | Supply and fixing of MS GATE with redoxide and 2 Coats of Anamil paint Complete finished item of work as directed by Engineer - in-charge | Civil | Labour | SWR33404 | 5175 | M2 | 219937.5
TOTAL : | [7 empty] | 20890118.6107
18% GST : | [7 empty] | 3760221.3499
Grand Total | [7 empty] | 24650339.9607
10072284.65
1665154.75
7377476.82
1092512.6
682689.82
10817833.99
20890118.64
0.02925

## Sheet1
Supply of LED fixture set of (LUMINAIREMAKE:PHILIPS/OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA.LEDMAKE:PHILIPSLUMILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Pol Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty.