## Sheet1
Schedule for the work "Power evacuation facility from EHT Bowrampet SS to 33/11 KV Bachupally SS executed from Pragathi nagar Khaman to 33/11KV Bachupally SS with M+6 towers and 100 sqmm AAA SCOH line by tapping to newly proposed 100 sqmm AAA conductor from 132KV Bowrampet SS at Pragathi nagar khaman in Medchal Operation circle in Masterplan Sub-division-1 of WCGH division of RR circle under T&D Improvement works"
1. Memo.No.CGM/MP/Gr.Hyd/F./D.No.1386/23-24, Dt: 31.10.2023.
2. WBS No. S-1654-13-04-01-01-001
Sl.No | Estimate Quantity(Only Figures) | PARTICULARS | Work Type | Item Short Description | SWR No/APSS/Morth cl.No | Rate (INR) (Upto 2 Decimals) | UOM | Amount
1 | 32 | Supply of M+3 Tower (Galvanized) | Elecy | Supply | SMR11683 | 140674.3 | EA | 4501577.6
2 | 32 | Supply of Material for Extension of M+3 Tower by 3M (Galvanized) | Elecy | Supply | SMR11684 | 28520.64 | EA | 912660.48
3 | 32 | Erection of M+3 Tower (Galvanized) | Elecy | Labour | SWR11850 | 64576 | EA | 2066432
4 | 32 | Erection of Extension of 3M for M+3 Tower (Galvanized) | Elecy | Labour | SWR11851 | 5168.95 | EA | 165406.4
5 | 27 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) M-Type Tower (1.2M x 1.2M x 3.3M ) 4.752cum | Elecy | Labour | SWR12090 | 3592.95 | EA | 97009.65
6 | 5 | Excavation of pits in hard rock requiring blasting. (other than SS) M-Type Tower (1.2M x 1.2M x 3.3M ) 4.752cum | Elecy | Labour | SWR12093 | 4810.58 | EA | 24052.9
7 | 30 | Laying of XLPE UG cable Four Run including excavation of trench of size 1050mm wide to 1200mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC - 33KV 3x400sqmm UG Cable | Elecy | Labour | SWR12036 | 1122 | M | 33660
8 | 120 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. - Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) - 33KV 3x400sqmm UG Cable | Elecy | Labour | SWR11988 | 1587.07 | M | 190448.4
9 | 70 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC - 33KV 3x400sqmm UG Cable | Elecy | Labour | SWR11972 | 749 | M | 52430
10 | 280 | Lay-2nd Cable in Excavated Trench | Elecy | Labour | SWR10988 | 204.1 | M | 57148
11 | 110 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) 33KV 3x400sqmm UG Cable | Elecy | Labour | SWR12004 | 323.85 | M | 35623.5
12 | 2 | Making of Straight through joints 33kv 3x400 xlpe | Elecy | Labour | SWR10382 | 5700.78 | EA | 11401.56
13 | 16 | Making of Outdoor/Indoor End Termination 33kv 3x400 xlpe | Elecy | Labour | SWR10387 | 2764.76 | EA | 44236.16
14 | 1 | Erection of 33 KV VCB with Control Panel | Elecy | Labour | SWR10460 | 12500 | EA | 12500
15 | 5.8 | Excavate-Pit for 33KV VCB | Elecy | Labour | SWR23224 | 331 | M3 | 1919.8
16 | 6.7 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Elecy | Labour | SWR20685 | 5160 | M3 | 34572
17 | 9.6 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | Labour | SWR10862 | 373 | M2 | 3580.8
18 | 1 | Rewiring, testing & Commissioning of 33/11 KV VCB. | Elecy | Labour | SWR20524 | 2660 | EA | 2660
19 | 9 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elecy | Supply | SMR11482 | 3486 | EA | 31374
20 | 9 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elecy | Labour | SWR10359 | 386 | EA | 3474
21 | 9 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elecy | Labour | SWR10357 | 1234.2 | EA | 11107.8
22 | 1 | Loading of 33 KV VCBs along with Panel boards | Elecy | Labour | SWR10198 | 1024 | EA | 1024
23 | 1 | Un loading of 33 KV VCBs along with Panel boards | Elecy | Labour | SWR10516 | 1044.48 | EA | 1044.48
24 | 3 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 10 Km and upto 20 Km with Lorry for each trip | Elecy | Labour | SWR11861 | 3299.7 | EA | 9899.1
25 | 500 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Elecy | Labour | SWR11879 | 27 | M | 13500
26 | 4 | Making of coil earthing pole with 8mm GI wire Nut & Bolts for AB Switch | Elecy | Labour | SWR12331 | 146.63 | EA | 586.52
27 | 4 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elecy | Labour | SWR10881 | 142 | EA | 568
28 | 10 | Painting of names on Strcutures & CT ratio on breaker with Yellow background | Elecy | Labour | SWR21510 | 80 | EA | 800
29 | 6 | Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . | Elecy | Supply | SMR40011 | 299 | EA | 1794
30 | 6 | Labour for Fixing of all types of clamps | Elecy | Labour | SWR10917 | 65 | EA | 390
31 | 32 | Numbering of poles incl. cost of paint | Elecy | Labour | SWR10378 | 32 | EA | 1024
32 | 1.6 | Dismantling of 100 Sqmm AAA/ACSR Conductor | Elecy | Labour | SWR22063 | 8274.75 | KM | 13239.6
33 | 1.6 | Restringing of existing loose Lines by removing the pin-binding and jumpers, Providing of temporary stays, providing stiffners pieces, replacement of damaged insulators, alignment of cross arms, pin binding and jumpering after tensioning and removing of the temporary stays complete . Restringing of 100 Sqmm Single ckt 3 cond | Elecy | Labour | SWR11310 | 10000 | KM | 16000
34 | 4 | Loading of 33KV 800 Amps AB Switch | Elecy | Labour | SWR10239 | 126 | EA | 504
35 | 4 | Un loading of 33KV 800 Amps AB Switch | Elecy | Labour | SWR10557 | 79 | EA | 316
36 | 4 | Erection of 33 KV AB Switch including alignment and earthing | Elecy | Labour | SWR10392 | 4500 | EA | 18000
37 | 15 | LOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10204 | 76 | EA | 1140
38 | 15 | UNLOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10522 | 50 | EA | 750
39 | 3.9 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Elecy | Labour | SWR10206 | 221 | TO | 861.9
40 | 3.9 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Elecy | Labour | SWR10524 | 185 | TO | 721.5
41 | 14.15 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 412.08 | TO | 5830.932
42 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elecy | Labour | SWR11040 | 990.68 | EA | 7925.44
43 | 1 | Excavation of pits in all soils except hard rock requiring blasting - 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M (1.31 cum) | Elecy | Labour | SWR10108 | 629.85 | EA | 629.85
44 | 15 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elecy | Labour | SWR10642 | 512.55 | EA | 7688.25
45 | 2 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting. 33 KV DP Structure with 175x85/150x75mm RS joist | Elecy | Labour | SWR11276 | 5670 | SET | 11340
46 | 7 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elecy | Labour | SWR11266 | 2643.83 | EA | 18506.81
47 | 7.65 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elecy | Supply | SMR40009 | 2181 | TO | 16684.65
48 | 7.65 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elecy | Supply | SMR40010 | 1293 | TO | 9891.45
49 | 7.65 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elecy | Labour | SWR10877 | 851 | TO | 6510.15
50 | 7.65 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium | Elecy | Labour | SWR10879 | 482 | TO | 3687.3
51 | 3 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Labour | SWR11230 | 1024 | DR | 3072
52 | 3 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Labour | SWR11231 | 1024 | DR | 3072
53 | 2 | Transport of Cond Drum,VCBs >30 & <50Km Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 30 Km and upto 50 Km with Lorry for each trip | Elecy | Labour | SWR11863 | 4372.74 | EA | 8745.48
54 | 9 | Loading of 33 KV, 10 KA LAs Station type | Elecy | Labour | SWR10266 | 41 | EA | 369
55 | 9 | Un loading of 33 KV, 10 KA LAs Station type | Elecy | Labour | SWR10584 | 35 | EA | 315
56 | 3 | Erection of 33 KV LAS station/Line type including earthing | Elecy | Labour | SWR10396 | 880 | SET | 2640
57 | 50 | S-GI Bolts & Nuts,Washers etc., | Elecy | Supply | SMR11488 | 117.5 | KG | 5875
58 | 8.4 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Elecy | Labour | SWR10356 | 6579 | M3 | 55263.6
59 | 0.25 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elecy | Labour | SWR11890 | 3893 | M3 | 973.25
60 | 1 | Submission of auto CAD Drawing as per pole schedule (Detailed survey and sketch) Upto 10 km | Elecy | Labour | SWR12104 | 6000 | LS | 6000
61 | 6 | Supply & Erection of Smart RFID marker | Elecy | Labour | SWR25089 | 2745 | EA | 16470
62 | 96 | Supply of 9" B Class GI pipe | Elecy | Supply | SMR40082 | 1113 | M | 106848
63 | 240 | Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing, barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | Elecy | Supply | SMR40077 | 363 | M | 87120
64 | 210 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elecy | Labour | SWR21903 | 30 | M | 6300
65 | 7 | Formation of Cut point for 33 KV Double circuit line excluding pole erection and stays | Elecy | Labour | SWR10466 | 3198.72 | EA | 22391.04
66 | 100 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | Elecy | Labour | SMR12488 | 90 | KG | 9000
67 | 29 | Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc. | Elecy | Labour | SWR11329 | 1130 | EA | 32770
68 | 6.5 | LOADING of MS Scrap | Elecy | Labour | SWR10258 | 578 | TO | 3757
69 | 6.5 | Un loading of MS Scrap | Elecy | Labour | SWR10576 | 578 | TO | 3757
70 | 2 | LOADING of Conductor drums | Elecy | Supply | SWR10191 | 202 | EA | 404
71 | 2 | UNLOADING of Conductor drums | Elecy | Labour | SWR10509 | 100 | EA | 200
72 | 15 | Removing and providing of jumpers in SS. | Elecy | Labour | SWR12509 | 64 | EA | 960
73 | 6 | Supply of CT stud clamps with hot dip galvanised bolts and nuts suitable for zebra / Panther conductor on one side and 28/30/40 mm CT stud on other side with stud size for single zebra / panther (4 bolted) with bimetallic sleeve for carrying 800 A | Elecy | Supply | SMR40023 | 399 | EA | 2394
74 | 1.7 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc. including transport of material from road side to location. 100 Sqmm Single Circuit (3 Conductors) | Elecy | Labour | SWR10366 | 13856.7 | KM | 23556.39
Total Amount | [7 empty] | 8866385.742
GST 18% | [7 empty] | 1595949.4336
Schedule Amount | [7 empty] | 10462335.1756