## Erramanzil
Estimate quantity | Detailed description of item | Work type eg., Earth work Electrical works., tec (Upto 200 characters) | Item short description | APSS/Morth CI.Number (Upto 200 Characters) | Rate INR upto 2 Decimals | UOM(upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | Erection of 5-Way RMU | Electrical works | Erection of 5-Way RMU | As per relevent standard specification | 2783.33 | EA | 2783.33
1 | Const. of plinth for mount. new 5Way RMU | Electrical works | Const. of plinth for mount. new 5Way RMU | As per relevent standard specification | 8000 | EA | 8000
1 | LOADING of 11KV 5 Way RMU | Electrical works | LOADING of 11KV 5 Way RMU | As per relevent standard specification | 1268.63 | EA | 1268.63
1 | UNLOADING of 11KV 5 Way RMU | Electrical works | UNLOADING of 11KV 5 Way RMU | As per relevent standard specification | 1268.63 | EA | 1268.63
10 | Supply of earthing pipe with materials,S-GI Bolts & Nuts,Washers etc., | Electrical works | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 1175
40 | Supply of earthing pipe with materials,S-Earthing GI flat 25x3 mm incl material | Electrical works | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 4200
6 | Supply of earthing pipe with materials,S-CI Pipe earthing 80mm dia 2.75m long | Electrical works | S-CI Pipe earthing 80mm dia 2.75m long | As per relevent standard specification | 2789 | EA | 16734
6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Electrical works | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 7405.2
1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading),Transport of Cond Drum,VCBs upto 10Km | Electrical works | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 2720.34
1340 | Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Lay-SR 11KV 3x185sqmm UG Cb CC/BT Compsr | Electrical works | Lay-SR 11KV 3x185sqmm UG Cb CC/BT Compsr | As per relevent standard specification | 1065.16 | M | 1427314.4
2 | UG Cables Joints :Making of Straight through joints, Straight through joint 11kv 3x185 xlpe | Electrical works | Straight through joint 11kv 3x185 xlpe | As per relevent standard specification | 3725.45 | EA | 7450.9
13 | Making of Outdoor/Indoor End Termination,OD/Idoor end termination 11kv 3x185 xlpe | Electrical works | OD/Idoor end termination 11kv 3x185 xlpe | As per relevent standard specification | 2370.63 | EA | 30818.19
3 | Dismantle-11KV 3Way RMU | Electrical works | Dismantle-11KV 3Way RMU | As per relevent standard specification | 600 | EA | 1800
3 | Dismantle-11KV 3Way RMU Plinth | Electrical works | Dismantle-11KV 3Way RMU Plinth | As per relevent standard specification | 1500 | EA | 4500
3 | Raising of DTR plinth- Dismantle-11KV Line AB Switch | Electrical works | Dismantle-11KV Line AB Switch | As per relevent standard specification | 1000.88 | EA | 3002.64
3 | Erection of AB Switch and aligment complete: Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Electrical works | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 9600
9 | Erection of AB Switch and aligment complete - Running of 11KV jumper from Line, AB switch, HG Fuse set to DTR for 3-Phases | Electrical works | L-Run 11KV Jumpering to AB Switch | As per relevent standard specification | 420.75 | SET | 3786.75
1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation, Erection of 9/10/11Meter Box pole | Electrical works | Erection of 9/10/11Meter Box pole | As per relevent standard specification | 2643.83 | EA | 2643.83
12 | End Termnatn of AB cable 120 to 185 Sqmm | Electrical works | End Termnatn of AB cable 120 to 185 Sqmm | As per relevent standard specification | 800 | EA | 9600
15 | Strt thr joints of AB cbl 120 to185 Sqmm | Electrical works | Strt thr joints of AB cbl 120 to185 Sqmm | As per relevent standard specification | 920 | EA | 13800
6 | LOADING of 9.1M PSCC POLE | Electrical works | LOADING of 9.1M PSCC POLE | As per relevent standard specification | 182 | EA | 1092
6 | UNLOADING of 9.1M PSCC POLE | Electrical works | UNLOADING of 9.1M PSCC POLE | As per relevent standard specification | 91 | EA | 546
6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)- Exca Hard pit w/o blast 0.76X0.76X1.83M | Electrical works | Exca Hard pit w/o blast 0.76X0.76X1.83M | As per relevent standard specification | 928 | EA | 5568
6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation, ERECTION OF LINES-Erection of 9.1M Pole | Electrical works | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 14400
3.24 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc., Mass concreting of supports incl. cement | Electrical works | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 21315.96
3 | Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays-Formatn of Horiz Cut point for 11KV line | Electrical works | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1435.81 | EA | 4307.43
0.16 | Dismantle-11KV AB Cb 3x185+70Sqmm | Electrical works | Dismantle-11KV AB Cb 3x185+70Sqmm | As per relevent standard specification | 18972 | KM | 3035.52
1 | Dismantle-3Ph DTR above 160KVA | Electrical works | Dismantle-3Ph DTR above 160KVA | As per relevent standard specification | 1178.1 | EA | 1178.1
0.5 | Stringing of LT AB Cable - Stringing of AB cable 3x70 + 1x16 + 1x50 | Electrical works | Stringing of AB cable 3x70 + 1x16 + 1x50 | As per relevent standard specification | 8450 | KM | 4225
0.5 | Dismanting of AB Cable -Dismantle-LT AB Cb 3x70+1x16+1x50 | Electrical works | Dismantle-LT AB Cb 3x70+1x16+1x50 | As per relevent standard specification | 9231 | KM | 4615.5
0.24 | Dismantling of Line -Dismantling of 11kV 34/ 55 Sqmm SC | Electrical works | Dismantling of 11kV 34/ 55 Sqmm SC | As per relevent standard specification | 4500 | KM | 1080
15 | Fabrication of materials including 2 coats of Red oxide painting, Fab Back clamps with 50 x 6 mm MS Flat | Electrical works | Fab Back clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 15 | EA | 225
1 | Fabrication of poles- Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Electrical works | Fabrication of 175x85/150x75mm RS joist | As per relevent standard specification | 512.55 | EA | 512.55
45 | Removing and Reconnection of LT Services | Electrical works | Removing and Reconnection of LT Services | As per relevent standard specification | 44 | EA | 1980