## 1. Zaheerabad SS
Zaheerabad Town-II SS Electrical Schedule
Name of the work: Estimate for erection of new 33/11 KV SS with connected 33 KV and 11 KV lines at Zaheerabad Town-II (V) in Zaheerabad (M) of Zaheerabad Division of Sangareddy Circle
S.No | SRR Codes | Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR10105 | 45 | ERECTION OF S.S. STRUCTURE: Coping of 0.45x0.45x0.45Mt with 1:8 slope Using form boxes (0.031Cumt.) | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 27000
2 | SWR10343 | 37 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 88800
3 | SWR10356 | 39.5078 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size (0.76x0.76x1.52M) *45= 39.50with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt) with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 259922.0794
4 | SWR11890 | 1.147 | ERECTION OF S.S. STRUCTURE: Coping of 0.45x0.45x0.45Mt with 1:8 slope Using form boxes (0.031Cumt.) | Civil work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | M3 | 4465.271
5 | SWR11331 | 37 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of poles with two coats of white cement (including cost of paint). | Electrical work | Paint-9.1M PSCC Poles as desc SSR | As per relevent standard specification | 485 | EA | 17945
6 | SWR11889 | 7.16 | Fabrication of 100 X 50mm MS Channel for formation of 11kV and 33kV bays: Fabrication and erection of M.S,Channel 100x50mm for forming of 33KV & 11 KV Bays as per standard specifications to facilitate stringing of bus, erection of LA sets, AB Switches bolts & Nuts etc. including painting with one coats of red oxide and two coats of Aluminium paint. GI bolts&nuts shall be used. | Electrical work | Fabr & Erect-MS Chnl 100x50mm for SS Bay | As per relevent standard specification | 6600 | TO | 47256
7 | SWR10404 | 166.6 | Erection of 33kV and 11kV Strung Bus with Panther (200Sqmm) ACSR Conductor: Erection of 33kV and 11kV Bus over the Substation structures with 200sqmm Panther ACSR conductor and giving Jumpers to connect the Switch gear by providing the suitable T clamps and round clamps suitable to Post type insulators & Insulators. | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 54591.488
8 | SWR10392 | 7 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 31500
9 | SWR10393 | 12 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 38400
10 | SWR11742 | 9 | Erection of 11 kV 400 A convential single(1/3) phasing AB switches.includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | S&E-400A 11KV ABSwth Conv 1ph(1/3) in SS | As per relevent standard specification | 4232 | EA | 38088
11 | SWR21240 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt). | Electrical work | Hoisting post ins&hrd wr 1panther 33kv | As per relevent standard specification | 781 | EA | 1562
12 | SWR21241 | 4 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 11kv | As per relevent standard specification | 507 | EA | 2028
13 | SWR10881 | 18 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 2556
14 | SWR23224 | 20.4 | Excavation of pit in all types of soils of size 2.2x2.2x0.85Mts.for Construction of Plinths for VCB (33KV & 11 KV ) | Earth work | Excavate-Pit for 33KV VCB | As per relevent standard specification | 331 | M3 | 6752.4
15 | SWR20685 | 22.264 | Providing of Base concreting (2.2x2.2x0.15 Mts) with 1:3:6 Concrete mix. Using form boxes, Providing of Concreting (2x2x1.0mts) with 1:3:6 Cocrete mix. Plastering of the plinth for smooth finishing with 12mm thick 1:3 cement motor and providing two coats white washing for part of the plinth above groung level. | Civil work | Cement concrete with 40MM metal VCB plinth | As per relevent standard specification | 5160 | M3 | 114882.24
16 | SWR10732 | 9 | Consruction of plinth for 11KV VCB 1.8x1.8x0.75m | Civil work | Cement concrete with 40MM metal VCB plinth | As per relevent standard specification | 26086 | EA | 234774
17 | SWR10460 | 1 | Erection of 33kv VCB: Assembling the VCB Structures and mounting the VCBs over the already erected foudation including wiring of Breaker Control Panel/CTs, erection of CTs and control pannel providing Jumpers. | Electrical work | Erection of 33kv VCB | As per relevent standard specification | 6346.08 | EA | 6346.08
18 | SWR10461 | 6 | Erection of Switchgear complete for 11 kV VCB includes Assembling the VCB Structures and mounting the VCBs over the already erected foudation including wiring of Breaker Control Panel/CTs, erection of CTs and control pannel providing Jumpers. | Electrical work | Erection of 11kv VCB | As per relevent standard specification | 12000 | EA | 72000
19 | SWR10396 | 2 | Erection of 33KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 1760
20 | SWR10397 | 1 | Erection of 11 KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 11kv LA stn type incl earthing | As per relevent standard specification | 559 | SET | 559
21 | SWR10398 | 4 | Erection of 11 KV Lightening Arrestors line type complete including jumpering. | Electrical work | Erect of 11kvLA line type incl earthing | As per relevent standard specification | 505 | SET | 2020
22 | SMR11607 | 1 | Supply of 33kv HG fuse set including providing of jumpers | Electrical work | S-33KV HG Fuse Set excl Ins & Chnl | As per relevent standard specification | 6431 | SET | 6431
23 | SWR10394 | 1 | Erection of 33kv HG fuse set including providing of jumpers | Electrical work | Erect. of 33kv HG Fuseset incl earthing | As per relevent standard specification | 1331.81 | SET | 1331.81
24 | SMR11608 | 1 | Supply of 11kv HG fuse set including providing of jumpers | Electrical work | S-11KV HG Fuse Set | As per relevent standard specification | 1733.75 | SET | 1733.75
25 | SWR10395 | 1 | Erection of 11kv HG fuse set including providing of jumpers | Electrical work | Erect. of 11kv HG Fuseset incl earthing | As per relevent standard specification | 740.52 | SET | 740.52
26 | SMR11482 | 32 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 111552
27 | SWR10357 | 32 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 39494.4
28 | SWR10920 | 531 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification.75x8 mm MS flat for Earth mat and connecting to electrodes. | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 34515
29 | SWR10919 | 1042 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification. 50x6 mm MS flat for raisers, double flat shall be run for structure poles raisers & equipment earthing. | Electrical work | Earthing for raisers of SS Flat 50x6 mm. | As per relevent standard specification | 41 | RMT | 42722
30 | SMR40033 | 4 | Providing of double earthing for neutral with flexible copper jumpers of adequate size including arrangement by fixing M.S.Channel 100x50mm. | Electrical work | SupCU Flexi jumper for Power T/F Neutral | As per relevent standard specification | 4725 | EA | 18900
31 | SWR11771 | 9 | Erection of 24 Volts Battery along with Charger on the VCB plinth and giving DC supply to VCB's. | Electrical work | Erect-24V Batery with Chrgr incl grot-SS | As per relevent standard specification | 1050 | EA | 9450
32 | SWR11879 | 1000 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable includes excavation of earth and back filling with sand and earth in alternate layers . The cable termination shall be made by providing proper size lugs and shall be identified with colours. | Electrical work | Laying-4 core cable | As per relevent standard specification | 19 | RMT | 19000
33 | SWR10463 | 1 | Erection of 25 kVA Three phase Station Transformer on the Substation Structures and giving jumpers/connections on HT side to the 11kV bus. Belting angle shall be provided both sides of DTR for securing DTR firmly in position. | Electrical work | Erection of Three Phase DTRs | As per relevent standard specification | 1139.95 | EA | 1139.95
34 | SMR40045 | 1 | Supply of AC Panel Board includes: Fixing of 1 No.100A, MCCB, 10kA capacity of any standard make including material cost. Fixing of suitable panel box 3x3x1 with M.S.Sheet of 16 SWG with front door compartments inclusive of material cost & powder coating (with C Channel ). Fabrication of panel Fixing of 96x96mm analog voltmeter with VSS switch Fixing of 20A HRC fuse Fixing of 3 phase supply indicator kwith HRC fuses Supply and fixing of 6 Sqmm copper flexible wire (PVC) Fixing of Stud type TBs for outgoing feeder Fixing of Epoxy bus supports. | Electrical work | Supply of AC Supply panel complete | As per relevent standard specification | 42000 | EA | 42000
35 | SMR40044 | 1 | Supply of DC Panel Board Fixing of suitable panel box of size 6'x6'x1' with M S sheet of 16 SWG with back doors (4'x6') and on front side with provision to fix up bakelite hylam sheet size of 4'x6' including cost of the panel with powder coating. Fixing of best quality of angles for panel. Fixing of C Channelfor panel. Fabrication of control panel including making suitable holes and board Fixing of Stud type TBs for outgoing feeder Fixing of 24V DC pilot lamps of standard make Fixing of healthy trip push buttons with LED lamp Fixing of plain switches for alarm acceptance and for PTR signal Fixing of ON/OFF push buttons Fixing of digital volt meter for 11kV Fixing of VSS of standard make, Fixing of Engraved AL plates for Alarm panel of various VCB Laying of 2.5Sqmm copper flexible wire for internal wiring . Fixing of digital frequency meter Fixing of Copper lugs and ferrules for internal wiring. Fixing of 4" Gang bells 24V DC Fixing of flow diagram with rading strip Fixing of HRC fuse units | Electrical work | Supply of DC Anunc.relay panel 8 feeders | As per relevent standard specification | 42500 | EA | 42500
36 | SWR20025 | 1 | fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supplied by tenderer. | Electrical work | 33/11kv S.S Erection of AC&DC Panel | As per relevent standard specification | 7871.85 | SET | 7871.85
37 | SWR10342 | 8 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 12000
38 | SWR10356 | 4.368 | Concreting the location after erection of pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) ( 0.6x0.6x1.5)mtrs | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 28737.072
39 | SWR10956 | 8 | Fixing of Metal halide/LED lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5M GI pipe complete. | Electrical work | Fixing of LED/Metal halide complete. | As per relevent standard specification | 1268 | EA | 10144
40 | SWR20028 | 8 | Supply and Fixing of junction box and Providing with proper Fuse protection and required glauds suitable for Cable Terminations. The box shall be fixed on the pole. | Electrical work | 33/11kv S.S Yard lighting junction box | As per relevent standard specification | 351.9 | EA | 2815.2
41 | SWR20526 | 2 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply & fixing of marshall box | As per relevent standard specification | 3085.5 | EA | 6171
42 | SMR40088 | 1 | Supply and fixing of filled sand bucket set complete (4 Nos. Buckets) with stand to mount fire buckets. | Electrical work | Sup Fire Buckets Stand with Buckets | As per relevent standard specification | 1386 | SET | 1386
43 | SMR40087 | 2 | Supply and fixing of CO2 Cylinder set as per IS2878 Specifications. | Electrical work | Sup TrollyMounted Co2 Cylinders(IS-2878) | As per relevent standard specification | 9240 | EA | 18480
44 | SWR11895 | 1 | Supplying and fixing of feeder indicator board to each of the 3Nos feeder breakers and LV breaker, danger boards made of 1'x1' and properly mounted on the structures. The letters written on the borad shall be 1.5"size with blue colour and background shall be of white colour | Electrical work | S&F-33/11KV SS Feeder Indicator Board | As per relevent standard specification | 551 | SET | 551
45 | SWR20032 | 1 | Supply and fixing of wooden board of size 3'x2'.5'indicating the layout of the Switch yard. | Electrical work | Sup &fix of board ind Switchyard layout | As per relevent standard specification | 1654 | EA | 1654
46 | SMR40086 | 1 | Supply and Erection of Permanent Name Board of on 3'x4' steel sheetmounted on steel frame as described in Specification. | Electrical work | Sup 33/11kv S.S Permanent name board | As per relevent standard specification | 10238 | EA | 10238
47 | SMR40076 | 1 | Supply of Digital clamp meter. | Electrical work | Supply of Digital clamp meter. | As per relevent standard specification | 2888 | EA | 2888
48 | SMR40064 | 1 | Supply of Rechargeable LED torch light of Standard make. | Electrical work | Sup Rechargeable LED torch light. | As per relevent standard specification | 1733 | EA | 1733
49 | SMR40063 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box containing ‘D’Spanners from size 6 to 54, Hammer small and big size, Ring spanners from 6 to 28, Adjustable spanner, Pipe wrench, Cutting Plier, Nose plier, Tester, insulated Screw drive. | Electrical work | SupTaparia Tool kit complete as per Spec | As per relevent standard specification | 4925 | SET | 4925
50 | SWR22090 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Electrical work | Sup& fix safety inst/SS Op. inst board | As per relevent standard specification | 2205 | EA | 2205
51 | SWR10401 | 1 | Erection of 33KV 1-PH PT's | Electrical work | erectionof PT's | As per relevent standard specification | 1079 | EA | 1079
52 | SMR11598 | 8 | Supply of 25 W LED lamp with fitting of philips make | Electrical work | S-25W LED fixture set | As per relevent standard specification | 3200 | EA | 25600
53 | SMR12378 | 1 | Supply of Alluminum Ladder(20 feet) | Electrical work | S-10ft Aluminium Ladder | As per relevent standard specification | 1654 | EA | 1654
54 | SMR40075 | 1 | Supply of Megger (2000 ohms, 0-2.5kv) | Electrical work | Supply of Earth megger (1000v) | As per relevent standard specification | 8085 | EA | 8085
55 | SMR11599 | 4 | Supply of Earth Discharging Rod 8 feet length, 3 mm thickness. | Electrical work | S-Earth Rod 8ft Long 3mm Thick | As per relevent standard specification | 1000 | EA | 4000
56 | SMR11488 | 200 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 23500
57 | SMR11591 | 66 | Supply of PG clamps for panther 2 bolted 800 A. | Electrical work | S-Al. alloy three bolted PG clamps 800A | As per relevent standard specification | 130 | EA | 8580
58 | SWR20029 | 350 | Supply and Laying of 2 core/4 core cable includes excavation earth and back filling with sand and earth in alternate layers as shown in the sketch. The cable termination shall be made by providing proper size of lugs at both ends of the cable termination. | Electrical work | 33/11kv S.S laying of 2/4core for light | As per relevent standard specification | 50 | M | 17500
59 | SWR20308 | 35 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 14255.15
60 | SWR20307 | 8 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 2172.16
61 | SWR11860 | 8 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 21762.72
62 | SWR10150 | 13 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 8022.3
63 | SWR10206 | 13 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 2873
64 | SWR10524 | 13 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 2405
65 | SWR11220 | 500 | Loading and unwinding of Panther conductor. | Electrical work | Load-Unwinding Panther conductor | As per relevent standard specification | 3 | M | 1500
66 | SWR11221 | 500 | Unloading of Panther conductor. | Electrical work | Unload-Unwinding Panther conductor | As per relevent standard specification | 2 | M | 1000
67 | SWR12416 | 3 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 6
68 | SWR10631 | 3 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 6
69 | SWR10618 | 3 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 195
70 | SWR10632 | 3 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 195
71 | SWR10212 | 2 | Loading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | LOADING of 11kv Pin/Post/Solid Core Insu | As per relevent standard specification | 1 | CRT | 2
72 | SWR10530 | 2 | Unloading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | UNLOADING of 11kv Pin/Post/Solid Core In | As per relevent standard specification | 1 | CRT | 2
73 | SWR11701 | 1000 | Loading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | Load-PVC Control Cable 10C | As per relevent standard specification | 1 | M | 1000
74 | SWR11712 | 1000 | Unloading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | UnLoad-PVC Control Cable 10C | As per relevent standard specification | 1.02 | M | 1020
75 | SWR11691 | 1 | Loading of 3Ph 25KVA Distribution Transformer. | Electrical work | Load-3Ph 25KVA DTR | As per relevent standard specification | 252 | EA | 252
76 | SWR11692 | 1 | UnLoading of 3Ph 25KVA Distribution Transformer. | Electrical work | UnLoad-3Ph 25KVA DTR | As per relevent standard specification | 202 | EA | 202
77 | SWR10200 | 2 | Loading of 33/11 KV Current Transformers/ Potential Transformers. | Electrical work | LOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 165 | EA | 330
78 | SWR10266 | 6 | Loading of 33 KV10 KA LAs Station type. | Electrical work | LOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 41 | EA | 246
79 | SWR10584 | 6 | Unloading of 33 KV10 KA LAs Station type. | Electrical work | UNLOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 35 | EA | 210
80 | SWR10265 | 12 | Loading of 11 KV10 KA LAs Line type. | Electrical work | LOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 384
81 | SWR10583 | 12 | Unloading of 11 KV10 KA LAs Line type. | Electrical work | UNLOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 384
82 | SWR10264 | 3 | Loading of 11 KV10 KA LAs Station type. | Electrical work | LOADING of 11 KV,10 KA LAs Station type | As per relevent standard specification | 32 | EA | 96
83 | SWR10582 | 3 | Unloading of 11 KV10 KA LAs Station type. | Electrical work | UNLOADING of 11 KV,10 KA LAs Station typ | As per relevent standard specification | 32 | EA | 96
84 | SWR10239 | 2 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 252
85 | SWR10557 | 7 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 553
86 | SWR10238 | 8 | loading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 640
87 | SWR10556 | 8 | Unloading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 640
88 | SWR11224 | 9 | Loading and Unloading of 12V/24V Battery Set. | Electrical work | Load/Unload-12V/24V Battery Set | As per relevent standard specification | 23 | EA | 207
89 | SWR10356 | 2.66 | ERECTION OF S.S. STRUCTURE: Providing of base concreting of size 0.76x0.76x0.15M with CC mix of ratio 1:3:6 Using form boxes(0.087Cu.Mt)x31 with 20mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 17500.14
90 | SWR10402 | 1 | Erection of 11kv Potential Transformer sets complete including jumpering. The LV side of the PT shall be provided with proper fuse protection mounted in separate marshalling boxwith proper size cable glands etc. The box shall be mounted on the Substation structure. | Electrical work | Erection of 11kv three phase PT s | As per relevent standard specification | 800 | SET | 800
91 | SWR10518 | 2 | Unloading of 33/11 KV Current Transformers/ Potential Transformers | Electrical work | UNLOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 128 | EA | 256
92 | SWR10674 | 1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
93 | SWR10356 | 4.32 | Concreting the location after erection of 8.0 Mtrs pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) ( 0.6x0.6x1.5)mtrs x 8 . | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 28421.28
94 | SWR21750 | 4 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply and fixing of PT Marshalling box | As per relevent standard specification | 1139.85 | EA | 4559.4
95 | SMR40067 | 2 | Supply of Hand Gloves | Electrical work | Supply of Hand Gloves | As per relevent standard specification | 289 | SET | 578
96 | SMR40071 | 2 | Supply of Safety Helmets of standard make | Electrical work | Supply of Safety Helmet of standard make | As per relevent standard specification | 231 | EA | 462
97 | SMR40009 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for First coat of 1st GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 11995.5
98 | SWR10877 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 1st coat of Aluminium | Electrical work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 4680.5
99 | SWR20904 | 20 | Supply & Providing of Panther T clamps |  | Supply & Providing of Panther T clamps. | As per relevent standard specification | 320 | EA | 6400
100 | SMR40010 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for second coat of 2nd GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 7111.5
101 | SWR10879 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 2nd coat of Aluminium | Electrical work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 2651
102 | SMR25233 | 37 | S-PSCC Pole 9.1Mtr 280kg | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 115048.17
103 | SMR25232 | 8 | S-PSCC Pole 8Mtr 140kg | Electrical work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 12640
104 | SMR12315 | 6 | S-33KV 800A DB Break AB Switch | Electrical work | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 243952.68
105 | SMR12316 | 3 | S-11KV 800A DB Break AB Switch | Electrical work | S-11KV 800A DB Break AB Switch | As per relevent standard specification | 30847.46 | EA | 92542.38
106 | SMR25211 | 9 | S-11KV 400A Conv ABSwitch with Insulator | Electrical work | S-11KV 400A Conv ABSwitch with Insulator | As per relevent standard specification | 11754 | EA | 105786
107 | SMR22745 | 5500 | S- MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 315975
108 | SMR12321 | 7160 | S-MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 403967.2
109 | SMR12322 | 3000 | S-MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 169500
110 | SMR25200 | 1 | S-LT Distribution Box (SMC) | Electrical work | S-LT Distribution Box (SMC) | As per relevent standard specification | 7797 | EA | 7797
111 | SMR12318 | 1 | S-11KV 200A Tilting Type AB Switch | Electrical work | S-11KV 200A Tilting Type AB Switch | As per relevent standard specification | 8991 | EA | 8991
112 | SWR22092 | 4.5 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 3442.5 | 33KV line
113 | SWR10107 | 100 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 70000
114 | SWR10105 | 21 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 12600
115 | SWR10978 | 100 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 416528
116 | SWR10343 | 21 | Erection of 9.1 Mts Sturt pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 50400
117 | SWR10981 | 11 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Horizontal Cut point for 33 KV line | As per relevent standard specification | 1759.5 | EA | 19354.5
118 | SWR10356 | 46.508 | Concreting the location after erection of 11 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.76X0.76X1.83 Mts)* 44 = 46.508 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 305976.132
119 | SWR10356 | 11.34 | Concreting the location after erection of 9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes(0.6X0.6X1.5 Mts)*21 = 11.34 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 74605.86
120 | SWR10366 | 5 | Paving of the 100 sqmm AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 12600.06 | KM | 63000.3
121 | SMR11488 | 200 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 23500
122 | SWR11180 | 100 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 43197
123 | SWR20308 | 21 | Sub Transportation of 9.1M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 8553.09
124 | SWR10191 | 5 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 1010
125 | SWR10509 | 5 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 500
126 | SWR11860 | 5 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 13601.7
127 | SWR10150 | 0.6 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 370.26
128 | SWR10206 | 0.6 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 132.6
129 | SWR10524 | 0.6 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 111
130 | SWR10211 | 28 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 84
131 | SWR10529 | 28 | Unloading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 84
132 | SWR12416 | 12 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 24
133 | SWR10631 | 12 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 24
134 | SWR10618 | 5 | Loading of 33KV Metal parts bag of 25 nos | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 325
135 | SWR10632 | 5 | Unloading of 33 KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 325
136 | SWR21190 | 30 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock,Hard rock Requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 15600
137 | SMR25236 | 100 | Supply of PSCC Pole 11Mtr 365 Kg | Electrical work | S-PSCC Pole 11Mtr 365 Kg | As per relevent standard specification | 5399 | EA | 539900
138 | SMR25233 | 21 | Supply of PSCC Pole 9.1Mtr 280kg | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 65297.61
139 | SMR25229 | 94 | Supply of 33KV V-Cross Arm without Clamps | Electrical work | S-33KV V-Cross Arm without Clamps | As per relevent standard specification | 1678 | EA | 157732
140 | SMR25228 | 30 | Supply of 33KV M.S.Back Clamps | Electrical work | S-33KV M.S.Back Clamps | As per relevent standard specification | 248 | SET | 7440
141 | SMR25230 | 94 | Supply of 33KV Top Cleat with Clamps | Electrical work | S-33KV Top Cleat with Clamps | As per relevent standard specification | 461 | SET | 43334
142 | SMR25207 | 500 | Supply of MS Angle 65X65X6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 28625
143 | SMR22745 | 500 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 28725
144 | SMR12321 | 450 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 25389
145 | SMR25231 | 30 | Supply of 33KV MS Stay Set with BasePlate | Electrical work | S-33KV MS Stay Set with BasePlate | As per relevent standard specification | 1035 | SET | 31050
146 | SMR12315 | 1 | Supply of 33KV 800A DB Break AB Switch | Electrical work | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 40658.78
147 | SMR40107 | 6 | Supply of Galvanised M+3 Tower as per ASCI Standard. Supply of Galvanised M+3 type tower as per Specification. i.e. 1.34 MT per each tower including the following terms. Supply of Suitable Hot dip Galvanised, Zinc coated Nuts and bolts with suitable plain and spring washers of 158 Kgs per each M+3 tower. Supply of material for Painting of structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 litres of thinner 1st coat is to be applied before erection of tower and 2nd coat after stringing. Supply of material for 2 nos. Pipe earthing of towers with 40mm dia GI pipe, including cost of pipe, bentonite powder and running of GI flat etc., per each tower. | Electrical work | S-M+3 Tower GALV | As per relevent standard specification | 110562.8 | EA | 663376.8
148 | SWR10984 | 6 | Erection of M+3 Tower, as per the following terms: Fabrication of tower Parts as per Specification @ 1.34 MT per each M+3 Tower . Setting of stubs in position for laying of foundation of towers with 1:2:4 cc mix using 40 mm HBG metal including cost of all concreting materials, form boxes and cement and curing for 14 days (40 mm HBG metal for pyramid portion and 20 mm HBG metal for concreting per each tower . Erection of tower parts completely as per specifications including erection of insulators with all accessories, jumpering,transport of meterial and bolts and nuts etc., Tack welding of total tower nuts and bolts . Including labour for Pipe earthing of towers with 40mm dia GI pipe, including cost of pipe, bentonite powder and running of GI flat etc., Transport of Material to site including loading and unloading. Labour charges for painting including scratching and cleaning of tower parts. | Electrical work | Erect- M+3 Tower GALV | As per relevent standard specification | 57554 | EA | 345324
149 | SMR40110 | 6 | Supply of extension of 3mtrs for M+3 Tower as per ASCI Standard. Supply of Galvanised M+3 type tower as per Specification @ 0.33 MT per each M+3 tower. Supply of Suitable Hot dip Galvanised, Zinc coated Nuts and bolts with suitable plain and spring washers @ 30.23 Kgs per each tower. Supply of material for Painting of structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 litres of thinner 1st coat is to be applied before erection of tower and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. | Electrical work | S-Mat. for Extn of M+3 Tower by 3M GALV | As per relevent standard specification | 22415.2 | EA | 134491.2
150 | SWR10987 | 6 | Erection of 3M extension for tower parts completely as per specifications including erection of insulators with all accessories, jumpering,transport of meterial and bolts and nuts etc., Transport of Material to site including loading and unloading. Labour charges for painting including scratching and cleaning of tower . | Electrical work | Erect-Extn of 3M for M+3 Tower GALV | As per relevent standard specification | 4473 | EA | 26838
151 | SWR22092 | 12 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 11 kv line. | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | EA | 9180 | 11 kv line
152 | SWR10105 | 200 | Excavation of Pole pits of size 2.6"x2.6"x5.0" for 9.1/8.0 mtrs PSCC Poles including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except hard rock requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 120000
153 | SWR10110 | 95 | Excavation of Pole pits of size (2.6" x 2.6" x 5.0') 0.88 cum 0.76 M x 0.76M x 1.52M for 9.1 mtrs PSCC Poles including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD (2.6" x 2.6" x 5.0') | As per relevent standard specification | 1440 | EA | 136800
154 | SWR10978 | 240 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 999667.2
155 | SWR10343 | 55 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 132000
156 | SWR10653 | 35 | Formation of 11 kv cut points (Vertical/Horizantal) including fixing of 11 KV Cross arms,clamps, strain insulators sets complete with hardware and stays (Bows and Eye-bolts), Excluding the cost of pit Excavation and pole erection. The contractor has to supply GI Bolts and Nuts. | Electrical work | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1350 | EA | 47250
157 | SWR10356 | 66.375 | Concreting the location after erection of 9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.6X0.6X1.5 Mts)* 14.8 = 7.992 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 436681.125
158 | SWR10365 | 12 | Paving of the conductor 55 Sqmm AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 3 Cond | As per relevent standard specification | 8500 | KM | 102000
159 | SMR11488 | 300 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 35250
160 | SWR10206 | 1.45 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 320.45
161 | SWR10524 | 1.45 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 268.25
162 | SWR11248 | 240 | Loading 11KV Polymer Pin Insulator- with GI pins | Electrical work | Load-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 240
163 | SWR11249 | 240 | Unloading 11KV Polymer Pin Insulator with GI pins | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 240
164 | SWR10134 | 1.45 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 851.904
165 | SWR11862 | 12 | Transport of VCB , Control pannels, current transformater, bosster etc, above 20 KM and upto 30 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 44296.56
166 | SWR10191 | 12 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 2424
167 | SWR10509 | 12 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 1200
168 | SWR11180 | 240 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 423.5 | EA | 101640
169 | SWR20308 | 55 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 22400.95
170 | SWR10228 | 240 | Loading of 11 KV V - Cross arms | Electrical work | LOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 960
171 | SWR10546 | 240 | Unloading of 11 KV V - Cross arms | Electrical work | UNLOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 960
172 | SWR12402 | 35 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 1680
173 | SWR12421 | 35 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 1680
174 | SWR10251 | 240 | Loading of 11 KV Top fittings | Electrical work | LOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 240
175 | SWR10569 | 240 | Unloading of 11 KV Top fittings | Electrical work | UNLOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 240
176 | SWR12416 | 210 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 420
177 | SWR10631 | 210 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 420
178 | SWR10353 | 30 | Erection of 11 kv Stay set complete including fixing of bow, fixing and binding of Eye bolt,Anchor rod,guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Assembly and erection of Stay set11kv&LT | As per relevent standard specification | 606.85 | SET | 18205.5
179 | SWR21190 | 30 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In Hard Gravel and Hard murram not requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 15600
180 | SMR25233 | 55 | Supply of PSCC Pole 9.1Mtr 280kg | Electrical Work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 171017.55
181 | SMR25236 | 240 | Supply of PSCC Pole 11Mtr 360kg | Electrical Work | S-PSCC Pole 11Mtr 360kg | As per relevent standard specification | 15635.59 | EA | 3752541.6
182 | SMR25218 | 240 | Supply of 11KV V X-Arms with MS Angle 65x65x6 | Electrical Work | S-11KV V X-Arms with MS Angle 65x65x6 | As per relevent standard specification | 743 | EA | 178320
183 | SMR25213 | 115 | Supply of MS Back Clamps for 9.1 M PSCC Pole | Electrical Work | S-MS Back Clamps for 9.1 M PSCC Pole | As per relevent standard specification | 92 | SET | 10580
184 | SMR25224 | 240 | Supply of 11KV Top Cleat with Clamps | Electrical Work | S-11KV Top Cleat with Clamps | As per relevent standard specification | 178 | SET | 42720
185 | SMR25205 | 850 | Supply of MS Channel 75x40 mm | Electrical Work | S-MS Channel 75x40 mm | As per relevent standard specification | 58.45 | KG | 49682.5
186 | SMR25206 | 200 | Supply of MS Angle 50x50x6 | Electrical Work | S-MS Angle 50x50x6 | As per relevent standard specification | 58.15 | KG | 11630
187 | SMR12321 | 400 | Supply of MS Flat 75x8mm | Electrical Work | Supply of MS Flat 75x8mm | As per relevent standard specification | 56.5 | KG | 22600
188 | SMR25225 | 30 | Supply of 11KV MS Stay Sets without BasePlate | Electrical Work | S-11KV MS Stay Sets without BasePlate | As per relevent standard specification | 622 | SET | 18660
189 | SMR25228 | 240 | Supply of 33KV M.S.Back Clamps | Electrical Work | S-33KV M.S.Back Clamps | As per relevent standard specification | 248 | SET | 59520
190 | SWR11980 | 100 | Laying of 33 KV 3x400 sqmm XLPE UG cable double run in Hard Rock(1.2*0.5x1=0.6cum) including excavation of trench of size 1200mm for 33 KV from road level providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Change and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site including the cost of lead and lift etc. | Electrical work | Laying of 33kV UG 2Run in Hard rock. | As per relevent standard specification | 1388.84 | RMT | 138884
191 | SWR11954 | 100 | Raising of 33KV 3x400 Sqmm XLPE UG Double cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (pipe cost extra) | Electrical work | Raise-DR 33KV 3x400sqmm UG Cb on support | As per relevent standard specification | 135.66 | M | 13566
192 | SWR10387 | 4 | Making of Outdoor/Indoor End Termination with 33 KV 3x400 Sqmm Cable | Electrical work | OD/Idoor end termination 33kv 3x400 xlpe | As per relevent standard specification | 2764.76 | EA | 11059.04
193 | SMR11483 | 2 | Supply of CI earthing pipe 80 mm dia, 2.75mt long thickness 10mm with flange | Electrical work | S-CI Pipe earthing 100mm dia 2m long | As per relevent standard specification | 2789 | EA | 5578
194 | SWR10147 | 1.1 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) upto 10KM | Electrical work | TRANSPORT OF STEEL MATERIAL up to 10KM | As per relevent standard specification | 332.52 | TO | 365.772
195 | SWR11230 | 2 | Loading of 11/33KV XLPE UG Cable for all sizes | Electrical work | Load-11/33KV XLPE UG Cable for all sizes | As per relevent standard specification | 1024 | DR | 2048
196 | SWR11231 | 2 | Unloading of 11/33KV XLPE UG Cable for all sizes | Electrical work | Unload-11/33KV XLPE UG Cable all sizes | As per relevent standard specification | 1024 | DR | 2048
197 | SWR11172 | 3 | Loading of 11/33KV Straight through joint kit | Electrical work | Loading 11/33KV Straight thr jointkit | As per relevent standard specification | 8 | EA | 24
198 | SWR11153 | 3 | Un-loading of 11/33KV Straight through joint kit | Electrical work | Un-loading 11/33KV Straight thr jointkit | As per relevent standard specification | 4 | EA | 12
199 | SWR11266 | 2 | Erection of 5 Mts RS Joist (Bit) Pole including fixing of Pole Mounted Box | Electrical work | R.S. joist box poles erection complete | As per relevent standard specification | 2643.83 | EA | 5287.66
200 | SWR10642 | 2 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Electrical work | Fabrication of 175x85/150x75mm RS joist | As per relevent standard specification | 512.55 | EA | 1025.1
201 | SWR10640 | 2 | painting of RS Joist including cross arms and clamps with one coat of red oxid and two coats of Al. paint including cost of paint and consumables | Electrical work | Painting of RS Joist(1C RO, 2C Al.Paint) | As per relevent standard specification | 1132 | EA | 2264
202 | SWR10298 | 2 | Cutting Charges for RS joist 175x85mm | Electrical work | Cutting Charges for RS joist 175x85mm | As per relevent standard specification | 47 | EA | 94
203 | SWR10356 | 2.11 | Concreting the location after erection of R.S. Joist pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.76X0.76X1.83 Mts)* 2 = 2.11Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 13881.69
204 | SWR10382 | 3 | Making of straight through joint kit 33KV XLPE Out-Door End kit (3x400sqmm) | Electrical work | Straight through joint 33kv 3x400 xlpe | As per relevent standard specification | 5700.78 | EA | 17102.34
205 | SWR11171 | 4 | Loading of 11/33 KV IN/OUT door kits | Electrical work | Loading of 11/33 KV IN/OUT door kits | As per relevent standard specification | 6 | EA | 24
206 | SWR11152 | 4 | Un-loading of 11/33 KV IN/OUT door kits | Electrical work | Un-loading of 11/33 KV IN/OUT door kits | As per relevent standard specification | 4 | EA | 16
207 | SWR10988 | 200 | Laying of 2nd cable in excavated trench | Electrical work | Lay-2nd Cable in Excavated Trench | As per relevent standard specification | 115 | M | 23000
208 | SWR10357 | 2 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1100 | EA | 2200
209 | SWR10359 | 2 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Earth work | ERECT. OF LINES-Providing of RCC collar | As per relevent standard specification | 386 | EA | 772
210 | SWR11988 | 100 | Laying of 33 KV 3x400 Sqmm XLPE UG cable Double Run in Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC/BT including excavation of trench of size 600mm wide and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. | Electrical work | Lay-DR 33KV 3x400sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 1587.07 | M | 158707
211 | SMR40081 | 100 | Supply of 6" B class GI pipe | Electrical work | S-6" B Class GI pipe 5mm thck 20Kg/M | As per relevent standard specification | 1044 | M | 104400
212 | SMR11610 | 150 | Supply of 6" DWC pipe | Electrical work | Supply of 6" DWC pipe | As per relevent standard specification | 1012 | M | 151800
213 | SMR40078 | 100 | Supply of 150MM Hume pipe of class NP3 | Electrical work | Supply of 150MM Hume pipe of class NP3 | As per relevent standard specification | 303 | M | 30300
214 | SWR10105 | 2 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 1200
215 | SWR10921 | 100 | Laying of earth mat Excvation 25x3MM | Earth work | Laying of earth mat Excvation 25x3MM | As per relevent standard specification | 68 | RMT | 6800
216 | SWR10204 | 2 | LOADING of R.S. Joists 175 x 85 mm | Electrical work | LOADING of R.S. Joists 175 x 85 mm | As per relevent standard specification | 76 | EA | 152
217 | SWR10522 | 2 | UNLOADING of R.S. Joists 175 x 85 mm | Electrical work | UNLOADING of R.S. Joists 175 x 85 mm | As per relevent standard specification | 50 | EA | 100
218 | SMR40009 | 1.2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for First coat of 1st GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 2617.2
219 | SWR10877 | 1..2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 1st coat of Aluminium | Electrical work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 1021.2
220 | SMR40010 | 1.2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for second coat of 2nd GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 1551.6
221 | SWR10879 | 1.2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 2nd coat of Aluminium | Electrical work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 578.4
222 | SWR22091 | 2 | Coil earthing of pole with No.8 GI wire | Electrical work | Coil earthing of pole with No.8 GI wire | As per relevent standard specification | 20 | EA | 40
223 | SWR11890 | 0.217 | ERECTION OF S.S. STRUCTURE: Coping of 0.45x0.45x0.45Mt with 1:8 slope Using form boxes (0.031Cumt.) | Electrical work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | EA | 844.781
224 | SMR22222 | 12 | Supply 33KV 3x400Sqmm Outdoor End Kit | Electrical work | Supply 33KV 3x400Sqmm Outdoor End Kit | As per relevent standard specification | 4554 | EA | 54648
225 | SMR22223 | 3 | Supply of 33KV 3x400SQmm Straight through joint kit | Electrical work | Supply of 33KV 3x400SQmm Straight through joint kit |  | 24151 | EA | 72453
226 | SMR11506 | 12 | 33KV 3X400 Heat Shble in/d end ter kit | Electrical work | 33KV 3X400 Heat Shble in/d end ter kit | As per relevent standard specification | 3589.96 | EA | 43079.52
227 | SMR12303 | 1000 | S-RS Joist Pole (175x85mm) | Electrical work | S-RS Joist Pole (175x85mm) | As per relevent standard specification | 60.75 | KGS | 60750
[6 empty] | Total |  |  | 13992845.0844 | 55320
1 | SWR34179 | 10 | Cutting and Levelling the site with the help of JCB including cost,conveyance of all materials,hire charges etc complete for finished item of work. | JCB | NA | As per relevant standard specification | 2164.1 | H | 21641
2 | SWR33015 | 100.79 | Earth Work Mass Excavation (Ordinary rock not requiring blasting) to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions, labour and material charges etc., complete as directed by the engineer-incharge. | Earth Work | NA | As per relevant standard specification | 347 | M3 | 34974.13
3 | SWR33028 | 25.3 | PCC (1:4:8) for levelling course using 40mm size hard broken Granite stone including cost and conveyance of all materials, HBG metal for foundations and leveling course and as directed by the Engineer- in - charge etc complete for finished item of work. | PCC | NA | As per relevant standard specification | 4182 | M3 | 105804.6
4 | SWR33041 | 126.6 | CRS masonry in CM (1:6) using Hard Granite Stones including cost and conveyance of all materials, seignorage charges, labour charge for construction and for dressing stones to required size and shape, dewatering, scaffolding, cutting for all leads and lifts, all incidental charges etc. complete for finished item of work as directed by the Engineer - in - charge. | Masonry | NA | As per relevant standard specification | 4525 | M3 | 572865
5 | SWR33068 | 19.4 | Construction of brick masonary in CM(1:6) including cost and conveyance of all materials, labour charges etc. complete for finished item of work | Masonry | NA | As per relevant standard specification | 7679 | M3 | 148972.6
6 | SWR33052 | 886.38 | Supplying and filling with borrowed gravel, watering, ramming, consolidating thoroughly complying with the standard specification including cost and conveyance of all materials, labour charges, hire charges of machinery, with all leads and incidental charges etc complete for finished item work | Gravel | NA | As per relevant standard specification | 435 | M3 | 385575.3
7 | SWR33098 | 6.53 | RCC M20 GRADE Nominal Mix (a) Footings | RCC | NA | As per relevant standard specification | 8322 | M3 | 54342.66
8 | SWR33100 | 4.77 | RCC M20 GRADE Nominal Mix (b) Columns | RCC | NA | As per relevant standard specification | 11017 | M3 | 52551.09
9 | SWR33099 | 1.65 | RCC M20 GRADE Nominal Mix (c) Plinth Beams | RCC | NA | As per relevant standard specification | 10742 | M3 | 17724.3
10 | SWR33107 | 0.72 | RCC M20 GRADE Nominal Mix (d) Lintels | RCC | NA | As per relevant standard specification | 11177 | M3 | 8047.44
11 | SWR33114 | 11.7 | RCC M20 GRADE Nominal Mix (e) Sunshade | RCC | NA | As per relevant standard specification | 1169 | M2 | 13677.3
12 | SWR33121 | 2.35 | RCC M20 GRADE Nominal Mix (f) Roof Beams | RCC | NA | As per relevant standard specification | 10752 | M3 | 25267.2
13 | SWR33128 | 6.94 | RCC M20 GRADE Nominal Mix (g) Slab | RCC | NA | As per relevant standard specification | 10303 | M3 | 71502.82
14 | SWR33144 | 2.4 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) / Mild steel (MS) steel bars (Fe 415/ Fe 500 grade as per IS 1786-1979) of different diameters for RCC works complete for finished item of work in all floors.( APSS No.126) | Steel | NA | As per relevant standard specification | 76127 | TO | 182704.8
15 | SWR33163 | 317.06 | Providing plastering of 20mm thick to all uneven faces of walls and ceiling of superstructure in two coats with base coat in CM 1:6 of 16mm thick and top coat in Cm 1:4 4mm thick with dubara sponge finish | Plastering | NA | As per relevant standard specification | 416 | M2 | 131896.96
16 | SWR33184 | 136.5 | Raised pointing in CM(1:3) including curing, cost and conveyance of all materials and labour charges for complete item of work. | Plastering | NA | As per relevant standard specification | 95 | M2 | 12967.5
17 | SWR33156 | 54.87 | Providing impervious coat over RCC roof slab surfaces to requried slopes with 20mm thick in CM 1:3 pro mixed with approvaled brand of water proffing compound as the raet of 1 kg per bag of cement inclding cost and conveyance of all materials | Plastering | NA | As per relevant standard specification | 445 | M2 | 24417.15
18 | SWR33264 | 5.7 | Supply and fixing of Flush type Doors with 35mm Thick Flush Shutters with Bondwood solied Block Board Type Faced on Both the sides with Commercial Type Plywood for finished item work as directed by the Engineer - in- charge. | Doors | NA | As per relevant standard specification | 6799.02 | M2 | 38754.414
19 | SWR33277 | 5.76 | Supply and Fixing of Aluminium sliding windows with fixed glass panels using aluminium sections 62x32x1.2mm providing 5mm plain glass fixed to frame with beading gasket and glazing clips with all accessories, locking arrangements including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Windows | NA | As per relevant standard specification | 3381.54 | M2 | 19477.6704
20 | SWR33310 | 6.25 | Supplying and fixing of MS safety grill with peripheral frame of ISA 25x25x4mm and horizontal & vertical 8mm square rods and including cost and coveyance of all mateirals with all leads and lifts, labour charges, painting charges complete for finished item of work | Windows | NA | As per relevant standard specification | 2539 | M2 | 15868.75
21 | SWR33219 | 26.5 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and approved size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and pointing with cement, labour etc, complete for finished item of work. | Flooring | NA | As per relevant standard specification | 662 | M2 | 17543
22 | SWR33236 | 6.94 | Providing skirting with tandoor blue slabs including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Flooring | NA | As per relevant standard specification | 729 | M2 | 5059.26
23 | SWR33029 | 40.07 | Plain Cement contrete - Nominal Mix (1:3:6) using 40 mm metal with concrete mixture including cost and conveyance of all materials labour charges etc. complete for finished iitem of work and as directed by the engineer-in-charge. | PCC | NA | As per relevant standard specification | 4484 | M3 | 179673.88
24 | SWR33030 | 6.75 | PCC(1:2:4) using 10 to 12 mm aggregate including cost and conveyance of all materials labour charges etc., complete for finished iitem of work and as directed by the engineer-in-charge. | PCC | NA | As per relevant standard specification | 5599 | M3 | 37793.25
25 | SWR33057 | 65.92 | Supply and Spreading of 20mm machine crushed metal including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | HBG metal | NA | As per relevant standard specification | 1514 | M3 | 99802.88
26 | SWR33403 | 110 | Supply and fixing of fencing of welded wire mesh (2"x2") of 3mm dia with support channels of 75x 40mm and angles around of 30x30x3 mm including cost and conveyance of all materials, fabrication charges, painting charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Welded mesh | NA | As per relevant standard specification | 2042 | M2 | 224620
27 | SWR33404 | 10 | Painting with two coats of OBD over a coat of primer including cost and conveyance of all materials ,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Paint | NA | As per relevant standard specification | 4579.89 | M2 | 45798.9
28 | SWR33333 | 107.9 | Painting with two coats of ACE paint over a coat of primer including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Paint | NA | As per relevant standard specification | 109.9 | M2 | 11858.21
29 | SWR33336 | 153 | Painting with lovely cem three coats including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Paint | NA | As per relevant standard specification | 195.91 | M2 | 29974.23
30 | SWR33329 | 196.5 | Supply and fixing of MS gates of approved design including cost and conveyance of all materials,fabrication charges etc complete for finished item of work. | Gate | NA | As per relevant standard specification | 70.47 | M2 | 13847.355
31 | SWR33442 | 25 | S&F Conceal PVC Pipe 32mm dia in Slab | Electrification | NA | As per relevant standard specification | 85 | RMT | 2125
32 | SWR33441 | 15 | S&F Conceal PVC Pipe 20mm dia in Wall | Electrification | NA | As per relevant standard specification | 89 | RMT | 1335
33 | SWR33457 | 15 | Wiring with 2X1.0 Sqm(14/.3mm) PVC insulated flexiable copper cable in the existing metalic/Non metalic conduit pipe with 6A mini modular SP switch, mounted on metalic box covereds with appropriate front plate modules etc ceiling rose including cot and conveyance of all mateials, labour charges complete for light points, bell points and fan points in non residential builsing except circuit moving finished in all types masonary as directed by department. | Electrification | NA | As per relevant standard specification | 580 | EA | 8700
34 | SWR33461 | 2 | Supply and fixing of 6A 3/2 pin flush type plug socket with 6A flush type marked switch control on a common board with earth continuity including wire leads earth connections along with all labour charges etc. complete | Electrification | NA | As per relevant standard specification | 469 | EA | 938
35 | SWR33464 | 2 | Supply and fixing of 16A 3pin flush type plug socket and 16A flush type fuse unit and 16A switch control. | Electrification | NA | As per relevant standard specification | 437 | EA | 874
36 | SWR33484 | 4 | Supply and fixing of slanting holders with 100W bulb with all connections and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | NA | As per relevant standard specification | 116 | EA | 464
37 | SWR33545 | 4 | Supply and fixing of patty type tube light fitting with 4' 0" - 40W tube light,40W copper choke,starter,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | NA | As per relevant standard specification | 868 | EA | 3472
38 | SWR33494 | 90 | Supply and run of 2 of 14/.3mm(1.00Sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | NA | As per relevant standard specification | 48 | RMT | 4320
39 | SWR33497 | 30 | Supply and run of 2 of 36/0.3 (2.5sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | NA | As per relevant standard specification | 95 | RMT | 2850
40 | SWR33520 | 1 | SPN Distribution board with IP-20 protection suitable for single phase 40A DP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 4Nos as out going MCBs in sheet steel enclosure including connections and cost of all material labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | NA | As per relevant standard specification | 5038 | EA | 5038
41 | SWR33596 | 1 | Providing independent earthing for main switches,IC cutouts and motors using 40mm. Dia. B-class G.I.Pipe of 2.5' length duly providing 12mm. Dia. 6No. Holes and required bolts,nuts and washers,including filling with equal preparation of salt and charcoal in layers and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | NA | As per relevant standard specification | 4891 | EA | 4891
42 | SWR33597 | 15 | Supply and run of No.8 SWG Copper wire including cost of all accessories and labour charges etc., Complete | Electrification | NA | As per relevant standard specification | 140 | RMT | 2100
43 | SWR33563 | 2 | Supply and Fixing of 48" ceiling fan of bajaj make(or equivalent make) including cost material,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Flooring | NA | As per relevant standard specification | 2215 | EA | 4430
44 | SWR33224 | 15.8 | Supply and fixing of ceramic tiles fantacy for dadoing including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 762 | M2 | 12039.6
45 | SWR34311 | 1 | Supply and fixing of 580mm x 440mm long Orissa pan of Parry, Neycer or Hindhusthan, make with 'P' or 'S' trap etc complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 2178 | EA | 2178
46 | SWR34386 | 2 | Supply and Fixing 4" PVC floor trap including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 269 | EA | 538
47 | SWR34382 | 2 | Supply,fixing 90mm dia. PVC Plain Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 84 | EA | 168
48 | SWR34385 | 1 | Supply,fixing 90mm dia. PVC Door Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 81 | EA | 81
49 | SWR34286 | 1 | S&Fixing 150mm x 100mm SWG gully traps Ist class grating & const. brick masonry in CM (1:6) prop inter mediate chamber and fitted with CI frame etc complete. | Plumbing | NA | As per relevant standard specification | 749 | EA | 749
50 | SWR34377 | 6 | Supply and Fixing 4" dia 3M Single socket PVC pipe including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 422 | RMT | 2532
51 | SWR34453 | 1 | Supply and Fixing 4" dia PVC cowl including labour charges etc. complete for finished item of work. | Plumbing | NA | As per relevant standard specification | 23 | EA | 23
52 | SWR34444 | 1 | Construction of soak pit with 4' dia RCM rings upto a depth of 6' including cost and conveyance of all materials as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 2950 | EA | 2950
53 | SWR34361 | 20 | CPVC Pipes and Fittings b) 22.20mm OD Pipe - SDR 11 | Plumbing | NA | As per relevant standard specification | 239 | RMT | 4780
54 | SWR34362 | 100 | CPVC Pipes and Fittings c) 28.60mm OD Pipe - SDR 11 | Plumbing | NA | As per relevant standard specification | 313 | RMT | 31300
55 | SWR34363 | 100 | Supply and fixing of 15mm dia. SS coated taps including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 410 | RMT | 41000
56 | SWR34344 | 18 | Supply and fixing of 20mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 230 | EA | 4140
57 | SWR34345 | 1 | Supply and fixing of 25mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 331 | EA | 331
58 | SWR34346 | 2 | Supply and fixing of 12.7mm bib tap Indian make including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 466 | EA | 932
59 | SWR34329 | 3 | Providing and placing on Terrace polyetheylene water storage tank with double layer approved brand and manufacture with cover complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 271 | EA | 813
60 | SWR34375 | 500 | Supply of steel table of size 4'x2.5'x30" with 18 mm plywood fixed with rubber beeding with drawers on right side with automatic locking arrangements etc complete for finished item of work and as directed by the engineer-in-charge. | Furniture | NA | As per relevant standard specification | 10 | L | 5000
61 | SWR34740 | 1 | Supply of 'S' type chair with arms teakwood frame with seat back 's' type on G.I pipe including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Furniture | NA | As per relevant standard specification | 5000 | EA | 5000
62 | SWR33857 | 1 | Supply of P V C chairs of Neelkamal of approved quality & make including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Furniture | NA | As per relevant standard specification | 3850 | EA | 3850
63 | SWR33858 | 2 | S&F Glow Sign Board | Board | NA | As per relevant standard specification | 1150 | EA | 2300
64 | SWR33406 | 150 | S-LDPE Sheet 500Micron | LDPE sheet | NA | As per relevant standard specification | 1411 | EA | 211650
65 | SWR33405 | 76 | S&Filling with Borrowed Stone Dust | Stone Dust | NA | As per relevant standard specification | 1269 | EA | 96444
66 | SWR33407 | 450 | Manufacture, supply ,laying and fixing of 450mm dia. NP3 class R.C.C. socket and spigot pipes (rate per meter of effective length) including transportaion ,taxes and duties etc. complete for finished item of work and as directed by the Engineer-in-charge. | Hume pipe | NA | As per relevant standard specification | 260.05 | M | 117022.5
67 | SWR33421 | 1.35 | S&F RCC Fencing Pole 0.115mx0.115mx2.7m in pits of size 0.5x0.5x0.5 m and refilled with P.C.C(1:4:8) using 20 mm HBG metal including cost & conveyance of all materials, labour charges etc complete for finished item of work. | Fencing poles | NA | As per relevant standard specification | 4542.3 | Sqm | 6132.105
68 | SWR33423 | 1.8 | S&F RCC Fencing Pole 0.1mx0.1mx1.8m in pits of size 0.5x0.5x0.5 m and refilled with P.C.C(1:4:8) using 20 mm HBG metal including cost & conveyance of all materials, labour charges etc complete for finished item of work. | Fencing poles | NA | As per relevant standard specification | 1930.48 | Sqm | 3474.864
69 | SWR33608 | 1 | S&Fixing of barbed wire 8 straight strands and 2 cross strands including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Barbed wire | NA | As per relevant standard specification | 5000 | EA | 5000
70 | SWR33609 | 90 | Prov supply of electricity to the site | Power Supply | NA | As per relevant standard specification | 336 | M | 30240
71 | SWR34830 | 90 | Geophysical Investgation Charges | Borewell | NA | As per relevant standard specification | 369 | M | 33210
72 | SWR33611 | 30 | Drilling-165mm Bore Well 0 to 90M | Borewell | NA | As per relevant standard specification | 844 | M | 25320
73 | SWR33636 | 1 | Drilling-165mm Bore Well 90m & above | Borewell | NA | As per relevant standard specification | 34237 | EA | 34237
74 | SWR33641 | 60 | S&F 160mm dia PVC Casing | Borewell | NA | As per relevant standard specification | 190 | EA | 11400
75 | SWR33644 | 1 | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | Borewell | NA | As per relevant standard specification | 1040 | EA | 1040
76 | SWR34203 | 1 | S&R 3C 2.5sqmm Flat Copper Cable | Borewell | NA | As per relevant standard specification | 182 | EA | 182
77 | SWR34410 | 178 | S&E D.O.L Starter 250V Single Phase | Borewell | NA | As per relevant standard specification | 160 | Rmt | 28480
78 | SWR34470 | 100.4 | Supply & fixing of Flange Clamps | Borewell | NA | As per relevant standard specification | 40 | M3 | 4016
79 | SWR34471 | 96.5 | S&F HDPE Pipe 40mm dia 6kg/sqcm | Borewell | NA | As per relevant standard specification | 97.5 | M3 | 9408.75
80 | SWR34472 | 886.38 | Seigniorage Charges - Sand | Seignorages | NA | As per relevant standard specification | 30 | M3 | 26591.4
[8 empty] | Civil Total | 3411093.8684
[8 empty] | Elec & Civil total | 17403938.9528

## 2. Arutla SS
Arutla SS Scdules
Name of the work: Estimate for erection of new 33/11 KV SS with connected 33 KV and 11 KV lines at Arutla (V) in Kandi(M) of Sangareddy Division of Sangareddy Circle (WBS No: S-1707-90-06-01-01-001).
S.No | SSR Code | Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR10105 | 39 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 23400
2 | SWR10343 | 31 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 74400
3 | SWR10356 | 27.28 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt)*31 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 179475.12
4 | SWR11890 | 0.96 | ERECTION OF S.S. STRUCTURE: Coping of 0.45x0.45x0.45Mt with 1:8 slope Using form boxes (0.031Cumt.) | Civil work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | M3 | 3737.28
5 | SWR11331 | 31 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of poles with two coats of white cement (including cost of paint). | Electrical work | Paint-9.1M PSCC Poles as desc SSR | As per relevent standard specification | 485 | EA | 15035
6 | SWR11889 | 5.5 | Fabrication of 100 X 50mm MS Channel for formation of 11kV and 33kV bays: Fabrication and erection of M.S,Channel 100x50mm for forming of 33KV & 11 KV Bays as per standard specifications to facilitate stringing of bus, erection of LA sets, AB Switches bolts & Nuts etc. including painting with one coats of red oxide and two coats of Aluminium paint. GI bolts&nuts shall be used. | Electrical work | Fabr & Erect-MS Chnl 100x50mm for SS Bay | As per relevent standard specification | 6600 | TO | 36300
7 | SWR10404 | 116 | Erection of 33kV and 11kV Strung Bus with Panther (200Sqmm) ACSR Conductor: Erection of 33kV and 11kV Bus over the Substation structures with 200sqmm Panther ACSR conductor and giving Jumpers to connect the Switch gear by providing the suitable T clamps and round clamps suitable to Post type insulators & Insulators. | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 38010.88
8 | SWR10884 | 50 | Connectionof equipment to bus and or another equipmentwithsingle zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Electrical work | Conn. of equip/bus single zebra/panther | As per relevent standard specification | 224 | EA | 11200
9 | SWR10392 | 2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 9000
10 | SWR10393 | 9 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 28800
11 | SWR11742 | 3 | Supply & erection of 11 kV 400 A convential single(1/3) phasing AB switches.includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | S&E-400A 11KV ABSwth Conv 1ph(1/3) in SS | As per relevent standard specification | 4232 | EA | 12696
12 | SWR21240 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt). | Electrical work | Hoisting post ins&hrd wr 1panther 33kv | As per relevent standard specification | 781 | EA | 1562
13 | SWR21241 | 4 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 11kv | As per relevent standard specification | 507 | EA | 2028
14 | SWR10881 | 11 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 1562
15 | SWR23224 | 16.46 | Excavation of pit in all types of soils of size 2.2x2.2x0.85Mts.for Construction of Plinths for VCB (33KV & 11 KV ) | Earth work | Excavate-Pit for 33KV VCB | As per relevent standard specification | 331 | M3 | 5448.26
16 | SWR20685 | 22.24 | Providing of Base concreting (2.2x2.2x0.15 Mts) with 1:3:6 Concrete mix. Using form boxes, Providing of Concreting (2x2x1.0mts) with 1:3:6 Cocrete mix. Plastering of the plinth for smooth finishing with 12mm thick 1:3 cement motor and providing two coats white washing for part of the plinth above groung level. | Civil work | Cement concrete with 40MM metal VCB plin | As per relevent standard specification | 5160 | M3 | 114758.4
17 | SWR10461 | 4 | Erection of Switchgear complete for 11 kV VCB includes Assembling the VCB Structures and mounting the VCBs over the already erected foudation including wiring of Breaker Control Panel/CTs, erection of CTs and control pannel providing Jumpers. | Electrical work | Erection of 11kv VCB | As per relevent standard specification | 12000 | EA | 48000
18 | SWR10396 | 2 | Erection of 33KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 1760
19 | SWR10397 | 1 | Erection of 11 KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 11kv LA stn type incl earthing | As per relevent standard specification | 559 | SET | 559
20 | SWR10398 | 3 | Erection of 11 KV Lightening Arrestors line type complete including jumpering. | Electrical work | Erect of 11kvLA line type incl earthing | As per relevent standard specification | 505 | SET | 1515
21 | SMR11607 | 1 | Supply of 33kv HG fuse set including providing of jumpers | Electrical work | S-33KV HG Fuse Set excl Ins & Chnl | As per relevent standard specification | 6431 | SET | 6431
22 | SWR10394 | 1 | Erection of 33kv HG fuse set including providing of jumpers | Electrical work | Erect. of 33kv HG Fuseset incl earthing | As per relevent standard specification | 1331.81 | SET | 1331.81
23 | SMR11608 | 1 | Supply of 11kv HG fuse set including providing of jumpers | Electrical work | S-11KV HG Fuse Set | As per relevent standard specification | 1733.75 | SET | 1733.75
24 | SWR10395 | 1 | Erection of 11kv HG fuse set including providing of jumpers | Electrical work | Erect. of 11kv HG Fuseset incl earthing | As per relevent standard specification | 740.52 | SET | 740.52
25 | SMR11482 | 22 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 76692
26 | SWR10357 | 22 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 27152.4
27 | SWR10920 | 500 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification.75x8 mm MS flat for Earth mat and connecting to electrodes. | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 32500
28 | SWR10919 | 950 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification. 50x6 mm MS flat for raisers, double flat shall be run for structure poles raisers & equipment earthing. | Electrical work | Earthing for raisers of SS Flat 50x6 mm. | As per relevent standard specification | 41 | RMT | 38950
29 | SMR40033 | 2 | Providing of double earthing for neutral with flexible copper jumpers of adequate size including arrangement by fixing M.S.Channel 100x50mm. | Electrical work | SupCU Flexi jumper for Power T/F Neutral | As per relevent standard specification | 4725 | EA | 9450
30 | SWR11771 | 4 | Erection of 24 Volts Battery along with Charger on the VCB plinth and giving DC supply to VCB's. | Electrical work | Erect-24V Batery with Chrgr incl grot-SS | As per relevent standard specification | 1050 | EA | 4200
31 | SWR11474 | 600 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable includes excavation of earth and back filling with sand and earth in alternate layers . The cable termination shall be made by providing proper size lugs and shall be identified with colours. | Electrical work | Laying-4 core cable | As per relevent standard specification | 15 | RMT | 9000
32 | SWR10463 | 1 | Erection of 25 KVA Three phase Station Transformer on the Substation Structures and giving jumpers/connections on HT side to the 11kV bus. Belting angle shall be provided both sides of DTR for securing DTR firmly in position. | Electrical work | Erection of Three Phase DTRs | As per relevent standard specification | 1139.95 | EA | 1139.95
33 | SMR40045 | 1 | Supply of AC Panel Board includes: Fixing of 1 No.100A, MCCB, 10kA capacity of any standard make including material cost. Fixing of suitable panel box 3x3x1 with M.S.Sheet of 16 SWG with front door compartments inclusive of material cost & powder coating (with C Channel ). Fabrication of panel Fixing of 96x96mm analog voltmeter with VSS switch Fixing of 20A HRC fuse Fixing of 3 phase supply indicator kwith HRC fuses Supply and fixing of 6 Sqmm copper flexible wire (PVC) Fixing of Stud type TBs for outgoing feeder Fixing of Epoxy bus supports. | Electrical work | Supply of AC Supply panel complete | As per relevent standard specification | 42000 | EA | 42000
34 | SMR40044 | 1 | Supply of DC Panel Board Fixing of suitable panel box of size 6'x6'x1' with M S sheet of 16 SWG with back doors (4'x6') and on front side with provision to fix up bakelite hylam sheet size of 4'x6' including cost of the panel with powder coating. Fixing of best quality of angles for panel. Fixing of C Channelfor panel. Fabrication of control panel including making suitable holes and board Fixing of Stud type TBs for outgoing feeder Fixing of 24V DC pilot lamps of standard make Fixing of healthy trip push buttons with LED lamp Fixing of plain switches for alarm acceptance and for PTR signal Fixing of ON/OFF push buttons Fixing of digital volt meter for 11kV Fixing of VSS of standard make, Fixing of Engraved AL plates for Alarm panel of various VCB Laying of 2.5Sqmm copper flexible wire for internal wiring . Fixing of digital frequency meter Fixing of Copper lugs and ferrules for internal wiring. Fixing of 4" Gang bells 24V DC Fixing of flow diagram with rading strip Fixing of HRC fuse units | Electrical work | Supply of DC Anunc.relay panel 8 feeders | As per relevent standard specification | 42500 | EA | 42500
35 | SWR20025 | 1 | fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supplied by tenderer. | Electrical work | 33/11kv S.S Erection of AC&DC Panel | As per relevent standard specification | 7871.85 | SET | 7871.85
36 | SWR10342 | 8 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 12000
37 | SWR10956 | 8 | Fixing of Metal halide/LED lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5M GI pipe complete. | Electrical work | Fixing of LED/Metal halide complete. | As per relevent standard specification | 1268 | EA | 10144
38 | SWR20028 | 8 | Supply and Fixing of junction box and Providing with proper Fuse protection and required glauds suitable for Cable Terminations. The box shall be fixed on the pole. | Electrical work | 33/11kv S.S Yard lighting junction box | As per relevent standard specification | 351.9 | EA | 2815.2
39 | SWR20526 | 1 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply & fixing of marshall box | As per relevent standard specification | 3085.5 | EA | 3085.5
40 | SMR40088 | 1 | Supply and fixing of filled sand bucket set complete (4 Nos. Buckets) with stand to mount fire buckets. | Electrical work | Sup Fire Buckets Stand with Buckets | As per relevent standard specification | 1386 | SET | 1386
41 | SMR40087 | 2 | Supply and fixing of CO2 Cylinder set as per IS2878 Specifications. | Electrical work | Sup TrollyMounted Co2 Cylinders(IS-2878) | As per relevent standard specification | 9240 | EA | 18480
42 | SWR11895 | 1 | Supplying and fixing of feeder indicator board to each of the 3Nos feeder breakers and LV breaker, danger boards made of 1'x1' and properly mounted on the structures. The letters written on the borad shall be 1.5"size with blue colour and background shall be of white colour | Electrical work | S&F-33/11KV SS Feeder Indicator Board | As per relevent standard specification | 551 | SET | 551
43 | SWR20032 | 1 | Supply and fixing of wooden board of size 3'x2'.5'indicating the layout of the Switch yard. | Electrical work | Sup &fix of board ind Switchyard layout | As per relevent standard specification | 1654 | EA | 1654
44 | SMR40086 | 1 | Supply and Erection of Permanent Name Board of on 3'x4' steel sheetmounted on steel frame as described in Specification. | Electrical work | Sup 33/11kv S.S Permanent name board | As per relevent standard specification | 10238 | EA | 10238
45 | SMR40076 | 1 | Supply of Digital clamp meter. | Electrical work | Supply of Digital clamp meter. | As per relevent standard specification | 2888 | EA | 2888
46 | SMR40064 | 1 | Supply of Rechargeable LED torch light of Standard make. | Electrical work | Sup Rechargeable LED torch light. | As per relevent standard specification | 1733 | EA | 1733
47 | SMR40063 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box containing ‘D’Spanners from size 6 to 54, Hammer small and big size, Ring spanners from 6 to 28, Adjustable spanner, Pipe wrench, Cutting Plier, Nose plier, Tester, insulated Screw drive. | Electrical work | SupTaparia Tool kit complete as per Spec | As per relevent standard specification | 4925 | SET | 4925
48 | SWR22090 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Electrical work | Sup& fix safety inst/SS Op. inst board | As per relevent standard specification | 2205 | EA | 2205
49 | SMR11598 | 8 | Supply of 25 W LED lamp with fitting of philips make | Electrical work | S-25W LED fixture set | As per relevent standard specification | 3200 | EA | 25600
50 | SMR12378 | 1 | Supply of Alluminum Ladder(20 feet) | Electrical work | S-10ft Aluminium Ladder | As per relevent standard specification | 1654 | EA | 1654
51 | SMR40075 | 1 | Supply of Megger (2000 ohms, 0-2.5kv) | Electrical work | Supply of Earth megger (1000v) | As per relevent standard specification | 8085 | EA | 8085
52 | SMR11599 | 4 | Supply of Earth Discharging Rod 8 feet length, 3 mm thickness. | Electrical work | S-Earth Rod 8ft Long 3mm Thick | As per relevent standard specification | 1000 | EA | 4000
53 | SMR11488 | 200 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 23500
54 | SMR11591 | 66 | Supply of PG clamps for panther 2 bolted 800 A. | Electrical work | S-Al. alloy three bolted PG clamps 800A | As per relevent standard specification | 130 | EA | 8580
55 | SWR20029 | 300 | Supply and Laying of 2 core/4 core cable includes excavation earth and back filling with sand and earth in alternate layers as shown in the sketch. The cable termination shall be made by providing proper size of lugs at both ends of the cable termination. | Electrical work | 33/11kv S.S laying of 2/4core for light | As per relevent standard specification | 50 | M | 15000
56 | SWR20308 | 31 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 12625.99
57 | SWR20307 | 8 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 2172.16
58 | SWR11860 | 4 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 10881.36
59 | SWR10150 | 10.5 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 6479.55
60 | SWR10206 | 10.5 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 2320.5
61 | SWR10524 | 10.5 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 1942.5
62 | SWR11220 | 350 | Loading and unwinding of Panther conductor. | Electrical work | Load-Unwinding Panther conductor | As per relevent standard specification | 3 | M | 1050
63 | SWR11221 | 350 | Unloading of Panther conductor. | Electrical work | Unload-Unwinding Panther conductor | As per relevent standard specification | 2 | M | 700
64 | SWR12416 | 2 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 4
65 | SWR10631 | 2 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 4
66 | SWR10618 | 2 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 130
67 | SWR10632 | 2 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 130
68 | SWR10212 | 2 | Loading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | LOADING of 11kv Pin/Post/Solid Core Insu | As per relevent standard specification | 1 | CRT | 2
69 | SWR10530 | 2 | Unloading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | UNLOADING of 11kv Pin/Post/Solid Core In | As per relevent standard specification | 1 | CRT | 2
70 | SWR11701 | 600 | Loading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | Load-PVC Control Cable 10C | As per relevent standard specification | 1 | M | 600
71 | SWR11712 | 600 | Unloading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | UnLoad-PVC Control Cable 10C | As per relevent standard specification | 1.02 | M | 612
72 | SWR11691 | 1 | Loading of 3Ph 25KVA Distribution Transformer. | Electrical work | Load-3Ph 25KVA DTR | As per relevent standard specification | 252 | EA | 252
73 | SWR11692 | 1 | UnLoading of 3Ph 25KVA Distribution Transformer. | Electrical work | UnLoad-3Ph 25KVA DTR | As per relevent standard specification | 202 | EA | 202
74 | SWR10200 | 1 | Loading of 33/11 KV Current Transformers/ Potential Transformers. | Electrical work | LOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 165 | EA | 165
75 | SWR10266 | 6 | Loading of 33 KV10 KA LAs Station type. | Electrical work | LOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 41 | EA | 246
76 | SWR10584 | 6 | Unloading of 33 KV10 KA LAs Station type. | Electrical work | UNLOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 35 | EA | 210
77 | SWR10265 | 9 | Loading of 11 KV10 KA LAs Line type. | Electrical work | LOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 288
78 | SWR10583 | 9 | Unloading of 11 KV10 KA LAs Line type. | Electrical work | UNLOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 288
79 | SWR10264 | 3 | Loading of 11 KV10 KA LAs Station type. | Electrical work | LOADING of 11 KV,10 KA LAs Station type | As per relevent standard specification | 32 | EA | 96
80 | SWR10582 | 3 | Unloading of 11 KV10 KA LAs Station type. | Electrical work | UNLOADING of 11 KV,10 KA LAs Station typ | As per relevent standard specification | 32 | EA | 96
81 | SWR10239 | 2 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 252
82 | SWR10557 | 2 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 158
83 | SWR10238 | 9 | loading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 720
84 | SWR10556 | 9 | Unloading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 720
85 | SWR11224 | 4 | Loading and Unloading of 12V/24V Battery Set. | Electrical work | Load/Unload-12V/24V Battery Set | As per relevent standard specification | 23 | EA | 92
86 | SWR10356 | 2.66 | ERECTION OF S.S. STRUCTURE: Providing of base concreting of size 0.76x0.76x0.15M with CC mix of ratio 1:3:6 Using form boxes(0.087Cu.Mt)x31 with 20mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 17500.14
87 | SWR10402 | 1 | Erection of 11kv Potential Transformer sets complete including jumpering. The LV side of the PT shall be provided with proper fuse protection mounted in separate marshalling boxwith proper size cable glands etc. The box shall be mounted on the Substation structure. | Electrical work | Erection of 11kv three phase PT s | As per relevent standard specification | 800 | SET | 800
88 | SWR10518 | 1 | Unloading of 33/11 KV Current Transformers/ Potential Transformers | Electrical work | UNLOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 128 | EA | 128
89 | SWR10674 | 1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67 | 1132927.79
90 | SWR10356 | 4.32 | Concreting the location after erection of 8.0 Mtrs pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) ( 0.6x0.6x1.5)mtrs x 8 . | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 28421.28
91 | SWR21750 | 2 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply and fixing of PT Marshalling box | As per relevent standard specification | 1139.85 | EA | 2279.7
92 | SMR40067 | 2 | Supply of Hand Gloves | Electrical work | Supply of Hand Gloves | As per relevent standard specification | 289 | SET | 578
93 | SMR40071 | 2 | Supply of Safety Helmets of standard make | Electrical work | Supply of Safety Helmet of standard make | As per relevent standard specification | 231 | EA | 462
94 | SMR40009 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for First coat of 1st GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 11995.5
95 | SWR10877 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 1st coat of Aluminium | Electrical work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 4680.5
96 | SMR40010 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for second coat of 2nd GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 7111.5
97 | SWR10879 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 2nd coat of Aluminium | Electrical work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 2651
98 | SMR25233 | 31 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 96391.71
99 | SMR22745 | 5500 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 315975
100 | SMR12321 | 2350 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 132587
101 | SMR12322 | 2280 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 128820
102 | SMR25232 | 8 | Supply of 8.0Mtr PSCC 140 Kg Pole | Electrical work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 12640
103 | SMR12315 | 2 | Supply of 33KV 800A DB Break AB Switch | Electrical work | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 81317.56
104 | SMR12316 | 2 | Supply of 11KV 800A DB Break AB Switch | Electrical work | S-11KV 800A DB Break AB Switch | As per relevent standard specification | 30847.46 | EA | 61694.92
105 | SMR12317 | 7 | Supply of 11KV 400A DB Break AB Switch | Electrical work | S-11KV 400A DB Break AB Switch | As per relevent standard specification | 18150 | EA | 127050
106 | SMR25200 | 1 | Supply of LT Distribution Box (SMC) | Electrical work | S-LT Distribution Box (SMC) | As per relevent standard specification | 7797 | EA | 7797
107 | SWR22092 | 4.274 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 3269.61
108 | SWR12087 | 10 | Excavation of Pole pits of size 2.4"x2.4"x8.2" (0.75M x 0.75M x 2.5M) 1.406 cum for 15mtrs Spun Poles including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except hard rock requiring blasting. | Earth work | Excvt Pit ext HardBlst 0.75Mx0.75Mx2.5M | As per relevent standard specification | 990 | EA | 9900
109 | SWR10107 | 28 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 19600
110 | SWR10112 | 5 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | As per relevent standard specification | 1680 | EA | 8400
111 | SWR10105 | 10 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 6000
112 | SWR10350 | 10 | Erection of Spun PSCC poles 12.5 Mtrs / 12.9Mtrs in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical work | Erection of Spun pole 12.5Mt | As per relevent standard specification | 4115.7 | EA | 41157
113 | SWR10978 | 33 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 137454.24
114 | SWR10343 | 10 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 24000
115 | SWR10981 | 15 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Horizontal Cut point for 33 KV line | As per relevent standard specification | 1759.5 | EA | 26392.5
116 | SWR10356 | 16.238 | Concreting the location after erection of 12.5Mtrs/11 Mtrs pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole. Using form boxes for 4 No's spun poles (0.75x0.75x1.95 Mts) *7 = 10.108 cu mtr , 6 No's11.0 mtr poles (0.76x0.76x1.83mtrs)*6 = 6.3 cu mtr. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 106829.802
117 | SWR10366 | 4.274 | Paving of the 100 sqmm AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 12600.06 | KM | 53852.6564
118 | SWR11321 | 10 | Dismantling of 11 Mtrs PSCC poles | Electrical work | Dismantle-11 Mtrs PSCC poles | As per relevent standard specification | 1813.15 | EA | 18131.5
119 | SWR11310 | 2.734 | Restringing of 100 Sqmm Single ckt 3 cond existing loose Lines by removing the pin-binding and jumpers, Providing of temporary stays, providing stiffners pieces, replacement of damaged insulators, alignment of cross arms, pin binding and jumpering after tensioning and removing of the temporary stays complete | Electrical work | Restring-100 Sqmm SC-3 Conductors | As per relevent standard specification | 9600 | KM | 26246.4
120 | SWR11308 | 0.3 | Restringing of 55 Sqmm Single ckt 3 cond existing loose Lines by removing the pin-binding and jumpers, Providing of temporary stays, providing stiffners pieces, replacement of damaged insulators, alignment of cross arms, pin binding and jumpering after tensioning and removing of the temporary stays complete | Electrical work | Restring-55 Sqmm SC-3 Conductors | As per relevent standard specification | 6400 | KM | 1920
121 | SMR11488 | 150 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 17625
122 | SWR11185 | 10 | Sub Transportation of spun Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt any Spun Pole incl. L&UL<10KM | As per relevent standard specification | 771.38 | EA | 7713.8
123 | SWR11180 | 33 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 14255.01
124 | SWR20308 | 10 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 4072.9
125 | SWR10191 | 3 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 606
126 | SWR10509 | 3 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 300
127 | SWR11860 | 3 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 8161.02
128 | SWR10150 | 2.86 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 1764.906
129 | SWR10206 | 2.86 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 632.06
130 | SWR10524 | 2.86 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 529.1
131 | SWR10211 | 30 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 90
132 | SWR10529 | 30 | Unloading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 90
133 | SWR12416 | 9 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 18
134 | SWR10631 | 9 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 18
135 | SWR10618 | 4 | Loading of 33KV Metal parts bag of 25 nos | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 260
136 | SWR10632 | 4 | Unloading of 33 KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 260
137 | SWR10354 | 6 | Erection of 33 kv Stay set complete including fixing of bow ,fixing and binding of Eye bolt, Anchor rod, guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. | Electrical work | Assembly and erection of Stay set 33kv | As per relevent standard specification | 684.53 | SET | 4107.18
138 | SWR21190 | 6 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock,Hard rock Requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 3120
139 | SWR10319 | 230 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 75 x 8 mm MS Flat | Electrical work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31 | EA | 7130
140 | SWR10322 | 48 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 75 x 8 mm MS Flat | Electrical work | Fab Stay clamps with 75x8 mm MM Flat | As per relevent standard specification | 42 | EA | 2016
141 | SWR10378 | 43 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevent standard specification | 32 | EA | 1376
142 | SMR25236 | 33 | Supply of 11Mtr PSCC 365 Kg Pole | Electrical work | S-PSCC Pole 11Mtr 365 Kg | As per relevent standard specification | 5399 | EA | 178167
143 | SMR25233 | 10 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 31094.1
144 | SMR25229 | 118 | Supply of 33KV V-Cross Arm without Clamps | Electrical work | S-33KV V-Cross Arm without Clamps | As per relevent standard specification | 1678 | EA | 198004
145 | SMR25207 | 660 | Supply of MS Angle 65X65X6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 37785
146 | SMR22745 | 1500 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 86175
147 | SMR12321 | 950 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 53599
148 | SMR25231 | 6 | Supply of 33KV MS Stay Set with BasePlate | Electrical work | S-33KV MS Stay Set with BasePlate | As per relevent standard specification | 1035 | SET | 6210
149 | SMR25238 | 10 | Supply of 12.5Mtr spun Pole | Electrical work | S-PSCC Spun Pole 12.5Mtr | As per relevent standard specification | 15635.59 | EA | 156355.9
150 | SWR22092 | 3.32 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 11 kv line. | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 2539.8 | 11KV line
151 | SWR10107 | 6 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11/9.1 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 4200
152 | SWR10105 | 40 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1/8.0 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 24000
153 | SWR10110 | 16 | Excavation of Pole pits of size (2.6" x 2.6" x 5.0') 0.88 cum 0.76 M x 0.76M x 1.52M for 9.1 mtrs PSCC Poles including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD (2.6" x 2.6" x 5.0') | As per relevent standard specification | 1440 | EA | 23040
154 | SWR10978 | 2 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 8330.56
155 | SWR10343 | 60 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 144000
156 | SWR10342 | 22 | Erection of 8.0 Mts PSCC Poles including fixing of 11 KV X arm and top cleats and fixing of Pin insulators complete with necessary hard ware for tangential locations excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 33000
157 | SWR10653 | 17 | Formation of 11 kv cut points (Vertical/Horizantal) including fixing of 11 KV Cross arms,clamps, strain insulators sets complete with hardware and stays (Bows and Eye-bolts), Excluding the cost of pit Excavation and pole erection. The contractor has to supply GI Bolts and Nuts. | Electrical work | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1350 | EA | 22950
158 | SWR10356 | 20.474 | Concreting the location after erection of 11 / 9.1 Mtrs pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole. Using form boxes for 2 No's 11 poles (0.76x0.76x1.83 Mts) *2 = 2.102 cu mtr , 34 No's 9.1 mtr poles (0.6x0.6x1.5mtrs)*34 = 18.36 cu mtr | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 134698.446
159 | SWR10365 | 3.32 | Paving of the conductor 55 Sqmm Single Circuit (3 Conductors) AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 3 Cond | As per relevent standard specification | 8500 | KM | 28220
160 | SMR11488 | 100 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 11750
161 | SWR10206 | 0.92 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 203.32
162 | SWR10524 | 0.92 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 170.2
163 | SWR11248 | 198 | Loading 11KV Polymer Pin Insulator with GI pins | Electrical work | Load-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 198
164 | SWR11249 | 198 | Unloading 11KV Polymer Pin Insulator with GI pins | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 198
165 | SWR10134 | 0.92 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 540.5184
166 | SWR11862 | 2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 20 KM and upto 30 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 7382.76
167 | SWR10191 | 2 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 404
168 | SWR10509 | 2 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 200
169 | SWR11180 | 2 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 863.94
170 | SWR20308 | 60 | Sub Transportation of 9.1M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 24437.4
171 | SWR20307 | 22 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 5973.44
172 | SWR10228 | 53 | Loading of 11 KV V - Cross arms | Electrical work | LOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 212
173 | SWR10546 | 53 | Unloading of 11 KV V - Cross arms | Electrical work | UNLOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 212
174 | SWR12402 | 6 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 288
175 | SWR12421 | 6 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 288
176 | SWR10251 | 53 | Loading of 11 KV Top fittings | Electrical work | LOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 53
177 | SWR10569 | 53 | Unloading of 11 KV Top fittings | Electrical work | UNLOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 53
178 | SWR12416 | 6 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 12
179 | SWR10631 | 6 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 12
180 | SWR10353 | 13 | Erection of 11 kv Stay set complete including fixing of bow, fixing and binding of Eye bolt,Anchor rod,guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Assembly and erection of Stay set11kv&LT | As per relevent standard specification | 606.85 | SET | 7889.05
181 | SWR10319 | 4 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 75 x 8 mm MS Flat | Electrical work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31 | EA | 124
182 | SWR10322 | 16 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 75 x 8 mm MS Flat | Electrical work | Fab Stay clamps with 75x8 mm MM Flat | As per relevent standard specification | 42 | EA | 672
183 | SWR10320 | 72 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 50 x 6 mm MS Flat | Electrical work | Fab Back clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 15 | EA | 1080
184 | SWR10323 | 98 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 50 x 6 mm MS Flat | Electrical work | Fab Stay clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 25 | EA | 2450
185 | SWR10378 | 62 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevent standard specification | 32 | EA | 1984
186 | SWR21190 | 13 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In Hard Gravel and Hard murram not requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 6760
187 | SMR25236 | 2 | Supply of 11Mtr PSCC 365 Kg Pole | Electrical work | S-PSCC Pole 11Mtr 365 Kg | As per relevent standard specification | 5399 | EA | 10798
188 | SMR25233 | 60 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 186564.6
189 | SMR25232 | 22 | Supply of 8.0Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 34760
190 | SMR25218 | 53 | Supply of 11KV V X-Arms with MS Angle 65x65x6 | Electrical work | S-11KV V X-Arms with MS Angle 65x65x6 | As per relevent standard specification | 743 | EA | 39379
191 | SMR25205 | 360 | Supply of MS Channel 75x40 mm | Electrical work | S-MS Channel 75x40 mm | As per relevent standard specification | 58.45 | KG | 21042
192 | SMR25206 | 250 | Supply of MS Angle 50x50x6 | Electrical work | S-MS Angle 50x50x6 | As per relevent standard specification | 58.15 | KG | 14537.5
193 | SMR12321 | 60 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 3385.2
194 | SMR12322 | 250 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 14125
195 | SMR25214 | 13 | Supply of LT/11KV MS Stay Sets with Base Plate | Electrical work | S-LT/11KV MS Stay Sets with Base Plate |  | 1168 | SET | 15184
196 | SWR10392 | 3 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 13500
197 | SWR10105 | 4 | ERECTION OF DP STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 2400
198 | SWR10343 | 4 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 9600
199 | SWR10356 | 2.16 | Concreting the location after erection of 9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes(0.6X0.6X1.5 Mts)*4 = 2.16 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 14210.64
200 | SMR11488 | 4 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 470
201 | SWR10206 | 0.65 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 143.65
202 | SWR10524 | 0.65 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 120.25
203 | SWR10134 | 0.65 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 381.888
204 | SWR20308 | 4 | Sub Transportation of 9.1M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 1629.16
205 | SWR12402 | 1 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 48
206 | SWR12421 | 1 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 48
207 | SWR12416 | 1 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 2
208 | SWR10631 | 1 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 2
209 | SMR11482 | 2 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 6972
210 | SWR10357 | 2 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 2468.4
211 | SWR34671 | 2 | providing of collar ring of 450mm dia at 4 pole structure | Electrical work | Collar/ Rings of 450mm dia | As per relevent standard specification | 250 | EA | 500
212 | SMR11485 | 35 | Supply of earthing GI Flat 25X3 mm including material | Electrical work | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 3675
213 | SWR10239 | 3 | Loading of 33 KV AB Switch Conventional 400/800 Amp | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 378
214 | SWR10557 | 3 | Unloading of 33 KV AB Switch Conventional 400/800 Amp | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 237
215 | SWR10421 | 18 | Fixing of T-Clamps | Electrical work | Fixing of T- clamp | As per relevent standard specification | 116 | EA | 2088
216 | SWR10404 | 5 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 1638.4
217 | SWR10884 | 9 | Connection of equipment to busand or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Electrical work | Conn. of equip/bus single zebra/panther | As per relevent standard specification | 224 | EA | 2016
218 | SMR12315 | 3 | Supply of 33KV 800A DB Break AB Switch | Electrical work | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 121976.34
219 | SMR25233 | 4 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 12437.64
220 | SMR25207 | 30 | Supply of MS Angle 65X65X6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 1717.5
221 | SMR22745 | 500 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 28725
222 | SMR12321 | 120 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 6770.4
223 | SWR10393 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 9600 | 1 pole AB Sw
224 | SMR11488 | 6 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 705
225 | SWR10206 | 0.26 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 57.46
226 | SWR10524 | 0.26 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 48.1
227 | SWR10134 | 0.26 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 152.7552
228 | SMR11484 | 3 | Supply of C I earth pipe of size 50mm dia, 2 mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 50mm dia 2m long | As per relevent standard specification | 2441 | EA | 7323
229 | SWR11222 | 6 | Loading/Unloading of C I earth pipe of size 80/50mm dia, 2 mtrs long for earth electrode | Electrical work | Load/Unload-CI pipe 80/50 mm dia 2mt L | As per relevent standard specification | 18 | EA | 108
230 | SWR34671 | 3 | providing of collar ring of 450mm dia at line AB switch | Electrical work | Collar/ Rings of 450mm dia | As per relevent standard specification | 250 | EA | 750
231 | SMR11485 | 30 | Supply of earthing GI Flat 25X3 mm including material | Electrical work | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 3150
232 | SWR10238 | 3 | Loading of 11 KV AB Switch Conventional 200/400 Amp | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 240
233 | SWR10556 | 3 | Unloading of 11 KV AB Switch Conventional 200/400 Amp | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 240
234 | SMR12317 | 3 | Supply of 11KV 400A DB Break AB Switch | Electrical work | S-11KV 400A DB Break AB Switch | As per relevent standard specification | 18150 | EA | 54450
235 | SMR25206 | 36 | Supply of MS Angle 50x50x6 | Electrical work | S-MS Angle 50x50x6 | As per relevent standard specification | 58.15 | KG | 2093.4
236 | SMR25205 | 120 | Supply of MS Channel 75x40 mm | Electrical work | S-MS Channel 75x40 mm | As per relevent standard specification | 58.45 | KG | 7014
237 | SMR12322 | 50 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 2825
[6 empty] | Total |  |  | 4622145.862
1 | SWR34179 | 6 | Cutting and Levelling the site with the help of JCB including cost,conveyance of all materials,hire charges etc complete for finished item of work. | Site | Hire-JCB to Level & Clear the Site | As per relevant standard specifiction | 2164.1 | H | 12984.6
2 | SWR33015 | 121.18 | Earth Work Mass Excavation (Ordinary rock not requiring blasting) to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions, labour and material charges etc., complete as directed by the engineer-incharge. | Earth Work | Excavation in Ordinary Soil | As per relevant standard specifiction | 347 | M3 | 42049.46
3 | SWR33028 | 21.69 | PCC (1:4:8) for levelling course using 40mm size hard broken Granite stone including cost and conveyance of all materials, HBG metal for foundations and leveling course and as directed by the Engineer- in - charge etc complete for finished item of work. | Civil | PCC with 40mm Metal (1:4:8) | As per relevant standard specifiction | 4064 | M3 | 88148.16
4 | SWR33041 | 126.9 | CRS masonry in CM (1:6) using Hard Granite Stones including cost and conveyance of all materials, seignorage charges, labour charge for construction and for dressing stones to required size and shape, dewatering,scaffolding,cutting for all leads and lifts, all incidental charges etc .complete for finished item of work as directed by the Engineer - in - charge. | Civil | CRS Masonary CM(1:6) 2nd Sort | As per relevant standard specifiction | 4437 | M3 | 563055.3
5 | SWR33068 | 20.6 | Construction of brick masonary in CM(1:6) including cost and conveyance of all materials, labour charges etc. complete for finished item of work | Civil | Brick Masonary in CM(1:6) GFloor | As per relevant standard specifiction | 7624 | M3 | 157054.4
6 | SWR33052 | 951.88 | Supplying and filling with borrowed gravel, watering, ramming, consolidating thoroughly complying with the standard specification including cost and conveyance of all materials, labour charges, hire charges of machinery, with all leads and incidental charges etc complete for finished item work | Civil | S&Filling with Borrowed Gravel | As per relevant standard specifiction | 435 | M3 | 414067.8
7 | SWR33098 | 7.25 | Reinforced Cement concerete M20 GRADE Nominal Mix for footings , columns, Beams and Slab using 12mm to 20mm size graded HBG machine crushed metal from approvaed quary giving cube crushing strenth of 20 N /sqm and a minimum of 400 kgs of cement for 1 cum of concrete including cost and conveyance charges for cement and all other materials to site, scaffolding charge, seignorage charges, centering, shuttering, machine mixing, laying concrete, curing for specified number of days vibrating etc compaction by pen vibrator or needle vibrator supplemented by hand spreeding rodding and tamping ,all incident and operational charges , all leads and lifts and for all leaving gaps and pockets etc complete, but excluding cost of steel and its fabrication, all incidental charges etc .complete for finshed item of work as directed by the Engineer-in-charge (a) Footings | Civil | RCC Footing: M20Gr, Steel Centering | As per relevant standard specifiction | 8227 | M3 | 59645.75
8 | SWR33100 | 6.51 | Reinforced Cement concerete M20 GRADE Nominal Mix for footings , columns, Beams and Slab using 12mm to 20mm size graded HBG machine crushed metal from approvaed quary giving cube crushing strenth of 20 N /sqm and a minimum of 400 kgs of cement for 1 cum of concrete including cost and conveyance charges for cement and all other materials to site, scaffolding charge, seignorage charges, centering, shuttering, machine mixing, laying concrete, curing for specified number of days vibrating etc compaction by pen vibrator or needle vibrator supplemented by hand spreeding rodding and tamping ,all incident and operational charges , all leads and lifts and for all leaving gaps and pockets etc complete, but excluding cost of steel and its fabrication, all incidental charges etc .complete for finshed item of work as directed by the Engineer-in-charge (b) Columns | Civil | RCC Column GF: M20Gr, Steel Centering | As per relevant standard specifiction | 10922 | M3 | 71102.22
9 | SWR33099 | 1.61 | Reinforced Cement concerete M20 GRADE Nominal Mix for footings , columns, Beams and Slab using 12mm to 20mm size graded HBG machine crushed metal from approvaed quary giving cube crushing strenth of 20 N /sqm and a minimum of 400 kgs of cement for 1 cum of concrete including cost and conveyance charges for cement and all other materials to site, scaffolding charge, seignorage charges, centering, shuttering, machine mixing, laying concrete, curing for specified number of days vibrating etc compaction by pen vibrator or needle vibrator supplemented by hand spreeding rodding and tamping ,all incident and operational charges , all leads and lifts and for all leaving gaps and pockets etc complete, but excluding cost of steel and its fabrication, all incidental charges etc .complete for finshed item of work as directed by the Engineer-in-charge (c) Plinth beams | Civil | RCC Plinth Beam: M20Gr, Steel Centering | As per relevant standard specifiction | 10647 | M3 | 17141.67
10 | SWR33107 | 0.55 | Reinforced Cement concerete M20 GRADE Nominal Mix for footings , columns, Beams and Slab using 12mm to 20mm size graded HBG machine crushed metal from approvaed quary giving cube crushing strenth of 20 N /sqm and a minimum of 400 kgs of cement for 1 cum of concrete including cost and conveyance charges for cement and all other materials to site, scaffolding charge, seignorage charges, centering, shuttering, machine mixing, laying concrete, curing for specified number of days vibrating etc compaction by pen vibrator or needle vibrator supplemented by hand spreeding rodding and tamping ,all incident and operational charges , all leads and lifts and for all leaving gaps and pockets etc complete, but excluding cost of steel and its fabrication, all incidental charges etc .complete for finshed item of work as directed by the Engineer-in-charge (d) Lintels | Civil | RCC Lintel GF: M20Gr, Steel Centering | As per relevant standard specifiction | 11082 | M3 | 6095.1
11 | SWR33114 | 11.7 | Reinforced Cement concerete M20 GRADE Nominal Mix for footings , columns, Beams and Slab using 12mm to 20mm size graded HBG machine crushed metal from approvaed quary giving cube crushing strenth of 20 N /sqm and a minimum of 400 kgs of cement for 1 cum of concrete including cost and conveyance charges for cement and all other materials to site, scaffolding charge, seignorage charges, centering, shuttering, machine mixing, laying concrete, curing for specified number of days vibrating etc compaction by pen vibrator or needle vibrator supplemented by hand spreeding rodding and tamping ,all incident and operational charges , all leads and lifts and for all leaving gaps and pockets etc complete, but excluding cost of steel and its fabrication, all incidental charges etc .complete for finshed item of work as directed by the Engineer-in-charge (e) Sunshade | Civil | RCC Sunshade GF: M20Gr, Steel Centering | As per relevant standard specifiction | 1162 | M2 | 13595.4
12 | SWR33121 | 2.35 | Reinforced Cement concerete M20 GRADE Nominal Mix for footings , columns, Beams and Slab using 12mm to 20mm size graded HBG machine crushed metal from approvaed quary giving cube crushing strenth of 20 N /sqm and a minimum of 400 kgs of cement for 1 cum of concrete including cost and conveyance charges for cement and all other materials to site, scaffolding charge, seignorage charges, centering, shuttering, machine mixing, laying concrete, curing for specified number of days vibrating etc compaction by pen vibrator or needle vibrator supplemented by hand spreeding rodding and tamping ,all incident and operational charges , all leads and lifts and for all leaving gaps and pockets etc complete, but excluding cost of steel and its fabrication, all incidental charges etc .complete for finshed item of work as directed by the Engineer-in-charge (e) Roof Beams | Civil | RCC Roof Beam GF: M20Gr, Steel Centering | As per relevant standard specifiction | 10657 | M3 | 25043.95
13 | SWR33128 | 6.94 | Reinforced Cement concerete M20 GRADE Nominal Mix for footings , columns, Beams and Slab using 12mm to 20mm size graded HBG machine crushed metal from approvaed quary giving cube crushing strenth of 20 N /sqm and a minimum of 400 kgs of cement for 1 cum of concrete including cost and conveyance charges for cement and all other materials to site, scaffolding charge, seignorage charges, centering, shuttering, machine mixing, laying concrete, curing for specified number of days vibrating etc compaction by pen vibrator or needle vibrator supplemented by hand spreeding rodding and tamping ,all incident and operational charges , all leads and lifts and for all leaving gaps and pockets etc complete, but excluding cost of steel and its fabrication, all incidental charges etc .complete for finshed item of work as directed by the Engineer-in-charge (f) Roof Slab | Civil | RCC Roof Slab GF: M20Gr, Steel Centering | As per relevant standard specifiction | 10208 | M3 | 70843.52
14 | SWR33144 | 2.6 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) / Mild steel (MS) steel bars (Fe 415/ Fe 500 grade as per IS 1786-1979) of different diameters for RCC works complete for finished item of work in all floors.( APSS No.126) | Civil | Reinforcement Steel Fe 415/500 | As per relevant standard specifiction | 75077 | TO | 195200.2
15 | SWR33163 | 353.86 | Providing plastering of 20mm thick to all uneven faces of walls and ceiling of superstructure in two coats with base coat in CM 1:6 of 16mm thick and top coat in Cm 1:4 4mm thick with dubara sponge finish | Civil | Plastering 20mm (16mm+4mm)GFloor | As per relevant standard specifiction | 410 | M2 | 145082.6
16 | SWR33184 | 155.64 | Raised pointing in CM(1:3) including curing, cost and conveyance of all materials and labour charges for complete item of work. | Civil | Raised Pointing to CRS Masonary CM(1:3) | As per relevant standard specifiction | 94 | M2 | 14630.16
17 | SWR33156 | 54.87 | Providing impervious coat over RCC roof slab surfaces to requried slopes with 20mm thick in CM 1:3 pro mixed with approvaled brand of water proffing compound as the raet of 1 kg per bag of cement inclding cost and conveyance of all materials | Civil | Impervious Coat 20mm CM(1:3) GFloor | As per relevant standard specifiction | 440 | M2 | 24142.8
18 | SWR33264 | 5.7 | Supply and fixing of Flush type Doors with 35mm Thick Flush Shutters with Bondwood solied Block Board Type Faced on Both the sides with Commercial Type Plywood for finished item work as directed by the Engineer - in- charge. | Doors | S&F MT Wood Frame & Door-Laminate | As per relevant standard specifiction | 6799.02 | M2 | 38754.414
19 | SWR33277 | 5.76 | Supply and Fixing of Aluminium sliding windows with fixed glass panels using aluminium sections 62x32x1.2mm providing 5mm plain glass fixed to frame with beading gasket and glazing clips with all accessories,locking arrangements including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Windows | S&F Aluminium Window | As per relevant standard specifiction | 3381.54 | M2 | 19477.6704
20 | SWR33310 | 6.25 | Supplying and fixing of MS safety grill with peripheral frame of ISA 25x25x4mm and horizontal & vertical 8mm square rods and including cost and coveyance of all mateirals with all leads and lifts, labour charges, painting charges complete for finished item of work | Windows | S&F of MS Safety Grill | As per relevant standard specifiction | 2539 | M2 | 15868.75
21 | SWR33219 | 29 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and approved size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and pointing with cement, labour etc, complete for finished item of work. | Flooring | Polished Shabad Flooring 20mm CM(1:3) | As per relevant standard specifiction | 659 | M2 | 19111
22 | SWR33236 | 10.67 | Providing skirting with tandoor blue slabs including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Flooring | Polished Shabad Skirting CM(1:3) | As per relevant standard specifiction | 726 | M2 | 7746.42
23 | SWR33029 | 34.11 | Plain Cement contrete - Nominal Mix (1:3:6) using 40 mm metal with concrete mixture including cost and conveyance of all materials labour charges etc. complete for finished iitem of work and as directed by the engineer-in-charge. | Civil | PCC with 40mm Metal (1:3:6) | As per relevant standard specifiction | 4371 | M3 | 149094.81
24 | SWR33030 | 14.73 | PCC(1:2:4) using 10 to 12 mm aggregate including cost and conveyance of all materials labour charges etc., complete for finished iitem of work and as directed by the engineer-in-charge. | Civil | PCC with 20mm Metal (1:2:4) | As per relevant standard specifiction | 5504 | M3 | 81073.92
25 | SWR33057 | 49.44 | Supply and Spreading of 20mm machine crushed metal including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | S&Spreading of 20mm HBG Metal | As per relevant standard specifiction | 1514 | M3 | 74852.16
26 | SWR33403 | 110 | Supply and fixing of fencing of welded wire mesh (2"x2") of 3mm dia with support channels of 75x 40mm and angles around of 30x30x3 mm including cost and conveyance of all materials, fabrication charges, painting charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Civil | S&F MS Security Fencing Mesh (2"X2") | As per relevant standard specifiction | 2042 | M2 | 224620
27 | SWR33333 | 73.7 | Painting with two coats of OBD over a coat of primer including cost and conveyance of all materials ,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Paint | Painting with OBD 2Coats+Primer | As per relevant standard specifiction | 109.9 | M2 | 8099.63
28 | SWR33336 | 177.8 | Painting with two coats of ACE paint over a coat of primer including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Paint | Painting SnowCem/Apex 2 Coats+Primer | As per relevant standard specifiction | 195.91 | M2 | 34832.798
29 | SWR33329 | 194.6 | Painting with lovely cem three coats including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Paint | Painting with SuryaCem of 3 Coat | As per relevant standard specifiction | 70.47 | M2 | 13713.462
30 | SWR33404 | 18.07 | Supply and fixing of MS gates of approved design including cost and conveyance of all materials,fabrication charges etc complete for finished item of work. | Civil | S&F MS Gate | As per relevant standard specifiction | 4579.89 | M2 | 82758.6123
31 | SWR33442 | 30 | Supply and fixing 32mm dia 1.5mm thick recessed( concealed) PVC pipe alnog with reinforcement to be laid in slab including No 14 SWG GI wire for earth contunity, cost of pipe, binding wire and all labour charges etc complete | Electrification | S&F Conceal PVC Pipe 25mm dia in Slab | As per relevant standard specifiction | 85 | RMT | 2550
32 | SWR33441 | 20 | Supply and fixing 20mm dia 1.5mm thick recessed( concealed) PVC pipe alog with reinforcement to be laid in slab including No 14 SWG GI wire for earth contunity, cost of pipe, binding wire and all labour charges etc complete | Electrification | S&F Conceal PVC Pipe 25mm dia in Wall | As per relevant standard specifiction | 89 | RMT | 1780
33 | SWR33457 | 15 | Wiring with 2X1.0 Sqm(14/.3mm) PVC insulated flexiable copper cable in the existing metalic/Non metalic conduit pipe with 6A mini modular SP switch, mounted on metalic box covereds with appropriate front plate modules etc ceiling rose including cot and conveyance of all mateials, labour charges complete for light points, bell points and fan points in non residential builsing except circuit moving finished in all types masonary as directed by department. | Electrification | S&F Modular Switch LP,FP,EFP for NRBuild | As per relevant standard specifiction | 580 | EA | 8700
34 | SWR33461 | 2 | Supply and fixing of 6A 3/2 pin flush type plug socket with 6A flush type marked switch control on a common board with earth continuity including wire leads earth connections along with all labour charges etc. complete | Electrification | S&F Modular 3/2pin 6A Sockets | As per relevant standard specifiction | 469 | EA | 938
35 | SWR33464 | 2 | Supply and fixing of 16A 3pin flush type plug socket and 16A flush type fuse unit and 16A switch control. | Electrification | S&F Modular 3pin 16/6A Sockets | As per relevant standard specifiction | 437 | EA | 874
36 | SWR33484 | 4 | Supply and fixing of slanting holders with 100W bulb with all connections and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F Batten Holder | As per relevant standard specifiction | 116 | EA | 464
37 | SWR33545 | 4 | Supply and fixing of patty type tube light fitting with 4' 0" - 40W tube light,40W copper choke,starter,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F 20W LED Retro Tube Light | As per relevant standard specifiction | 868 | EA | 3472
38 | SWR33494 | 90 | Supply and run of 2 of 14/.3mm(1.00Sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | S&R 2 of 14/0.3mm (1.0sqmm) (FR) | As per relevant standard specifiction | 48 | RMT | 4320
39 | SWR33497 | 30 | Supply and run of 2 of 36/0.3 (2.5sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | S&R 2 of 36/0.3mm (2.5sqmm) (FR) | As per relevant standard specifiction | 95 | RMT | 2850
40 | SWR33520 | 1 | SPN Distribution board with IP-20 protection suitable for single phase 40A DP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 4Nos as out going MCBs in sheet steel enclosure including connections and cost of all material labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F 8wySPNDB IP-20,10kA-6-32A SPMCB 4No | As per relevant standard specifiction | 5038 | EA | 5038
41 | SWR33596 | 1 | Providing independent earthing for main switches,IC cutouts and motors using 40mm. Dia. B-class G.I.Pipe of 2.5' length duly providing 12mm. Dia. 6No. Holes and required bolts,nuts and washers,including filling with equal preparation of salt and charcoal in layers and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | Provd-Independent Earthing | As per relevant standard specifiction | 4891 | EA | 4891
42 | SWR33597 | 15 | Supply and run of No.8 SWG Copper wire including cost of all accessories and labour charges etc., Complete | Electrification | S&R No.8 SWG Copper Wire | As per relevant standard specifiction | 140 | RMT | 2100
43 | SWR33563 | 2 | Supply and Fixing of 48" ceiling fan of bajaj make(or equivalent make) including cost material,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F 1200mm (48'') Sweep Ceiling Fan | As per relevant standard specifiction | 2215 | EA | 4430
44 | SWR33224 | 13.7 | Supply and fixing of ceramic tiles fantacy for dadoing including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Flooring | Ceramic Tile Flooring 20mm CM(1:3) | As per relevant standard specifiction | 759 | M2 | 10398.3
45 | SWR34311 | 1 | Supply and fixing of 580mm x 440mm long Orissa pan of Parry, Neycer or Hindhusthan, make with 'P' or 'S' trap etc complete for finished item of work and as directed by the engineer-in-charge. | Sanitary | S&F Orissa Pan WC 580mmx440mm | As per relevant standard specifiction | 2178 | EA | 2178
46 | SWR34386 | 2 | Supply and Fixing 4" PVC floor trap including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Sanitary | S&F Floor Trap (Bell Mouth) 110mm | As per relevant standard specifiction | 269 | EA | 538
47 | SWR34382 | 2 | Supply,fixing 90mm dia. PVC Plain Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Sanitary | S&F 90mm dia Plain Bend PVC/SWR Pipe | As per relevant standard specifiction | 84 | EA | 168
48 | SWR34385 | 1 | Supply,fixing 90mm dia. PVC Door Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Sanitary | S&F 75mm dia Door Bend PVC/SWR Pipe | As per relevant standard specifiction | 81 | EA | 81
49 | SWR34286 | 1 | S&Fixing 150mm x 100mm SWG gully traps Ist class grating & const. brick masonry in CM (1:6) prop inter mediate chamber and fitted with CI frame etc complete. | Sanitary | S&F 150mmx100mm SWG Gully Trap | As per relevant standard specifiction | 749 | EA | 749
50 | SWR34377 | 6 | Supply and Fixing 4" dia 3M Single socket PVC pipe including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Sanitary | S&F 110mm dia 3M 1Socket PVC/SWR Pipe | As per relevant standard specifiction | 422 | RMT | 2532
51 | SWR34453 | 1 | Supply and Fixing 4" dia PVC cowl including labour charges etc. complete for finished item of work. | Sanitary | S&F 4" dia PVC Cowl | As per relevant standard specifiction | 23 | EA | 23
52 | SWR34444 | 1 | Construction of soak pit with 4' dia RCM rings upto a depth of 6' including cost and conveyance of all materials as directed by the engineer-in-charge. | Sanitary | Construct- 4' dia & 5' Ht Soak Pit | As per relevant standard specifiction | 2950 | EA | 2950
53 | SWR34362 | 150 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) a) 22.20mm OD Pipe - SDR 11 | Plumbing | S&F 22.20mm OD CPVC Pipe-SDR 11 | As per relevant standard specifiction | 313 | RMT | 46950
54 | SWR34363 | 100 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) b) 28.60mm OD Pipe - SDR 11 | Plumbing | S&F 28.60mm OD CPVC Pipe-SDR 11 | As per relevant standard specifiction | 410 | RMT | 41000
55 | SWR34344 | 24 | Supply and fixing of 15mm dia. SS coated taps including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F-15mm GM/Bronze Ball Valve | As per relevant standard specifiction | 230 | EA | 5520
56 | SWR34345 | 1 | Supply and fixing of 20mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F-20mm GM/Bronze Ball Valve | As per relevant standard specifiction | 331 | EA | 331
57 | SWR34346 | 2 | Supply and fixing of 25mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F-25mm GM/Bronze Ball Valve | As per relevant standard specifiction | 466 | EA | 932
58 | SWR34329 | 4 | Supply and fixing of 12.7mm bib tap Indian make including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F-15mm Bib Tap 400gm Full turn | As per relevant standard specifiction | 271 | EA | 1084
59 | SWR34375 | 1000 | Providing and placing on Terrace polyetheylene water storage tank with double layer approved brand and manufacture with cover complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F Polyethylene Water Storage Tank | As per relevant standard specifiction | 10 | L | 10000
60 | SWR34740 | 1 | Supply of steel table of size 4'x2.5'x30" with 18 mm plywood fixed with rubber beeding with drawers on right side with automatic locking arrangements etc complete for finished item of work and as directed by the engineer-in-charge. | Furniture | S-3x2ft Office Table | As per relevant standard specifiction | 5000 | EA | 5000
61 | SWR33857 | 1 | Supply of 'S' type chair with arms teakwood frame with seat back 's' type on G.I pipe including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Furniture | Supply of S-Type Chair | As per relevant standard specifiction | 3850 | EA | 3850
62 | SWR33858 | 2 | Supply of P V C chairs of Neelkamal of approved quality & make including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Furniture | Supply of PVC Chair | As per relevant standard specifiction | 1150 | EA | 2300
63 | SWR33422 | 2.5 | S&F Glow Sign Board including cost and conveyance of labour and material charges | Civil | S&F Glow Sign Board | As per relevant standard specifiction | 3730.36 | M2 | 9325.9
64 | SWR34656 | 759 | S-LDPE Sheet 500Micron including cost and conveyance of labour and material charges | Civil | S-LDPE Sheet 500Micron | As per relevant standard specifiction | 95 | M2 | 72105
65 | SWR33054 | 71.42 | S&Filling with Borrowed Stone Dust including cost and conveyance of labour and material charges | Civil | S&Filling with Borrowed Stone Dust | As per relevant standard specifiction | 1000 | M3 | 71420
66 | SWR33415 | 7.3 | Manufacture, supply ,laying and fixing of 450mm dia. NP3 class R.C.C. socket and spigot pipes (rate per meter of effective length) including transportaion ,taxes and duties etc. complete for finished item of work and as directed by the Engineer-in-charge. | Civil | S&F RCC Hume Pipe of 450mm dia | As per relevant standard specifiction | 1344 | Rmt | 9811.2
67 | SWR33425 | 1 | Prov supply of electricity to the site | Civil | Provd-Supply of Electricity to Site | As per relevant standard specifiction | 5677.88 | EA | 5677.88
68 | SWR33608 | 1 | Geophysical Investgation Charges | Electrification | Geophysical Investgation Charges | As per relevant standard specifiction | 5000 | EA | 5000
69 | SWR33609 | 90 | Drilling-165mm Bore Well 0 to 90M | Borewell | Drilling-165mm Bore Well 0 to 90M | As per relevant standard specifiction | 336 | M | 30240
70 | SWR34830 | 30 | Drilling-165mm Bore Well 90m to 120M | Borewell | Drill-165mm Bore Well 90M to 120M | As per relevant standard specifiction | 369 | M | 11070
71 | SWR34830 | 30 | Drilling-165mm Bore Well 120m to 150M | Borewell | Drill-165mm Bore Well 90M to 120M | As per relevant standard specifiction | 369 | M | 11070
72 | SWR33611 | 30 | S&F 160mm dia PVC Casing | Borewell | S&F 160mm dia PVC Casing | As per relevant standard specifiction | 844 | M | 25320
73 | SWR33636 | 1 | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | Borewell | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | As per relevant standard specifiction | 34237 | EA | 34237
74 | SWR33641 | 60 | S&R 3C 2.5sqmm Flat Copper Cable | Borewell | S&R 3C 2.5sqmm Flat Copper Cable | As per relevant standard specifiction | 190 | EA | 11400
75 | SWR33644 | 1 | S&E D.O.L Starter 250V Single Phase | Borewell | S&E D.O.L Starter 250V Single Phase | As per relevant standard specifiction | 1040 | EA | 1040
76 | SWR34203 | 1 | Supply & fixing of Flange Clamps | Borewell | Supply & ixing of Flange Clamps | As per relevant standard specifiction | 182 | EA | 182
77 | SWR34410 | 178 | S&F HDPE Pipe 40mm dia 6kg/sqcm | Borewell | S&F HDPE Pipe 40mm dia 6kg/sqcm | As per relevant standard specifiction | 160 | Rmt | 28480
78 | SWR33406 | 80 | S&F RCC Fencing Pole 0.115mx0.115mx2.7m in pits of size 0.5x0.5x0.5 m and refilled with P.C.C(1:4:8) using 20 mm HBG metal including cost & conveyance of all materials,labour chargesv etc complete for finished item of | Fencing | S&F RCC Fencing Pole 0.115mx0.115mx2.7m | As per relevant standard specifiction | 1433.9 | EA | 114712
79 | SWR33407 | 130 | S&Fixing of barbed wire 8 straight strands and 2 cross strands including cost & conveyance of all materials, labour charges etc complete for finished item of work. | Fencing | S&F Barbed Wire 8H & 2Cross | As per relevant standard specifiction | 260.05 | RMT | 33806.5
80 | SWR33421 | 1.35 | S&F MS Board with support channels and erection in pits size of 0.45x0.45x0.45m duly concreting with PCC (1:2:4) using 12 to 20mm metal including cost & conveyance of all materials, labour charges etc complete for finished item of work. | Name board | S&F MS Board | As per relevant standard specifiction | 4542.3 | M2 | 6132.105
81 | SWR34470 | 172.3 | Seigniorage Charges - Sand | Seignorages | Seigniorage Charges - Sand | As per relevant standard specifiction | 40 | M3 | 6892
82 | SWR34471 | 151.5 | Seigniorage Charges - Metal | Seignorages | Seigniorage Charges - Metal | As per relevant standard specifiction | 97.5 | M3 | 14771.25
83 | SWR34472 | 951.88 | Seigniorage Charges - Gravel | Seignorages | Seigniorage Charges - Gravel | As per relevant standard specifiction | 30 | M3 | 28556.4
[7 empty] | Civil total |  | 3400127.2717
[7 empty] | Civil & Electrical total |  | 8022273.1337

## 3. Gudpally SS
Gudpally SS Schedules
Name of the work: Estimate for erection of new 33/11 KV SS with connected 33 KV and 11 KV lines at Gudpally (V) in Mogudampally (M) of Zaheerabad Division of Sangareddy Circle (WBS No: S-1743-90-06-03-01-001).
S.No | SRR Codes | Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR10105 | 39 | ERECTION OF S.S. STRUCTURE: Coping of 0.45x0.45x0.45Mt with 1:8 slope Using form boxes (0.031Cumt.) | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 23400
2 | SWR10343 | 31 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 74400
3 | SWR10356 | 27.19 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt)*31 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 178883.01
4 | SWR11890 | 0.96 | ERECTION OF S.S. STRUCTURE: Coping of 0.45x0.45x0.45Mt with 1:8 slope Using form boxes (0.031Cumt.) | Civil work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | M3 | 3737.28
5 | SWR11331 | 31 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of poles with two coats of white cement (including cost of paint). | Electrical work | Paint-9.1M PSCC Poles as desc SSR | As per relevent standard specification | 485 | EA | 15035
6 | SWR11889 | 5.5 | Fabrication of 100 X 50mm MS Channel for formation of 11kV and 33kV bays: Fabrication and erection of M.S,Channel 100x50mm for forming of 33KV & 11 KV Bays as per standard specifications to facilitate stringing of bus, erection of LA sets, AB Switches bolts & Nuts etc. including painting with one coats of red oxide and two coats of Aluminium paint. GI bolts&nuts shall be used. | Electrical work | Fabr & Erect-MS Chnl 100x50mm for SS Bay | As per relevent standard specification | 6600 | TO | 36300
7 | SWR10404 | 118.5 | Erection of 33kV and 11kV Strung Bus with Panther (200Sqmm) ACSR Conductor: Erection of 33kV and 11kV Bus over the Substation structures with 200sqmm Panther ACSR conductor and giving Jumpers to connect the Switch gear by providing the suitable T clamps and round clamps suitable to Post type insulators & Insulators. | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 38830.08
8 | SWR10392 | 2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 9000
9 | SWR10393 | 7 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 22400
10 | SWR11742 | 3 | Supply & erection of 11 kV 400 A convential single(1/3) phasing AB switches.includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | S&E-400A 11KV ABSwth Conv 1ph(1/3) in SS | As per relevent standard specification | 4232 | EA | 12696
11 | SWR21240 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt). | Electrical work | Hoisting post ins&hrd wr 1panther 33kv | As per relevent standard specification | 781 | EA | 1562
12 | SWR21241 | 4 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 11kv | As per relevent standard specification | 507 | EA | 2028
13 | SWR10881 | 12 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 1704
14 | SWR23224 | 16.46 | Excavation of pit in all types of soils of size 2.2x2.2x0.85Mts.for Construction of Plinths for VCB (33KV & 11 KV ) | Earth work | Excavate-Pit for 33KV VCB | As per relevent standard specification | 331 | M3 | 5448.26
15 | SWR20685 | 22.264 | Providing of Base concreting (2.2x2.2x0.15 Mts) with 1:3:6 Concrete mix. Using form boxes, Providing of Concreting (2x2x1.0mts) with 1:3:6 Cocrete mix. Plastering of the plinth for smooth finishing with 12mm thick 1:3 cement motor and providing two coats white washing for part of the plinth above groung level. | Civil work | Cement concrete with 40MM metal VCB plin | As per relevent standard specification | 5160 | M3 | 114882.24
16 | SWR10461 | 4 | Erection of Switchgear complete for 11 kV VCB includes Assembling the VCB Structures and mounting the VCBs over the already erected foudation including wiring of Breaker Control Panel/CTs, erection of CTs and control pannel providing Jumpers. | Electrical work | Erection of 11kv VCB | As per relevent standard specification | 12000 | EA | 48000
17 | SWR10396 | 2 | Erection of 33KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 1760
18 | SWR10397 | 1 | Erection of 11 KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 11kv LA stn type incl earthing | As per relevent standard specification | 559 | SET | 559
19 | SWR10398 | 3 | Erection of 11 KV Lightening Arrestors line type complete including jumpering. | Electrical work | Erect of 11kvLA line type incl earthing | As per relevent standard specification | 505 | SET | 1515
20 | SMR11607 | 1 | Supply of 33kv HG fuse set including providing of jumpers | Electrical work | S-33KV HG Fuse Set excl Ins & Chnl | As per relevent standard specification | 6431 | SET | 6431
21 | SWR10394 | 1 | Erection of 33kv HG fuse set including providing of jumpers | Electrical work | Erect. of 33kv HG Fuseset incl earthing | As per relevent standard specification | 1331.81 | SET | 1331.81
22 | SMR11608 | 1 | Supply of 11kv HG fuse set including providing of jumpers | Electrical work | S-11KV HG Fuse Set | As per relevent standard specification | 1733.75 | SET | 1733.75
23 | SWR10395 | 1 | Erection of 11kv HG fuse set including providing of jumpers | Electrical work | Erect. of 11kv HG Fuseset incl earthing | As per relevent standard specification | 740.52 | SET | 740.52
24 | SMR11482 | 23 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 80178
25 | SWR10357 | 23 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 28386.6
26 | SWR10920 | 500 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification.75x8 mm MS flat for Earth mat and connecting to electrodes. | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 32500
27 | SWR10919 | 500 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification. 50x6 mm MS flat for raisers, double flat shall be run for structure poles raisers & equipment earthing. | Electrical work | Earthing for raisers of SS Flat 50x6 mm. | As per relevent standard specification | 41 | RMT | 20500
28 | SMR40033 | 2 | Providing of double earthing for neutral with flexible copper jumpers of adequate size including arrangement by fixing M.S.Channel 100x50mm. | Electrical work | SupCU Flexi jumper for Power T/F Neutral | As per relevent standard specification | 4725 | EA | 9450
29 | SWR11771 | 4 | Erection of 24 Volts Battery along with Charger on the VCB plinth and giving DC supply to VCB's. | Electrical work | Erect-24V Batery with Chrgr incl grot-SS | As per relevent standard specification | 1050 | EA | 4200
30 | SWR11474 | 700 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable includes excavation of earth and back filling with sand and earth in alternate layers . The cable termination shall be made by providing proper size lugs and shall be identified with colours. | Electrical work | Laying-4 core cable | As per relevent standard specification | 15 | RMT | 10500
31 | SWR10463 | 1 | Erection of 25 kVA Three phase Station Transformer on the Substation Structures and giving jumpers/connections on HT side to the 11kV bus. Belting angle shall be provided both sides of DTR for securing DTR firmly in position. | Electrical work | Erection of Three Phase DTRs | As per relevent standard specification | 1139.95 | EA | 1139.95
32 | SMR40045 | 1 | Supply of AC Panel Board includes: Fixing of 1 No.100A, MCCB, 10kA capacity of any standard make including material cost. Fixing of suitable panel box 3x3x1 with M.S.Sheet of 16 SWG with front door compartments inclusive of material cost & powder coating (with C Channel ). Fabrication of panel Fixing of 96x96mm analog voltmeter with VSS switch Fixing of 20A HRC fuse Fixing of 3 phase supply indicator kwith HRC fuses Supply and fixing of 6 Sqmm copper flexible wire (PVC) Fixing of Stud type TBs for outgoing feeder Fixing of Epoxy bus supports. | Electrical work | Supply of AC Supply panel complete | As per relevent standard specification | 42000 | EA | 42000
33 | SMR40044 | 1 | Supply of DC Panel Board Fixing of suitable panel box of size 6'x6'x1' with M S sheet of 16 SWG with back doors (4'x6') and on front side with provision to fix up bakelite hylam sheet size of 4'x6' including cost of the panel with powder coating. Fixing of best quality of angles for panel. Fixing of C Channelfor panel. Fabrication of control panel including making suitable holes and board Fixing of Stud type TBs for outgoing feeder Fixing of 24V DC pilot lamps of standard make Fixing of healthy trip push buttons with LED lamp Fixing of plain switches for alarm acceptance and for PTR signal Fixing of ON/OFF push buttons Fixing of digital volt meter for 11kV Fixing of VSS of standard make, Fixing of Engraved AL plates for Alarm panel of various VCB Laying of 2.5Sqmm copper flexible wire for internal wiring . Fixing of digital frequency meter Fixing of Copper lugs and ferrules for internal wiring. Fixing of 4" Gang bells 24V DC Fixing of flow diagram with rading strip Fixing of HRC fuse units | Electrical work | Supply of DC Anunc.relay panel 8 feeders | As per relevent standard specification | 42500 | EA | 42500
34 | SWR20025 | 1 | fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supplied by tenderer. | Electrical work | 33/11kv S.S Erection of AC&DC Panel | As per relevent standard specification | 7871.85 | SET | 7871.85
35 | SWR10342 | 8 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 12000
36 | SWR10356 | 4.368 | Concreting the location after erection of pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) ( 0.6x0.6x1.5)mtrs | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 28737.072
37 | SWR10956 | 8 | Fixing of Metal halide/LED lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5M GI pipe complete. | Electrical work | Fixing of LED/Metal halide complete. | As per relevent standard specification | 1268 | EA | 10144
38 | SWR20028 | 8 | Supply and Fixing of junction box and Providing with proper Fuse protection and required glauds suitable for Cable Terminations. The box shall be fixed on the pole. | Electrical work | 33/11kv S.S Yard lighting junction box | As per relevent standard specification | 351.9 | EA | 2815.2
39 | SWR20526 | 2 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply & fixing of marshall box | As per relevent standard specification | 3085.5 | EA | 6171
40 | SMR40088 | 1 | Supply and fixing of filled sand bucket set complete (4 Nos. Buckets) with stand to mount fire buckets. | Electrical work | Sup Fire Buckets Stand with Buckets | As per relevent standard specification | 1386 | SET | 1386
41 | SMR40087 | 2 | Supply and fixing of CO2 Cylinder set as per IS2878 Specifications. | Electrical work | Sup TrollyMounted Co2 Cylinders(IS-2878) | As per relevent standard specification | 9240 | EA | 18480
42 | SWR11895 | 1 | Supplying and fixing of feeder indicator board to each of the 3Nos feeder breakers and LV breaker, danger boards made of 1'x1' and properly mounted on the structures. The letters written on the borad shall be 1.5"size with blue colour and background shall be of white colour | Electrical work | S&F-33/11KV SS Feeder Indicator Board | As per relevent standard specification | 551 | SET | 551
43 | SWR20032 | 1 | Supply and fixing of wooden board of size 3'x2'.5'indicating the layout of the Switch yard. | Electrical work | Sup &fix of board ind Switchyard layout | As per relevent standard specification | 1654 | EA | 1654
44 | SMR40086 | 1 | Supply and Erection of Permanent Name Board of on 3'x4' steel sheetmounted on steel frame as described in Specification. | Electrical work | Sup 33/11kv S.S Permanent name board | As per relevent standard specification | 10238 | EA | 10238
45 | SMR40076 | 1 | Supply of Digital clamp meter. | Electrical work | Supply of Digital clamp meter. | As per relevent standard specification | 2888 | EA | 2888
46 | SMR40064 | 1 | Supply of Rechargeable LED torch light of Standard make. | Electrical work | Sup Rechargeable LED torch light. | As per relevent standard specification | 1733 | EA | 1733
47 | SMR40063 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box containing ‘D’Spanners from size 6 to 54, Hammer small and big size, Ring spanners from 6 to 28, Adjustable spanner, Pipe wrench, Cutting Plier, Nose plier, Tester, insulated Screw drive. | Electrical work | SupTaparia Tool kit complete as per Spec | As per relevent standard specification | 4925 | SET | 4925
48 | SWR22090 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Electrical work | Sup& fix safety inst/SS Op. inst board | As per relevent standard specification | 2205 | EA | 2205
49 | SMR11598 | 8 | Supply of 25 W LED lamp with fitting of philips make | Electrical work | S-25W LED fixture set | As per relevent standard specification | 3200 | EA | 25600
50 | SMR12378 | 1 | Supply of Alluminum Ladder(20 feet) | Electrical work | S-10ft Aluminium Ladder | As per relevent standard specification | 1654 | EA | 1654
51 | SMR40075 | 1 | Supply of Megger (2000 ohms, 0-2.5kv) | Electrical work | Supply of Earth megger (1000v) | As per relevent standard specification | 8085 | EA | 8085
52 | SMR11599 | 4 | Supply of Earth Discharging Rod 8 feet length, 3 mm thickness. | Electrical work | S-Earth Rod 8ft Long 3mm Thick | As per relevent standard specification | 1000 | EA | 4000
53 | SMR11488 | 200 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 23500
54 | SMR11591 | 66 | Supply of PG clamps for panther 2 bolted 800 A. | Electrical work | S-Al. alloy three bolted PG clamps 800A | As per relevent standard specification | 130 | EA | 8580
55 | SWR20029 | 200 | Supply and Laying of 2 core/4 core cable includes excavation earth and back filling with sand and earth in alternate layers as shown in the sketch. The cable termination shall be made by providing proper size of lugs at both ends of the cable termination. | Electrical work | 33/11kv S.S laying of 2/4core for light | As per relevent standard specification | 50 | M | 10000
56 | SWR20308 | 31 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 12625.99
57 | SWR20307 | 8 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 2172.16
58 | SWR11860 | 4 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 10881.36
59 | SWR10150 | 10.61 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 6547.431
60 | SWR10206 | 10.61 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 2344.81
61 | SWR10524 | 10.61 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 1962.85
62 | SWR11220 | 350 | Loading and unwinding of Panther conductor. | Electrical work | Load-Unwinding Panther conductor | As per relevent standard specification | 3 | M | 1050
63 | SWR11221 | 350 | Unloading of Panther conductor. | Electrical work | Unload-Unwinding Panther conductor | As per relevent standard specification | 2 | M | 700
64 | SWR12416 | 1 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 2
65 | SWR10631 | 1 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 2
66 | SWR10618 | 1 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 65
67 | SWR10632 | 1 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 65
68 | SWR10212 | 1 | Loading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | LOADING of 11kv Pin/Post/Solid Core Insu | As per relevent standard specification | 1 | CRT | 1
69 | SWR10530 | 1 | Unloading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | UNLOADING of 11kv Pin/Post/Solid Core In | As per relevent standard specification | 1 | CRT | 1
70 | SWR11701 | 700 | Loading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | Load-PVC Control Cable 10C | As per relevent standard specification | 1 | M | 700
71 | SWR11712 | 700 | Unloading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | UnLoad-PVC Control Cable 10C | As per relevent standard specification | 1.02 | M | 714
72 | SWR11691 | 1 | Loading of 3Ph 25KVA Distribution Transformer. | Electrical work | Load-3Ph 25KVA DTR | As per relevent standard specification | 252 | EA | 252
73 | SWR11692 | 1 | UnLoading of 3Ph 25KVA Distribution Transformer. | Electrical work | UnLoad-3Ph 25KVA DTR | As per relevent standard specification | 202 | EA | 202
74 | SWR10200 | 1 | Loading of 33/11 KV Current Transformers/ Potential Transformers. | Electrical work | LOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 165 | EA | 165
75 | SWR10266 | 6 | Loading of 33 KV10 KA LAs Station type. | Electrical work | LOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 41 | EA | 246
76 | SWR10584 | 6 | Unloading of 33 KV10 KA LAs Station type. | Electrical work | UNLOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 35 | EA | 210
77 | SWR10265 | 9 | Loading of 11 KV10 KA LAs Line type. | Electrical work | LOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 288
78 | SWR10583 | 9 | Unloading of 11 KV10 KA LAs Line type. | Electrical work | UNLOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 288
79 | SWR10264 | 3 | Loading of 11 KV10 KA LAs Station type. | Electrical work | LOADING of 11 KV,10 KA LAs Station type | As per relevent standard specification | 32 | EA | 96
80 | SWR10582 | 3 | Unloading of 11 KV10 KA LAs Station type. | Electrical work | UNLOADING of 11 KV,10 KA LAs Station typ | As per relevent standard specification | 32 | EA | 96
81 | SWR10239 | 2 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 252
82 | SWR10557 | 2 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 158
83 | SWR10238 | 8 | loading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 640
84 | SWR10556 | 8 | Unloading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 640
85 | SWR11224 | 4 | Loading and Unloading of 12V/24V Battery Set. | Electrical work | Load/Unload-12V/24V Battery Set | As per relevent standard specification | 23 | EA | 92
86 | SWR10356 | 2.66 | ERECTION OF S.S. STRUCTURE: Providing of base concreting of size 0.76x0.76x0.15M with CC mix of ratio 1:3:6 Using form boxes(0.087Cu.Mt)x31 with 20mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 17500.14
87 | SWR10402 | 1 | Erection of 11kv Potential Transformer sets complete including jumpering. The LV side of the PT shall be provided with proper fuse protection mounted in separate marshalling boxwith proper size cable glands etc. The box shall be mounted on the Substation structure. | Electrical work | Erection of 11kv three phase PT s | As per relevent standard specification | 800 | SET | 800
88 | SWR10518 | 1 | Unloading of 33/11 KV Current Transformers/ Potential Transformers | Electrical work | UNLOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 128 | EA | 128
89 | SWR10674 | 1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
90 | SWR10356 | 4.32 | Concreting the location after erection of 8.0 Mtrs pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) ( 0.6x0.6x1.5)mtrs x 8 . | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 28421.28
91 | SWR21750 | 1 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply and fixing of PT Marshalling box | As per relevent standard specification | 1139.85 | EA | 1139.85
92 | SMR40067 | 2 | Supply of Hand Gloves | Electrical work | Supply of Hand Gloves | As per relevent standard specification | 289 | SET | 578
93 | SMR40071 | 2 | Supply of Safety Helmets of standard make | Electrical work | Supply of Safety Helmet of standard make | As per relevent standard specification | 231 | EA | 462
94 | SMR40009 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for First coat of 1st GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 11995.5
95 | SWR10877 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 1st coat of Aluminium | Electrical work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 4680.5
96 | SWR20904 | 20 | Supply & Providing of Panther T clamps |  | Supply & Providing of Panther T clamps. | As per relevent standard specification | 320 | EA | 6400
97 | SMR40010 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for second coat of 2nd GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 7111.5
98 | SWR10879 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 2nd coat of Aluminium | Electrical work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 2651
99 | SMR25233 | 8 | S-PSCC Pole 9.1Mtr 280kg | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 24875.28
100 | SMR25232 | 31 | S-PSCC Pole 8Mtr 140kg | Electrical work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 48980
101 | SMR12315 | 2 | S-33KV 800A DB Break AB Switch | Electrical work | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 81317.56
102 | SMR12316 | 1 | S-11KV 800A DB Break AB Switch | Electrical work | S-11KV 800A DB Break AB Switch | As per relevent standard specification | 30847.46 | EA | 30847.46
103 | SMR25211 | 6 | S-11KV 400A Conv ABSwitch with Insulator | Electrical work | S-11KV 400A Conv ABSwitch with Insulator | As per relevent standard specification | 11754 | EA | 70524
104 | SMR22745 | 5500 | S- MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 315975
105 | SMR12321 | 2350 | S-MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 132587
106 | SMR12322 | 2760 | S-MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 155940
107 | SMR25200 | 1 | S-LT Distribution Box (SMC) | Electrical work | S-LT Distribution Box (SMC) | As per relevent standard specification | 7797 | EA | 7797
108 | SMR12318 | 1 | S-11KV 200A Tilting Type AB Switch | Electrical work | S-11KV 200A Tilting Type AB Switch | As per relevent standard specification | 8991 | EA | 8991
109 | SWR22092 | 11.5 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 8797.5 | 33KV line
110 | SWR10109 | 30 | Excavation of Pole pits of size.0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") 1.94 cum for 12.5mtrs Spun Poles including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except hard rock requiring blasting. | Earth work | EXCAVATION OF PIT(3.0" x 3.0" x 7.6") | As per relevent standard specification | 842.78 | EA | 25283.4
111 | SWR10107 | 80 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 56000
112 | SWR10112 | 120 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | As per relevent standard specification | 1680 | EA | 201600
113 | SWR10105 | 58 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 34800
114 | SWR10350 | 30 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Spun poles 12.5 Mtrs / 12.9Mtrs PSCC | Earth work | Erection of Spun pole 12.5Mt | As per relevent standard specification | 4115.7 | EA | 123471
115 | SWR10978 | 200 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 833056
116 | SWR10343 | 58 | Erection of 9.1 Mts Sturt pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 139200
117 | SWR10981 | 29 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Horizontal Cut point for 33 KV line | As per relevent standard specification | 1759.5 | EA | 51025.5
118 | SWR10356 | 77.513 | Concreting the location after erection of 11 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.76X0.76X1.83 Mts)* 73 = 77.2 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 509958.027
119 | SWR10356 | 31.32 | Concreting the location after erection of 9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes(0.6X0.6X1.5 Mts)*58 = 31.32 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 206054.28
120 | SWR10356 | 34.5 | Excavation of Pole pits of size 0.75x0.9x1.95 Mts for 12.5mts Spun Poles including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except hard rock requiring blasting.(0.75x0.9x1.95 Mtrs)*24=34.6 Cu.Mt. | Earth work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 226975.5
121 | SWR10366 | 11.5 | Paving of the 100 sqmm AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 12600.06 | KM | 144900.69
122 | SMR11488 | 300 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 35250
123 | SWR11185 | 30 | Sub Transportation of spun pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt any Spun Pole incl. L&UL<10KM | As per relevent standard specification | 771.38 | EA | 23141.4
124 | SWR11180 | 200 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 86394
125 | SWR20308 | 58 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 23622.82
126 | SWR10191 | 11 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 2222
127 | SWR10509 | 11 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 1100
128 | SWR11860 | 11 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 29923.74
129 | SWR10150 | 1.72 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 1061.412
130 | SWR10206 | 1.72 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 380.12
131 | SWR10524 | 1.72 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 318.2
132 | SWR10211 | 69 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 207
133 | SWR10529 | 69 | Unloading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 207
134 | SWR12416 | 11 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 22
135 | SWR10631 | 11 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 22
136 | SWR10618 | 15 | Loading of 33KV Metal parts bag of 25 nos | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 975
137 | SWR10632 | 15 | Unloading of 33 KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 975
138 | SWR10354 | 138 | Erection of 33 kv Stay set complete including fixing of bow ,fixing and binding of Eye bolt, Anchor rod, guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. | Electrical work | Assembly and erection of Stay set 33kv | As per relevent standard specification | 684.53 | SET | 94465.14
139 | SWR21190 | 138 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock,Hard rock Requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 71760
140 | SMR25238 | 30 | Supply of PSCC Spun Pole 12.5Mtr | Electrical work | S-PSCC Spun Pole 12.5Mtr | As per relevent standard specification | 15635.59 | EA | 469067.7
141 | SMR25236 | 200 | Supply of PSCC Pole 11Mtr 365 Kg | Electrical work | S-PSCC Pole 11Mtr 365 Kg | As per relevent standard specification | 5399 | EA | 1079800
142 | SMR25233 | 58 | Supply of PSCC Pole 9.1Mtr 280kg | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 180345.78
143 | SMR25229 | 201 | Supply of 33KV V-Cross Arm without Clamps | Electrical work | S-33KV V-Cross Arm without Clamps | As per relevent standard specification | 1678 | EA | 337278
144 | SMR25228 | 201 | Supply of 33KV M.S.Back Clamps | Electrical work | S-33KV M.S.Back Clamps | As per relevent standard specification | 248 | SET | 49848
145 | SMR25230 | 201 | Supply of 33KV Top Cleat with Clamps | Electrical work | S-33KV Top Cleat with Clamps | As per relevent standard specification | 461 | SET | 92661
146 | SMR25207 | 580 | Supply of MS Angle 65X65X6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 33205
147 | SMR22745 | 1120 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 64344
148 | SMR12321 | 100 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 5642
149 | SMR25231 | 138 | Supply of 33KV MS Stay Set with BasePlate | Electrical work | S-33KV MS Stay Set with BasePlate | As per relevent standard specification | 1035 | SET | 142830
150 | SMR25228 | 254 | Supply of 33KV M.S.Back Clamps | Electrical work | S-33KV M.S.Back Clamps | As per relevent standard specification | 248 | SET | 62992
151 | SMR12315 | 1 | Supply of 33KV 800A DB Break AB Switch | Electrical work | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 40658.78
152 | SWR22092 | 3.7 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 11 kv line. | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | EA | 2830.5 | 11 kv line
153 | SWR10105 | 37 | Excavation of Pole pits of size 2.6"x2.6"x5.0" for 9.1/8.0 mtrs PSCC Poles including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except hard rock requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 22200
154 | SWR10110 | 56 | Excavation of Pole pits of size (2.6" x 2.6" x 5.0') 0.88 cum 0.76 M x 0.76M x 1.52M for 9.1 mtrs PSCC Poles including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD (2.6" x 2.6" x 5.0') | As per relevent standard specification | 1440 | EA | 80640
155 | SWR10343 | 74 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 177600
156 | SWR10342 | 19 | Erection of 8.0 Mts PSCC Poles including fixing of 11 KV X arm and top cleats and fixing of Pin insulators complete with necessary hard ware for tangential locations excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 28500
157 | SWR10653 | 10 | Formation of 11 kv cut points (Vertical/Horizantal) including fixing of 11 KV Cross arms,clamps, strain insulators sets complete with hardware and stays (Bows and Eye-bolts), Excluding the cost of pit Excavation and pole erection. The contractor has to supply GI Bolts and Nuts. | Electrical work | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1350 | EA | 13500
158 | SWR10356 | 7.992 | Concreting the location after erection of 9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.6X0.6X1.5 Mts)* 14.8 = 7.992 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 52579.368
159 | SWR10365 | 3.8 | Paving of the conductor 55 Sqmm AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 3 Cond | As per relevent standard specification | 8500 | KM | 32300
160 | SMR11488 | 80 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 9400
161 | SWR10206 | 0.5 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 110.5
162 | SWR10524 | 0.5 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 92.5
163 | SWR11248 | 12 | Loading 11KV Polymer Pin Insulator- with GI pins | Electrical work | Load-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 12
164 | SWR11249 | 12 | Unloading 11KV Polymer Pin Insulator with GI pins | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 12
165 | SWR10134 | 1.5 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 881.28
166 | SWR11862 | 2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 20 KM and upto 30 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 7382.76
167 | SWR10191 | 1.5 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 303
168 | SWR10509 | 1.5 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 150
169 | SWR20307 | 19 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 5158.88
170 | SWR20308 | 19 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 7738.51
171 | SWR10228 | 65 | Loading of 11 KV V - Cross arms | Electrical work | LOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 260
172 | SWR10546 | 65 | Unloading of 11 KV V - Cross arms | Electrical work | UNLOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 260
173 | SWR12402 | 2 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 96
174 | SWR12421 | 2 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 96
175 | SWR10251 | 65 | Loading of 11 KV Top fittings | Electrical work | LOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 65
176 | SWR10569 | 65 | Unloading of 11 KV Top fittings | Electrical work | UNLOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 65
177 | SWR12416 | 5 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 10
178 | SWR10631 | 5 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 10
179 | SWR10353 | 45 | Erection of 11 kv Stay set complete including fixing of bow, fixing and binding of Eye bolt,Anchor rod,guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Assembly and erection of Stay set11kv&LT | As per relevent standard specification | 606.85 | SET | 27308.25
180 | SWR21190 | 45 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In Hard Gravel and Hard murram not requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 23400
181 | SMR25233 | 74 | Supply of PSCC Pole 9.1Mtr 280kg | Electrical Work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 230096.34
182 | SMR25232 | 19 | Supply of PSCC Pole 8Mtr 140kg | Electrical Work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 30020
183 | SMR25218 | 65 | Supply of 11KV V X-Arms with MS Angle 65x65x6 | Electrical Work | S-11KV V X-Arms with MS Angle 65x65x6 | As per relevent standard specification | 743 | EA | 48295
184 | SMR25213 | 65 | Supply of MS Back Clamps for 9.1 M PSCC Pole | Electrical Work | S-MS Back Clamps for 9.1 M PSCC Pole | As per relevent standard specification | 92 | SET | 5980
185 | SMR25224 | 65 | Supply of 11KV Top Cleat with Clamps | Electrical Work | S-11KV Top Cleat with Clamps | As per relevent standard specification | 178 | SET | 11570
186 | SMR25205 | 200 | Supply of MS Channel 75x40 mm | Electrical Work | S-MS Channel 75x40 mm | As per relevent standard specification | 58.45 | KG | 11690
187 | SMR25206 | 100 | Supply of MS Angle 50x50x6 | Electrical Work | S-MS Angle 50x50x6 | As per relevent standard specification | 58.15 | KG | 5815
188 | SMR12322 | 50 | Supply of MS Flat 50x6mm | Electrical Work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 2825
189 | SMR25225 | 45 | Supply of 11KV MS Stay Sets without BasePlate | Electrical Work | S-11KV MS Stay Sets without BasePlate | As per relevent standard specification | 622 | SET | 27990
190 | SMR25228 | 86 | Supply of 33KV M.S.Back Clamps | Electrical Work | S-33KV M.S.Back Clamps | As per relevent standard specification | 248 | SET | 21328
191 | SWR10392 | 3 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 13500 | DP Str
192 | SWR10105 | 18 | ERECTION OF DP STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1/8.0 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 10800
193 | SWR10342 | 12 | Erection of 8.0 Mts PSCC Poles including fixing of 11 KV X arm and top cleats and fixing of Pin insulators complete with necessary hard ware for tangential locations excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 18000
194 | SWR10343 | 6 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 14400
195 | SWR10356 | 9.72 | Concreting the location after erection of 9.1/8.0 Mtrs pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) ( 0.6x0.6x1.5)mtrs x 18 . | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 63947.88
196 | SMR11488 | 7.5 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 881.25
197 | SWR10206 | 0.885 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 195.585
198 | SWR10524 | 0.9 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 166.5
199 | SWR10134 | 0.9 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 528.768
200 | SWR20307 | 12 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 3258.24
201 | SWR20308 | 6 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 2443.74
202 | SWR12402 | 3 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 144
203 | SWR12421 | 3 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 144
204 | SWR12416 | 3 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 6
205 | SWR10631 | 3 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 6
206 | SMR11482 | 6 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 20916
207 | SWR10357 | 6 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 7405.2
208 | SMR11485 | 20 | Supply of earthing GI Flat 25X3 mm including material | Electrical work | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 2100
209 | SMR12315 | 3 | S-33KV 800A DB Break AB Switch | Electrical work | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 121976.34
210 | SMR25233 | 6 | S-PSCC Pole 9.1Mtr 280kg | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 18656.46
211 | SMR25232 | 12 | S-PSCC Pole 8Mtr 140kg | Electrical work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 18960
212 | SMR25207 | 180 | S-MS Angle 65X65X6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 10305
213 | SMR22745 | 600 | S- MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 34470
214 | SMR12321 | 150 | S-MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 8463
[6 empty] | Total |  |  | 8823791.803
1 | SWR34179 | 12 | Levelling the site with the help of JCB including cost, conveyance of all materials,hire charges etc complete for finished item of work. | JCB | Hire-JCB to Level & Clear the Site | As per relevant standard specifiction | 2164.1 | H | 25969.2
2 | SWR33015 | 106.05 | Earth Work Mass Excavation (Ordinary soil) to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions, labour and material charges etc., complete as directed by the engineer-incharge. | Earth Work | Excavation in Ordinary Soil | As per relevant standard specifiction | 347 | M3 | 36799.35
3 | SWR33028 | 22.06 | PCC (1:4:8) for levelling course using 40mm size hard broken Granite stone including cost and conveyance of all materials, HBG metal for foundations and leveling course and as directed by the Engineer- in - charge etc complete for finished item of work. | Concrete | PCC with 40mm Metal (1:4:8) | As per relevant standard specifiction | 4268 | M3 | 94152.08
4 | SWR33041 | 126.3 | CRS masonry in CM (1:6) using Hard Granite Stones including cost and conveyance of all materials, seignorage charges, labour charge for construction and for dressing stones to required size and shape, dewatering, scaffolding, cutting for all leads and lifts, all incidental charges etc .complete for finished item of work as directed by the Engineer - in - charge. | Masonry | CRS Masonary CM(1:6) 2nd Sort | As per relevant standard specifiction | 4586 | M3 | 579211.8
5 | SWR33068 | 19.4 | Construction of brick masonary in CM(1:6) including cost and conveyance of all materials, labour charges etc. complete for finished item of work | Masonry | Brick Masonary in CM(1:6) GFloor | As per relevant standard specifiction | 7717 | M3 | 149709.8
6 | SWR33052 | 869.93 | Supplying and filling with borrowed gravel, watering, ramming, consolidating thoroughly complying with the standard specification including cost and conveyance of all materials, labour charges,hire charges of machnery,with all leads and incidental charges etc complete for finished item work | Earth Work | S&Filling with Borrowed Gravel | As per relevant standard specifiction | 435 | M3 | 378419.55
7 | SWR33098 | 6.53 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (a) Footings | RCC | RCC Footing: M20Gr, Steel Centering | As per relevant standard specifiction | 8408 | M3 | 54904.24
8 | SWR33100 | 4.77 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (b) Columns | RCC | RCC Column GF: M20Gr, Steel Centering | As per relevant standard specifiction | 11103 | M3 | 52961.31
9 | SWR33099 | 1.65 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (c) Plinth Beams | RCC | RCC Plinth Beam: M20Gr, Steel Centering | As per relevant standard specifiction | 10828 | M3 | 17866.2
10 | SWR33107 | 0.72 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (d) Lintels | RCC | RCC Lintel GF: M20Gr, Steel Centering | As per relevant standard specifiction | 11263 | M3 | 8109.36
11 | SWR33114 | 11.7 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (e) Sunshade | RCC | RCC Sunshade GF: M20Gr, Steel Centering | As per relevant standard specifiction | 1176 | M2 | 13759.2
12 | SWR33121 | 2.35 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (f) Roof Beams | RCC | RCC Roof Beam GF: M20Gr, Steel Centering | As per relevant standard specifiction | 10838 | M3 | 25469.3
13 | SWR33128 | 6.94 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (g) Slab of 130 mm thick | RCC | RCC Roof Slab GF: M20Gr, Steel Centering | As per relevant standard specifiction | 10389 | M3 | 72099.66
14 | SWR33144 | 2.2 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) / Mild steel (MS) steel bars (Fe 415/ Fe 500 grade as per IS 1786-1979) of different diameters for RCC works complete for finished item of work in all floors.( APSS No.126) | Steel | Reinforcement Steel Fe 415/500 | As per relevant standard specifiction | 76127 | TO | 167479.4
15 | SWR33163 | 317.06 | Providing plastering of 20mm thick to all uneven faces of walls and ceiling of superstructure in two coats with base coat in CM 1:6 of 16mm thick and top coat in Cm 1:4 4mm thick with dubara sponge finish | Plastering | Plastering 20mm (16mm+4mm)GFloor | As per relevant standard specifiction | 420 | M2 | 133165.2
16 | SWR33184 | 136.5 | Raised pointing in CM(1:3) including curing, cost and conveyance of all materials and labour charges for complete item of work. | Pointing | Raised Pointing to CRS Masonary CM(1:3) | As per relevant standard specifiction | 96 | M2 | 13104
17 | SWR33156 | 54.87 | Providing impervious coat over RCC roof slab surfaces to requried slopes with 20mm thick in CM 1:3 pro mixed with approvaled brand of water proffing compound as the raet of 1 kg per bag of cement inclding cost and conveyance of all materials | Roof plastering | Impervious Coat 20mm CM(1:3) GFloor | As per relevant standard specifiction | 449 | M2 | 24636.63
18 | SWR33264 | 5.7 | Supply and fixing of Flush type Doors with 35mm Thick Flush Shutters with Bondwood solied Block Board Type Faced on Both the sides with Commercial Type Plywood for finished item work as directed by the Engineer - in- charge. | Doors | S&F MT Wood Frame & Door-Laminate | As per relevant standard specifiction | 6799.02 | M2 | 38754.414
19 | SWR33277 | 5.76 | Supply and Fixing of Aluminium sliding windows with fixed glass panels using aluminium sections 62x32x1.2mm providing 5mm plain glass fixed to frame with beading gasket and glazing clips with all accessories,locking arrangements including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Windows | S&F Aluminium Window | As per relevant standard specifiction | 3381.54 | M2 | 19477.6704
20 | SWR33310 | 6.25 | Supplying and fixing of MS safety grill with peripheral frame of ISA 25x25x4mm and horizontal & vertical 8mm square rods and including cost and coveyance of all mateirals with all leads and lifts, labour charges, painting charges complete for finished item of work | Window grills | S&F of MS Safety Grill | As per relevant standard specifiction | 2539 | M2 | 15868.75
21 | SWR33219 | 26.5 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and approved size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and pointing with cement, labour etc, complete for finished item of work. | Flooring | Polished Shabad Flooring 20mm CM(1:3) | As per relevant standard specifiction | 665 | M2 | 17622.5
22 | SWR33236 | 6.94 | Providing skirting with tandoor blue slabs including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Flooring | Polished Shabad Skirting CM(1:3) | As per relevant standard specifiction | 731 | M2 | 5073.14
23 | SWR33029 | 40.07 | Plain Cement contrete - Nominal Mix (1:3:6) using 40 mm metal with concrete mixture including cost and conveyance of all materials labour charges etc. complete for finished iitem of work and as directed by the engineer-in-charge. | Concrete | PCC with 40mm Metal (1:3:6) | As per relevant standard specifiction | 4570 | M3 | 183119.9
24 | SWR33030 | 6.75 | PCC(1:2:4) using 10 to 12 mm aggregate including cost and conveyance of all materials labour charges etc., complete for finished iitem of work and as directed by the engineer-in-charge. | Concrete | PCC with 20mm Metal (1:2:4) | As per relevant standard specifiction | 5685 | M3 | 38373.75
25 | SWR33057 | 65.92 | Supply and Spreading of 20mm machine crushed metal including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Metal | S&Spreading of 20mm HBG Metal | As per relevant standard specifiction | 1514 | M3 | 99802.88
26 | SWR33403 | 110 | Supply and fixing of fencing of welded wire mesh (1" x 2") of 3mm dia with support channels of 75x 40mm and angles around of 30x30x3 mm including cost and conveyance of all materials, fabrication charges, painting charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Welded mesh | S&F MS Security Fencing Mesh (2"X2") | As per relevant standard specifiction | 2042 | M2 | 224620
27 | SWR33333 | 107.9 | Painting with two coats of OBD over a coat of primer including cost and conveyance of all materials ,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Painting | Painting with OBD 2Coats+Primer | As per relevant standard specifiction | 109.9 | M2 | 11858.21
28 | SWR33336 | 153 | Painting with two coats of ACE paint over a coat of primer including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Painting | Painting SnowCem/Apex 2 Coats+Primer | As per relevant standard specifiction | 195.91 | M2 | 29974.23
29 | SWR33329 | 196.5 | Painting with lovely cem three coats including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Painting | Painting with SuryaCem of 3 Coat | As per relevant standard specifiction | 70.47 | M2 | 13847.355
30 | SWR33442 | 25 | S&F Conceal PVC Pipe 32mm dia in Slab including cost and conveyance of all material and labour charges complete for finished item of work | Electrification | S&F Conceal PVC Pipe 25mm dia in Slab | As per relevant standard specifiction | 85 | RMT | 2125
31 | SWR33441 | 15 | S&F Conceal PVC Pipe 20mm dia in Wall including cost and conveyance of all material and labour charges complete for finished item of work | Electrification | S&F Conceal PVC Pipe 25mm dia in Wall | As per relevant standard specifiction | 89 | RMT | 1335
32 | SWR33457 | 15 | Wiring with 2X1.0 Sqm(14/.3mm) PVC insulated flexiable copper cable in the existing metalic/Non metalic conduit pipe with 6A mini modular SP switch, mounted on metalic box covereds with appropriate front plate modules etc ceiling rose including cot and conveyance of all mateials, labour charges complete for light points, bell points and fan points in non residential builsing except circuit moving finished in all types masonary as directed by department. | Electrification | S&F Modular Switch LP,FP,EFP for NRBuild | As per relevant standard specifiction | 580 | EA | 8700
33 | SWR33461 | 2 | Supply and fixing of 6A 3/2 pin flush type plug socket with 6A flush type marked switch control on a common board with earth continuity including wire leads earth connections along with all labour charges etc. complete | Electrification | S&F Modular 3/2pin 6A Sockets | As per relevant standard specifiction | 469 | EA | 938
34 | SWR33464 | 2 | Supply and fixing of 16A 3pin flush type plug socket and 16A flush type fuse unit and 16A switch control. | Electrification | S&F Modular 3pin 16/6A Sockets | As per relevant standard specifiction | 437 | EA | 874
35 | SWR33484 | 4 | Supply and fixing of slanting holders with 100W bulb with all connections and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F Batten Holder | As per relevant standard specifiction | 116 | EA | 464
36 | SWR33545 | 4 | Supply and fixing of patty type tube light fitting with 4' 0" - 40W tube light,40W copper choke,starter,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F 20W LED Retro Tube Light | As per relevant standard specifiction | 868 | EA | 3472
37 | SWR33494 | 90 | Supply and run of 2 of 14/.3mm(1.00Sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | S&R 2 of 14/0.3mm (1.0sqmm) (FR) | As per relevant standard specifiction | 48 | RMT | 4320
38 | SWR33497 | 30 | Supply and run of 2 of 36/0.3 (2.5sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | S&R 2 of 36/0.3mm (2.5sqmm) (FR) | As per relevant standard specifiction | 95 | RMT | 2850
39 | SWR33520 | 1 | SPN Distribution board with IP-20 protection suitable for single phase 40A DP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 4Nos as out going MCBs in sheet steel enclosure including connections and cost of all material labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F 8wySPNDB IP-20,10kA-6-32A SPMCB 4No | As per relevant standard specifiction | 5038 | EA | 5038
40 | SWR33596 | 1 | Providing independent earthing for main switches,IC cutouts and motors using 40mm. Dia. B-class G.I.Pipe of 2.5' length duly providing 12mm. Dia. 6No. Holes and required bolts,nuts and washers,including filling with equal preparation of salt and charcoal in layers and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | Provd-Independent Earthing | As per relevant standard specifiction | 4891 | EA | 4891
41 | SWR33597 | 15 | Supply and run of No.8 SWG Copper wire including cost of all accessories and labour charges etc., Complete | Electrification | S&R No.8 SWG Copper Wire | As per relevant standard specifiction | 140 | RMT | 2100
42 | SWR33563 | 2 | Supply and Fixing of 48" ceiling fan of bajaj make(or equivalent make) including cost material,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F 1200mm (48'') Sweep Ceiling Fan | As per relevant standard specifiction | 2215 | EA | 4430
43 | SWR33224 | 15.8 | Supply and fixing of ceramic tiles fantacy for dadoing including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Flooring | Ceramic Tile Flooring 20mm CM(1:3) | As per relevant standard specifiction | 765 | M2 | 12087
44 | SWR34311 | 1 | Supply and fixing of 580mm x 440mm long Orissa pan of Parry, Neycer or Hindhusthan, make with 'P' or 'S' trap etc complete for finished item of work and as directed by the engineer-in-charge. | Sanitary | S&F Orissa Pan WC 580mmx440mm | As per relevant standard specifiction | 2178 | EA | 2178
45 | SWR34386 | 2 | Supply and Fixing 4" PVC floor trap including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F Floor Trap (Bell Mouth) 110mm | As per relevant standard specifiction | 269 | EA | 538
46 | SWR34382 | 2 | Supply,fixing 90mm dia. PVC Plain Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F 90mm dia Plain Bend PVC/SWR Pipe | As per relevant standard specifiction | 84 | EA | 168
47 | SWR34385 | 1 | Supply,fixing 90mm dia. PVC Door Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F 75mm dia Door Bend PVC/SWR Pipe | As per relevant standard specifiction | 81 | EA | 81
48 | SWR34286 | 1 | S&Fixing 150mm x 100mm SWG gully traps Ist class grating & constg brick masonry in CM (1:6) prop inter mediate chamber and fitted with CI frame etc complete. | Sanitary | S&F 150mmx100mm SWG Gully Trap | As per relevant standard specifiction | 749 | EA | 749
49 | SWR34377 | 6 | Supply and Fixing 4" dia 3M Single socket PVC pipe including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F 110mm dia 3M 1Socket PVC/SWR Pipe | As per relevant standard specifiction | 422 | RMT | 2532
50 | SWR34453 | 1 | Supply and Fixing 4" dia PVC cowl including labour charges etc. complete for finished item of work. | Plumbing | S&F 4" dia PVC Cowl | As per relevant standard specifiction | 23 | EA | 23
51 | SWR34444 | 1 | Construction of soak pit with 4' dia RCM rings upto a depth of 6' including cost and conveyance of all materials as directed by the engineer-in-charge. | Sanitary | Construct- 4' dia & 5' Ht Soak Pit | As per relevant standard specifiction | 2950 | EA | 2950
52 | SWR34361 | 20 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) 15.90mm OD Pipe - SDR 11 | Plumbing | S&F 15.90mm OD CPVC Pipe-SDR 11 | As per relevant standard specifiction | 239 | RMT | 4780
53 | SWR34362 | 100 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) 22.20mm OD Pipe - SDR 11 | Plumbing | S&F 22.20mm OD CPVC Pipe-SDR 11 | As per relevant standard specifiction | 313 | RMT | 31300
54 | SWR34363 | 100 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) 28.60mm OD Pipe - SDR 11 | Plumbing | S&F 28.60mm OD CPVC Pipe-SDR 11 | As per relevant standard specifiction | 410 | RMT | 41000
55 | SWR34344 | 18 | Supply and fixing of 15mm dia. SS coated taps including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F-15mm GM/Bronze Ball Valve | As per relevant standard specifiction | 230 | EA | 4140
56 | SWR34345 | 1 | Supply and fixing of 20mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F-20mm GM/Bronze Ball Valve | As per relevant standard specifiction | 331 | EA | 331
57 | SWR34346 | 2 | Supply and fixing of 25mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F-25mm GM/Bronze Ball Valve | As per relevant standard specifiction | 466 | EA | 932
58 | SWR34329 | 3 | Supply and fixing of 12.7mm bib tap Indian make including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F-15mm Bib Tap 400gm Full turn | As per relevant standard specifiction | 271 | EA | 813
59 | SWR34375 | 500 | Providing and placing on Terrace polyetheylene water storage tank with double layer approved brand and manufacture with cover complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F Polyethylene Water Storage Tank | As per relevant standard specifiction | 10 | L | 5000
60 | SWR34740 | 1 | Supply of steel table of size 4'x2.5'x30" with 18 mm plywood fixed with rubber beeding with drawers on right side with automatic locking arrangements etc complete for finished item of work and as directed by the engineer-in-charge. | Furniture | S-3x2ft Office Table | As per relevant standard specifiction | 5000 | EA | 5000
61 | SWR33857 | 1 | Supply of 'S' type chair with arms teakwood frame with seat back 's' type on G.I pipe including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Furniture | Supply of S-Type Chair | As per relevant standard specifiction | 3850 | EA | 3850
62 | SWR33858 | 2 | Supply of P V C chairs of Neelkamal of approved quality & make including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Furniture | Supply of PVC Chair | As per relevant standard specifiction | 1150 | EA | 2300
63 | SWR33406 | 150 | S&Fixing of R.C.C fencing poles of size 0.115mx0.115mx2.7m including cost & conveyance of all materials,labour chargesv etc complete for finished item of work. | Fencing | S&F RCC Fencing Pole 0.115mx0.115mx2.7m | As per relevant standard specifiction | 1411 | EA | 211650
64 | SWR33405 | 76 | Providing and fixing 1.80 metre long RCC fencing posts with 6 mm bar bibs of pole size 0.1x0.1x1.8m in pit size of 0.45x0.45x0.45 and filled with PCC (1:4:8) using 20mm metal including cost & conveyance of all materials, labour charges etc complete for finished item of work. | Fencing | S&F RCC Fencing Pole 0.1mx0.1mx1.8m | As per relevant standard specifiction | 1269 | EA | 96444
65 | SWR33407 | 275 | S&Fixing of barbed wire 8 straight strands and 2 cross strands including cost & conveyance of all materials, labour charges etc complete for finished item of work. | Fencing | S&F Barbed Wire 8H & 2Cross | As per relevant standard specifiction | 260.05 | M | 71513.75
66 | SWR33421 | 1.35 | Supply and Fixing of Substation name board of size 5'x3' iron sheet with angle frame and channel supports of size 75x40mm, 8' height including concreting of channel supports and painting with enamel paint complete. | Name board | S&F MS Board | As per relevant standard specifiction | 4542.3 | Sqm | 6132.105
67 | SWR33423 | 1.8 | S&F Poly Vinyl Acrylic Board including cost and conveyance of all labour and material charges complete. | Name board | S&F Poly Vinyl Acrylic Board | As per relevant standard specifiction | 1930.48 | Sqm | 3474.864
68 | SWR33608 | 1 | Geophysical Investgation Charges | Borewell | Geophysical Investgation Charges | As per relevant standard specifiction | 5000 | EA | 5000
69 | SWR33609 | 90 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work. 0 to 90M | Borewell | Drilling-165mm Bore Well 0 to 90M | As per relevant standard specifiction | 336 | M | 30240
70 | SWR34830 | 30 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work. 90m to 120M | Borewell | Drill-165mm Bore Well 90M to 120M | As per relevant standard specifiction | 369 | M | 11070
71 | SWR34831 | 30 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work. 120m to 150M | Borewell | Drill-165mm Bore Well 120M to 150M | As per relevant standard specifiction | 369 | M | 11070
72 | SWR33611 | 30 | Suppy & fixing of 160 mm dia. 6 kg/cm2 PVC casing pipe including cost and conveyance of all materials labour charges etc complete for finished item of work | Borewell | S&F 160mm dia PVC Casing | As per relevant standard specifiction | 844 | M | 25320
73 | SWR33636 | 1 | Supply & fixing of 2HP Multistage submersible motor pumpset of approved make (Texmo or equivalent type) including cost and conveyance of all materials etc complete for finished item of work. | Borewell | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | As per relevant standard specifiction | 34237 | EA | 34237
74 | SWR33641 | 60 | S&R 3C 2.5sqmm Flat Copper Cable including cost of all materials and labour charges for finished item of work. | Borewell | S&R 3C 2.5sqmm Flat Copper Cable | As per relevant standard specifiction | 190 | EA | 11400
75 | SWR33644 | 1 | Supply and fixing of Panel box and starter including cost of all materials and labour charges for finished item of work. | Borewell | S&E D.O.L Starter 250V Single Phase | As per relevant standard specifiction | 1040 | EA | 1040
76 | SWR34203 | 1 | Supply & fixing of Flange Clamps including cost of all materials and labour charges for finished item of work. | Borewell | Supply & ixing of Flange Clamps | As per relevant standard specifiction | 182 | EA | 182
77 | SWR34410 | 178 | Suppy & fixing of HDPE pipe 1.5" dia. including cost & conveyance of all materials labour charges etc complete for finished item of work. | Borewell | S&F-HDPE Pipe 40mm dia 16kg/sqcm-SDR 9 | As per relevant standard specifiction | 160 | Rmt | 28480
78 | SWR34470 | 98.8 | Seigniorage Charges - Sand | Seigniorages | Seigniorage Charges - Sand | As per relevant standard specifiction | 40 | M3 | 3952
79 | SWR34471 | 96.5 | Seigniorage Charges - Metal | Seigniorages | Seigniorage Charges - Metal | As per relevant standard specifiction | 97.5 | M3 | 9408.75
80 | SWR34472 | 869.93 | Seigniorage Charges - Gravel | Seigniorages | Seigniorage Charges - Gravel | As per relevant standard specifiction | 30 | M3 | 26097.9
[7 empty] | Civil |  | 3295210.4484
[7 empty] | Elec & Civil total |  | 12119002.2514

## 4. Gopanpally SS
Gopanpally SS Schedules
Name of the work: Estimate for erection of new 33/11 KV SS with connected 33 KV and 11 KV lines at Gopanpally (V) in Mogudampally (M) of Zaheerabad Division of Sangareddy Circle (WBS No: S-1742-90-06-03-01-002)
S.No | SRR Codes | Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR22092 | 3 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 2295
2 | SWR10105 | 15 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 9000
3 | SWR10343 | 15 | Erection of 9.1 Mts Sturt pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 36000
4 | SWR10107 | 60 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 42000
5 | SWR10978 | 60 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 249916.8
6 | SWR10981 | 10 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Horizontal Cut point for 33 KV line | As per relevent standard specification | 1759.5 | EA | 17595
7 | SWR10356 | 21.14 | Concreting the location after erection of 11 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.76X0.76X1.83 Mts)* 20 = 21.14 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 139080.06
8 | SWR10356 | 8.1 | Concreting the location after erection of 9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.6X0.6X1.5 Mts)* 15 = 8.1 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 53289.9
9 | SWR10356 | 9 | Concreting the location after erection of 9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.45X0.45X1.265 Mts)* 36 = 9 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 59211
10 | SWR10366 | 3 | Paving of the 100 sqmm AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 12600.06 | KM | 37800.18
11 | SMR11488 | 80 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 9400
12 | SWR11180 | 60 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 25918.2
13 | SWR20308 | 15 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 6109.35
14 | SWR10191 | 3 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 606
15 | SWR10509 | 3 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 300
16 | SWR11860 | 3 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 8161.02
17 | SWR10150 | 0.6 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 370.26
18 | SWR10206 | 0.6 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 132.6
19 | SWR10524 | 0.6 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 111
20 | SWR10211 | 8 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 24
21 | SWR10529 | 8 | Unloading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 24
22 | SWR12416 | 6 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 12
23 | SWR10631 | 6 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 12
24 | SWR10618 | 2 | Loading of 33KV Metal parts bag of 25 nos | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 130
25 | SWR10632 | 2 | Unloading of 33 KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 130
26 | SWR10354 | 36 | Erection of 33 kv Stay set complete including fixing of bow ,fixing and binding of Eye bolt, Anchor rod, guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. | Electrical work | Assembly and erection of Stay set 33kv | As per relevent standard specification | 684.53 | SET | 24643.08
27 | SWR21190 | 36 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In Hard Gravel and Hard murram not requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 18720
28 | SMR25236 | 60 | Supply of PSCC Pole 11Mtr 365 Kg | Electrical work | S-PSCC Pole 11Mtr 365 Kg | As per relevent standard specification | 5399 | EA | 323940
29 | SMR25233 | 15 | Supply of PSCC Pole 9.1Mtr 280kg | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 46641.15
30 | SMR25229 | 53 | Supply of 33KV V-Cross Arm without Clamps | Electrical work | S-33KV V-Cross Arm without Clamps | As per relevent standard specification | 1678 | EA | 88934
31 | SMR25228 | 53 | Supply of 33KV M.S.Back Clamps | Electrical work | S-33KV M.S.Back Clamps | As per relevent standard specification | 248 | SET | 13144
32 | SMR25230 | 53 | Supply of 33KV Top Cleat with Clamps | Electrical work | S-33KV Top Cleat with Clamps | As per relevent standard specification | 461 | SET | 24433
33 | SMR25207 | 100 | Supply of MS Angle 65X65X6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 5725
34 | SMR22745 | 400 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 22980
35 | SMR12321 | 100 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 5642
36 | SMR25231 | 36 | Supply of 33KV MS Stay Set with BasePlate | Electrical work | S-33KV MS Stay Set with BasePlate | As per relevent standard specification | 1035 | SET | 37260
37 | SMR25228 | 66 | Supply of 33KV M.S.Back Clamps | Electrical work | S-33KV M.S.Back Clamps | As per relevent standard specification | 248 | SET | 16368
38 | SWR22092 | 1.8 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 11 kv line. | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 1377
39 | SWR10105 | 47 | Excavation of Pole pits of size 0.76x0.76x1.52 Mts' for 9.1/8.0 mts PSCC Poles including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts. In all soils except hard rock requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 28200
40 | SWR10343 | 36 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 86400
41 | SWR10342 | 11 | Erection of 8.0 Mts PSCC Poles including fixing of 11 KV X arm and top cleats and fixing of Pin insulators complete with necessary hard ware for tangential locations excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 16500
42 | SWR10653 | 5 | Formation of 11 kv cut points (Vertical/Horizantal) including fixing of 11 KV Cross arms,clamps, strain insulators sets complete with hardware and stays (Bows and Eye-bolts), Excluding the cost of pit Excavation and pole erection. The contractor has to supply GI Bolts and Nuts. | Electrical work | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1350 | EA | 6750
43 | SWR10356 | 5.07 | Concreting the location after erection of 9.1/8 .0 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.6X0.6X1.5 Mts)* 9.4 = 5.07 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 33355.53
44 | SWR10365 | 1.8 | Paving of the conductor 55 Sqmm AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 3 Cond | As per relevent standard specification | 8500 | KM | 15300
45 | SMR11488 | 50 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 5875
46 | SWR10206 | 0.2 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 44.2
47 | SWR10524 | 0.2 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 37
48 | SWR11248 | 108 | Loading 11KV Polymer Pin Insulator- with GI pins | Electrical work | Load-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 108
49 | SWR11249 | 108 | Unloading 11KV Polymer Pin Insulator with GI pins | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 108
50 | SWR10134 | 1 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 587.52
51 | SWR11862 | 1 | Transport of VCB , Control pannels, current transformater, bosster etc, above 20 KM and upto 30 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 3691.38
52 | SWR10191 | 2 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 404
53 | SWR10509 | 2 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 200
54 | SWR20307 | 11 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 2986.72
55 | SWR20308 | 36 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 14662.44
56 | SWR10228 | 31 | Loading of 11 KV V - Cross arms | Electrical work | LOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 124
57 | SWR10546 | 31 | Unloading of 11 KV V - Cross arms | Electrical work | UNLOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 124
58 | SWR12402 | 2 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 96
59 | SWR12421 | 2 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 96
60 | SWR10251 | 31 | Loading of 11 KV Top fittings | Electrical work | LOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 31
61 | SWR10569 | 31 | Unloading of 11 KV Top fittings | Electrical work | UNLOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 31
62 | SWR12416 | 1 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 2
63 | SWR10631 | 1 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 2
64 | SWR10353 | 22 | Erection of 11 kv Stay set complete including fixing of bow, fixing and binding of Eye bolt,Anchor rod,guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Assembly and erection of Stay set11kv&LT | As per relevent standard specification | 606.85 | SET | 13350.7
65 | SWR21190 | 22 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In Hard Gravel and Hard murram not requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 11440
66 | SMR25233 | 36 | Supply of PSCC Pole 9.1Mtr 280kg | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 111938.76
67 | SMR25232 | 11 | Supply of PSCC Pole 8Mtr 140kg | Electrical work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 17380
68 | SMR25218 | 32 | Supply of 11KV V X-Arms with MS Angle 65x65x6 | Electrical work | S-11KV V X-Arms with MS Angle 65x65x6 | As per relevent standard specification | 743 | EA | 23776
69 | SMR25213 | 32 | Supply of MS Back Clamps for 9.1 M PSCC Pole | Electrical work | S-MS Back Clamps for 9.1 M PSCC Pole | As per relevent standard specification | 92 | SET | 2944
70 | SMR25224 | 32 | Supply of 11KV Top Cleat with Clamps | Electrical work | S-11KV Top Cleat with Clamps | As per relevent standard specification | 178 | SET | 5696
71 | SMR25205 | 100 | Supply of MS Channel 75x40 mm | Electrical work | S-MS Channel 75x40 mm | As per relevent standard specification | 58.45 | KG | 5845
72 | SMR25206 | 50 | Supply of MS Angle 50x50x6 | Electrical work | S-MS Angle 50x50x6 | As per relevent standard specification | 58.15 | KG | 2907.5
73 | SMR12322 | 50 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 2825
74 | SMR25225 | 22 | Supply of 11KV MS Stay Sets without BasePlate | Electrical work | S-11KV MS Stay Sets without BasePlate | As per relevent standard specification | 622 | SET | 13684
75 | SMR25228 | 40 | Supply of 33KV M.S.Back Clamps | Electrical work | S-33KV M.S.Back Clamps | As per relevent standard specification | 248 | SET | 9920
76 | SWR10392 | 1 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 4500
77 | SWR10105 | 6 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 3600
78 | SWR10342 | 4 | Erection of 8.0 Mts PSCC Poles including fixing of 11 KV X arm and top cleats and fixing of Pin insulators complete with necessary hard ware for tangential locations excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 6000
79 | SWR10343 | 2 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 4800
80 | SWR10356 | 3.24 | Concreting the location after erection of 9.1/8.0 Mtrs pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) ( 0.6x0.6x1.5)mtrs x 6=3.24 Cu.Mt . | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 21315.96
81 | SMR11488 | 2.5 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 293.75
82 | SWR10206 | 0.3 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 66.3
83 | SWR10524 | 0.3 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 55.5
84 | SWR10134 | 0.3 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 176.256
85 | SWR20307 | 4 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 1086.08
86 | SWR20308 | 2 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 814.58
87 | SWR12402 | 1 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 48
88 | SWR12421 | 1 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 48
89 | SWR12416 | 1 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 2
90 | SWR10631 | 1 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 2
91 | SMR11482 | 2 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 6972
92 | SWR10357 | 2 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 2468.4
93 | SMR11485 | 20 | Supply of earthing GI Flat 25X3 mm including material | Electrical work | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 2100
94 | SMR12315 | 1 | Supply of 33KV 800A DB Break AB Switch | Electrical work | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 40658.78
95 | SMR25233 | 2 | Supply of PSCC Pole 9.1Mtr 280kg | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 6218.82
96 | SMR25232 | 4 | Supply of PSCC Pole 8Mtr 140kg | Electrical work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 6320
97 | SMR25207 | 60 | Supply of MS Angle 65X65X6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 3435
98 | SMR22745 | 200 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 11490
99 | SMR12321 | 50 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 2821
100 | SWR10105 | 39 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1/8.0 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 23400
101 | SWR10343 | 31 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 74400
102 | SWR10356 | 27.19 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt)*31 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 178883.01
103 | SWR11890 | 0.96 | ERECTION OF S.S. STRUCTURE: Coping of 0.45x0.45x0.45Mt with 1:8 slope Using form boxes (0.031Cumt.) | Civil work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | M3 | 3737.28
104 | SWR11331 | 31 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of poles with two coats of white cement (including cost of paint). | Electrical work | Paint-9.1M PSCC Poles as desc SSR | As per relevent standard specification | 485 | EA | 15035
105 | SWR11889 | 5.5 | Fabrication of 100 X 50mm MS Channel for formation of 11kV and 33kV bays: Fabrication and erection of M.S,Channel 100x50mm for forming of 33KV & 11 KV Bays as per standard specifications to facilitate stringing of bus, erection of LA sets, AB Switches bolts & Nuts etc. including painting with one coats of red oxide and two coats of Aluminium paint. GI bolts&nuts shall be used. | Electrical work | Fabr & Erect-MS Chnl 100x50mm for SS Bay | As per relevent standard specification | 6600 | TO | 36300
106 | SWR10404 | 118.5 | Erection of 33kV and 11kV Strung Bus with Panther (200Sqmm) ACSR Conductor: Erection of 33kV and 11kV Bus over the Substation structures with 200sqmm Panther ACSR conductor and giving Jumpers to connect the Switch gear by providing the suitable T clamps and round clamps suitable to Post type insulators & Insulators. | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 38830.08
107 | SWR10392 | 2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 9000
108 | SWR10393 | 7 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 22400
109 | SWR11742 | 3 | Supply & erection of 11 kV 400 A convential single(1/3) phasing AB switches.includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | S&E-400A 11KV ABSwth Conv 1ph(1/3) in SS | As per relevent standard specification | 4232 | EA | 12696
110 | SWR21240 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt). | Electrical work | Hoisting post ins&hrd wr 1panther 33kv | As per relevent standard specification | 781 | EA | 1562
111 | SWR21241 | 4 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 11kv | As per relevent standard specification | 507 | EA | 2028
112 | SWR10881 | 12 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 1704
113 | SWR23224 | 16.46 | Excavation of pit in all types of soils of size 2.2x2.2x0.85Mts.for Construction of Plinths for VCB (33KV & 11 KV ) | Earth work | Excavate-Pit for 33KV VCB | As per relevent standard specification | 331 | M3 | 5448.26
114 | SWR20685 | 22.264 | Providing of Base concreting (2.2x2.2x0.15 Mts) with 1:3:6 Concrete mix. Using form boxes, Providing of Concreting (2x2x1.0mts) with 1:3:6 Cocrete mix. Plastering of the plinth for smooth finishing with 12mm thick 1:3 cement motor and providing two coats white washing for part of the plinth above groung level. | Civil work | Cement concrete with 40MM metal VCB plin | As per relevent standard specification | 5160 | M3 | 114882.24
115 | SWR10461 | 4 | Erection of Switchgear complete for 11 kV VCB includes Assembling the VCB Structures and mounting the VCBs over the already erected foudation including wiring of Breaker Control Panel/CTs, erection of CTs and control pannel providing Jumpers. | Electrical work | Erection of 11kv VCB | As per relevent standard specification | 12000 | EA | 48000
116 | SWR10396 | 2 | Erection of 33KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 1760
117 | SWR10397 | 1 | Erection of 11 KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 11kv LA stn type incl earthing | As per relevent standard specification | 559 | SET | 559
118 | SWR10398 | 3 | Erection of 11 KV Lightening Arrestors line type complete including jumpering. | Electrical work | Erect of 11kvLA line type incl earthing | As per relevent standard specification | 505 | SET | 1515
119 | SMR11607 | 1 | Supply of 33kv HG fuse set including providing of jumpers | Electrical work | S-33KV HG Fuse Set excl Ins & Chnl | As per relevent standard specification | 6431 | SET | 6431
120 | SWR10394 | 1 | Erection of 33kv HG fuse set including providing of jumpers | Electrical work | Erect. of 33kv HG Fuseset incl earthing | As per relevent standard specification | 1331.81 | SET | 1331.81
121 | SMR11608 | 1 | Supply of 11kv HG fuse set including providing of jumpers | Electrical work | S-11KV HG Fuse Set | As per relevent standard specification | 1733.75 | SET | 1733.75
122 | SWR10395 | 1 | Erection of 11kv HG fuse set including providing of jumpers | Electrical work | Erect. of 11kv HG Fuseset incl earthing | As per relevent standard specification | 740.52 | SET | 740.52
123 | SMR11482 | 23 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 80178
124 | SWR10357 | 23 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 28386.6
125 | SWR10920 | 500 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification.75x8 mm MS flat for Earth mat and connecting to electrodes. | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 32500
126 | SWR10919 | 500 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification. 50x6 mm MS flat for raisers, double flat shall be run for structure poles raisers & equipment earthing. | Electrical work | Earthing for raisers of SS Flat 50x6 mm. | As per relevent standard specification | 41 | RMT | 20500
127 | SMR40033 | 2 | Providing of double earthing for neutral with flexible copper jumpers of adequate size including arrangement by fixing M.S.Channel 100x50mm. | Electrical work | SupCU Flexi jumper for Power T/F Neutral | As per relevent standard specification | 4725 | EA | 9450
128 | SWR11771 | 4 | Erection of 24 Volts Battery along with Charger on the VCB plinth and giving DC supply to VCB's. | Electrical work | Erect-24V Batery with Chrgr incl grot-SS | As per relevent standard specification | 1050 | EA | 4200
129 | SWR11474 | 700 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable includes excavation of earth and back filling with sand and earth in alternate layers . The cable termination shall be made by providing proper size lugs and shall be identified with colours. | Electrical work | Laying-4 core cable | As per relevent standard specification | 15 | RMT | 10500
130 | SWR10463 | 1 | Erection of 25 kVA Three phase Station Transformer on the Substation Structures and giving jumpers/connections on HT side to the 11kV bus. Belting angle shall be provided both sides of DTR for securing DTR firmly in position. | Electrical work | Erection of Three Phase DTRs | As per relevent standard specification | 1139.95 | EA | 1139.95
131 | SMR40045 | 1 | Supply of AC Panel Board includes: Fixing of 1 No.100A, MCCB, 10kA capacity of any standard make including material cost. Fixing of suitable panel box 3x3x1 with M.S.Sheet of 16 SWG with front door compartments inclusive of material cost & powder coating (with C Channel ). Fabrication of panel Fixing of 96x96mm analog voltmeter with VSS switch Fixing of 20A HRC fuse Fixing of 3 phase supply indicator kwith HRC fuses Supply and fixing of 6 Sqmm copper flexible wire (PVC) Fixing of Stud type TBs for outgoing feeder Fixing of Epoxy bus supports. | Electrical work | Supply of AC Supply panel complete | As per relevent standard specification | 42000 | EA | 42000
132 | SMR40044 | 1 | Supply of DC Panel Board Fixing of suitable panel box of size 6'x6'x1' with M S sheet of 16 SWG with back doors (4'x6') and on front side with provision to fix up bakelite hylam sheet size of 4'x6' including cost of the panel with powder coating. Fixing of best quality of angles for panel. Fixing of C Channelfor panel. Fabrication of control panel including making suitable holes and board Fixing of Stud type TBs for outgoing feeder Fixing of 24V DC pilot lamps of standard make Fixing of healthy trip push buttons with LED lamp Fixing of plain switches for alarm acceptance and for PTR signal Fixing of ON/OFF push buttons Fixing of digital volt meter for 11kV Fixing of VSS of standard make, Fixing of Engraved AL plates for Alarm panel of various VCB Laying of 2.5Sqmm copper flexible wire for internal wiring . Fixing of digital frequency meter Fixing of Copper lugs and ferrules for internal wiring. Fixing of 4" Gang bells 24V DC Fixing of flow diagram with rading strip Fixing of HRC fuse units | Electrical work | Supply of DC Anunc.relay panel 8 feeders | As per relevent standard specification | 42500 | EA | 42500
133 | SWR20025 | 1 | fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supplied by tenderer. | Electrical work | 33/11kv S.S Erection of AC&DC Panel | As per relevent standard specification | 7871.85 | SET | 7871.85
134 | SWR10342 | 8 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 12000
135 | SWR10356 | 4.368 | Concreting the location after erection of 8.0 Mtrs pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) ( 0.6x0.6x1.5)mtrs x 8 . | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 28737.072
136 | SWR10956 | 8 | Fixing of Metal halide/LED lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5M GI pipe complete. | Electrical work | Fixing of LED/Metal halide complete. | As per relevent standard specification | 1268 | EA | 10144
137 | SWR20028 | 8 | Supply and Fixing of junction box and Providing with proper Fuse protection and required glauds suitable for Cable Terminations. The box shall be fixed on the pole. | Electrical work | 33/11kv S.S Yard lighting junction box | As per relevent standard specification | 351.9 | EA | 2815.2
138 | SWR20526 | 2 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply & fixing of marshall box | As per relevent standard specification | 3085.5 | EA | 6171
139 | SMR40088 | 1 | Supply and fixing of filled sand bucket set complete (4 Nos. Buckets) with stand to mount fire buckets. | Electrical work | Sup Fire Buckets Stand with Buckets | As per relevent standard specification | 1386 | SET | 1386
140 | SMR40087 | 2 | Supply and fixing of CO2 Cylinder set as per IS2878 Specifications. | Electrical work | Sup TrollyMounted Co2 Cylinders(IS-2878) | As per relevent standard specification | 9240 | EA | 18480
141 | SWR11895 | 1 | Supplying and fixing of feeder indicator board to each of the 3Nos feeder breakers and LV breaker, danger boards made of 1'x1' and properly mounted on the structures. The letters written on the borad shall be 1.5"size with blue colour and background shall be of white colour | Electrical work | S&F-33/11KV SS Feeder Indicator Board | As per relevent standard specification | 551 | SET | 551
142 | SWR20032 | 1 | Supply and fixing of wooden board of size 3'x2'.5'indicating the layout of the Switch yard. | Electrical work | Sup &fix of board ind Switchyard layout | As per relevent standard specification | 1654 | EA | 1654
143 | SMR40086 | 1 | Supply and Erection of Permanent Name Board of on 3'x4' steel sheetmounted on steel frame as described in Specification. | Electrical work | Sup 33/11kv S.S Permanent name board | As per relevent standard specification | 10238 | EA | 10238
144 | SMR40076 | 1 | Supply of Digital clamp meter. | Electrical work | Supply of Digital clamp meter. | As per relevent standard specification | 2888 | EA | 2888
145 | SMR40064 | 1 | Supply of Rechargeable LED torch light of Standard make. | Electrical work | Sup Rechargeable LED torch light. | As per relevent standard specification | 1733 | EA | 1733
146 | SMR40063 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box containing ‘D’Spanners from size 6 to 54, Hammer small and big size, Ring spanners from 6 to 28, Adjustable spanner, Pipe wrench, Cutting Plier, Nose plier, Tester, insulated Screw drive. | Electrical work | SupTaparia Tool kit complete as per Spec | As per relevent standard specification | 4925 | SET | 4925
147 | SWR22090 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Electrical work | Sup& fix safety inst/SS Op. inst board | As per relevent standard specification | 2205 | EA | 2205
148 | SMR11598 | 8 | Supply of 25 W LED lamp with fitting of philips make | Electrical work | S-25W LED fixture set | As per relevent standard specification | 3200 | EA | 25600
149 | SMR12378 | 1 | Supply of Alluminum Ladder(20 feet) | Electrical work | S-10ft Aluminium Ladder | As per relevent standard specification | 1654 | EA | 1654
150 | SMR40075 | 1 | Supply of Megger (2000 ohms, 0-2.5kv) | Electrical work | Supply of Earth megger (1000v) | As per relevent standard specification | 8085 | EA | 8085
151 | SMR11599 | 4 | Supply of Earth Discharging Rod 8 feet length, 3 mm thickness. | Electrical work | S-Earth Rod 8ft Long 3mm Thick | As per relevent standard specification | 1000 | EA | 4000
152 | SMR11488 | 200 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 23500
153 | SMR11591 | 66 | Supply of PG clamps for panther 2 bolted 800 A. | Electrical work | S-Al. alloy three bolted PG clamps 800A | As per relevent standard specification | 130 | EA | 8580
154 | SWR20029 | 200 | Supply and Laying of 2 core/4 core cable includes excavation earth and back filling with sand and earth in alternate layers as shown in the sketch. The cable termination shall be made by providing proper size of lugs at both ends of the cable termination. | Electrical work | 33/11kv S.S laying of 2/4core for light | As per relevent standard specification | 50 | M | 10000
155 | SWR20308 | 31 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 12625.99
156 | SWR20307 | 8 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 2172.16
157 | SWR11860 | 4 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 10881.36
158 | SWR10150 | 10.61 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 6547.431
159 | SWR10206 | 10.61 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 2344.81
160 | SWR10524 | 10.61 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 1962.85
161 | SWR11220 | 350 | Loading and unwinding of Panther conductor. | Electrical work | Load-Unwinding Panther conductor | As per relevent standard specification | 3 | M | 1050
162 | SWR11221 | 350 | Unloading of Panther conductor. | Electrical work | Unload-Unwinding Panther conductor | As per relevent standard specification | 2 | M | 700
163 | SWR12416 | 1 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 2
164 | SWR10631 | 1 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 2
165 | SWR10618 | 1 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 65
166 | SWR10632 | 1 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 65
167 | SWR10212 | 1 | Loading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | LOADING of 11kv Pin/Post/Solid Core Insu | As per relevent standard specification | 1 | CRT | 1
168 | SWR10530 | 1 | Unloading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | UNLOADING of 11kv Pin/Post/Solid Core In | As per relevent standard specification | 1 | CRT | 1
169 | SWR11701 | 700 | Loading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | Load-PVC Control Cable 10C | As per relevent standard specification | 1 | M | 700
170 | SWR11712 | 700 | Unloading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | UnLoad-PVC Control Cable 10C | As per relevent standard specification | 1.02 | M | 714
171 | SWR11691 | 1 | Loading of 3Ph 25KVA Distribution Transformer. | Electrical work | Load-3Ph 25KVA DTR | As per relevent standard specification | 252 | EA | 252
172 | SWR11692 | 1 | UnLoading of 3Ph 25KVA Distribution Transformer. | Electrical work | UnLoad-3Ph 25KVA DTR | As per relevent standard specification | 202 | EA | 202
173 | SWR10200 | 1 | Loading of 33/11 KV Current Transformers/ Potential Transformers. | Electrical work | LOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 165 | EA | 165
174 | SWR10266 | 6 | Loading of 33 KV10 KA LAs Station type. | Electrical work | LOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 41 | EA | 246
175 | SWR10584 | 6 | Unloading of 33 KV10 KA LAs Station type. | Electrical work | UNLOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 35 | EA | 210
176 | SWR10265 | 9 | Loading of 11 KV10 KA LAs Line type. | Electrical work | LOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 288
177 | SWR10583 | 9 | Unloading of 11 KV10 KA LAs Line type. | Electrical work | UNLOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 288
178 | SWR10264 | 3 | Loading of 11 KV10 KA LAs Station type. | Electrical work | LOADING of 11 KV,10 KA LAs Station type | As per relevent standard specification | 32 | EA | 96
179 | SWR10582 | 3 | Unloading of 11 KV10 KA LAs Station type. | Electrical work | UNLOADING of 11 KV,10 KA LAs Station typ | As per relevent standard specification | 32 | EA | 96
180 | SWR10239 | 2 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 252
181 | SWR10557 | 2 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 158
182 | SWR10238 | 8 | loading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 640
183 | SWR10556 | 8 | Unloading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 640
184 | SWR11224 | 4 | Loading and Unloading of 12V/24V Battery Set. | Electrical work | Load/Unload-12V/24V Battery Set | As per relevent standard specification | 23 | EA | 92
185 | SWR10356 | 2.66 | ERECTION OF S.S. STRUCTURE: Providing of base concreting of size 0.76x0.76x0.15M with CC mix of ratio 1:3:6 Using form boxes(0.087Cu.Mt)x31 with 20mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 17500.14
186 | SWR10402 | 1 | Erection of 11kv Potential Transformer sets complete including jumpering. The LV side of the PT shall be provided with proper fuse protection mounted in separate marshalling boxwith proper size cable glands etc. The box shall be mounted on the Substation structure. | Electrical work | Erection of 11kv three phase PT s | As per relevent standard specification | 800 | SET | 800
187 | SWR10518 | 1 | Unloading of 33/11 KV Current Transformers/ Potential Transformers | Electrical work | UNLOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 128 | EA | 128
188 | SWR10674 | 1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
189 | SWR10356 | 4.32 | Concreting the location after erection of 8.0 Mtrs pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) ( 0.6x0.6x1.5)mtrs x 8 . | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 28421.28
190 | SWR21750 | 1 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply and fixing of PT Marshalling box | As per relevent standard specification | 1139.85 | EA | 1139.85
191 | SMR40067 | 2 | Supply of Hand Gloves | Electrical work | Supply of Hand Gloves | As per relevent standard specification | 289 | SET | 578
192 | SMR40071 | 2 | Supply of Safety Helmets of standard make | Electrical work | Supply of Safety Helmet of standard make | As per relevent standard specification | 231 | EA | 462
193 | SMR40009 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for First coat of 1st GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 11995.5
194 | SWR10877 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 1st coat of Aluminium | Electrical work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 4680.5
195 | SWR20904 | 20 | Supply & Providing of Panther T clamps |  | Supply & Providing of Panther T clamps. | As per relevent standard specification | 320 | EA | 6400
196 | SMR40010 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for second coat of 2nd GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 7111.5
197 | SWR10879 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 2nd coat of Aluminium | Electrical work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 2651
198 | SMR25233 | 8 | Supply of PSCC Pole 9.1Mtr 280kg | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 24875.28
199 | SMR25232 | 31 | Supply of PSCC Pole 8Mtr 140kg | Electrical work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 48980
200 | SMR12315 | 2 | Supply of 33KV 800A DB Break AB Switch | Electrical work | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 81317.56
201 | SMR12316 | 1 | Supply of 11KV 800A DB Break AB Switch | Electrical work | S-11KV 800A DB Break AB Switch | As per relevent standard specification | 30847.46 | EA | 30847.46
202 | SMR25211 | 6 | Supply of 11KV 400A Conv ABSwitch with Insulator | Electrical work | S-11KV 400A Conv ABSwitch with Insulator | As per relevent standard specification | 11754 | EA | 70524
203 | SMR22745 | 5500 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 315975
204 | SMR12321 | 2350 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 132587
205 | SMR12322 | 2760 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 155940
206 | SMR25200 | 1 | Supply of LT Distribution Box (SMC) | Electrical work | S-LT Distribution Box (SMC) | As per relevent standard specification | 7797 | EA | 7797
207 | SMR12318 | 1 | Supply of 11KV 200A Tilting Type AB Switch | Electrical work | S-11KV 200A Tilting Type AB Switch | As per relevent standard specification | 8991 | EA | 8991
[6 empty] | Total |  |  | 3961856.739
1 | SWR34179 | 60 | Hiring of JCB for leveling of ground including cost & conveyance of all etc complete for finished item of work | JCB | Hire-JCB to Level & Clear the Site | As per relevant standard specifiction | 2164.1 | H | 129846
2 | SWR33015 | 106.05 | Earth Work Mass Excavation (Ordinary soil) to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions, labour and material charges etc., complete as directed by the engineer-incharge. | Earth Work | Excavation in Ordinary Soil | As per relevant standard specifiction | 347 | M3 | 36799.35
3 | SWR33028 | 22.06 | PCC (1:4:8) for levelling course using 40mm size hard broken Granite stone including cost and conveyance of all materials, HBG metal for foundations and leveling course and as directed by the Engineer- in - charge etc complete for finished item of work. | Concrete | PCC with 40mm Metal (1:4:8) | As per relevant standard specifiction | 4240 | M3 | 93534.4
4 | SWR33041 | 112.8 | CRS masonry in CM (1:6) using Hard Granite Stones including cost and conveyance of all materials, seignorage charges, labour charge for construction and for dressing stones to required size and shape, dewatering, scaffolding, cutting for all leads and lifts, all incidental charges etc .complete for finished item of work as directed by the Engineer - in - charge. | Masonry | CRS Masonary CM(1:6) 2nd Sort | As per relevant standard specifiction | 4566 | M3 | 515044.8
5 | SWR33068 | 19.4 | Construction of brick masonary in CM(1:6) including cost and conveyance of all materials, labour charges etc. complete for finished item of work | Masonry | Brick Masonary in CM(1:6) GFloor | As per relevant standard specifiction | 7704 | M3 | 149457.6
6 | SWR33052 | 826.01 | Supplying and filling with borrowed gravel, watering, ramming, consolidating thoroughly complying with the standard specification including cost and conveyance of all materials, labour charges,hire charges of machnery,with all leads and incidental charges etc complete for finished item work | Earth Work | S&Filling with Borrowed Gravel | As per relevant standard specifiction | 435 | M3 | 359314.35
7 | SWR33098 | 6.53 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (a) Footings | RCC | RCC Footing: M20Gr, Steel Centering | As per relevant standard specifiction | 8379 | M3 | 54714.87
8 | SWR33100 | 4.77 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (b) Columns | RCC | RCC Column GF: M20Gr, Steel Centering | As per relevant standard specifiction | 11074 | M3 | 52822.98
9 | SWR33099 | 1.65 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (c) Plinth Beams | RCC | RCC Plinth Beam: M20Gr, Steel Centering | As per relevant standard specifiction | 10799 | M3 | 17818.35
10 | SWR33107 | 0.72 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (d) Lintels | RCC | RCC Lintel GF: M20Gr, Steel Centering | As per relevant standard specifiction | 11234 | M3 | 8088.48
11 | SWR33114 | 11.7 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (e) Sunshade | RCC | RCC Sunshade GF: M20Gr, Steel Centering | As per relevant standard specifiction | 1174 | M2 | 13735.8
12 | SWR33121 | 2.35 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (f) Roof Beams | RCC | RCC Roof Beam GF: M20Gr, Steel Centering | As per relevant standard specifiction | 10809 | M3 | 25401.15
13 | SWR33128 | 6.94 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (g) Slab of 130 mm thick | RCC | RCC Roof Slab GF: M20Gr, Steel Centering | As per relevant standard specifiction | 10360 | M3 | 71898.4
14 | SWR33144 | 2.2 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) / Mild steel (MS) steel bars (Fe 415/ Fe 500 grade as per IS 1786-1979) of different diameters for RCC works complete for finished item of work in all floors.( APSS No.126) | Steel | Reinforcement Steel Fe 415/500 | As per relevant standard specifiction | 76127 | TO | 167479.4
15 | SWR33163 | 317.06 | Providing plastering of 20mm thick to all uneven faces of walls and ceiling of superstructure in two coats with base coat in CM 1:6 of 16mm thick and top coat in Cm 1:4 4mm thick with dubara sponge finish | Plastering | Plastering 20mm (16mm+4mm)GFloor | As per relevant standard specifiction | 419 | M2 | 132848.14
16 | SWR33184 | 136.5 | Raised pointing in CM(1:3) including curing, cost and conveyance of all materials and labour charges for complete item of work. | Pointing | Raised Pointing to CRS Masonary CM(1:3) | As per relevant standard specifiction | 96 | M2 | 13104
17 | SWR33156 | 54.87 | Providing impervious coat over RCC roof slab surfaces to requried slopes with 20mm thick in CM 1:3 pro mixed with approvaled brand of water proffing compound as the raet of 1 kg per bag of cement inclding cost and conveyance of all materials | Roof plastering | Impervious Coat 20mm CM(1:3) GFloor | As per relevant standard specifiction | 448 | M2 | 24581.76
18 | SWR33264 | 5.7 | Supply and fixing of Flush type Doors with 35mm Thick Flush Shutters with Bondwood solied Block Board Type Faced on Both the sides with Commercial Type Plywood for finished item work as directed by the Engineer - in- charge. | Doors | S&F MT Wood Frame & Door-Laminate | As per relevant standard specifiction | 6799.02 | M2 | 38754.414
19 | SWR33277 | 5.76 | Supply and Fixing of Aluminium sliding windows with fixed glass panels using aluminium sections 62x32x1.2mm providing 5mm plain glass fixed to frame with beading gasket and glazing clips with all accessories,locking arrangements including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Windows | S&F Aluminium Window | As per relevant standard specifiction | 3381.54 | M2 | 19477.6704
20 | SWR33310 | 6.25 | Supplying and fixing of MS safety grill with peripheral frame of ISA 25x25x4mm and horizontal & vertical 8mm square rods and including cost and coveyance of all mateirals with all leads and lifts, labour charges, painting charges complete for finished item of work | Window grills | S&F of MS Safety Grill | As per relevant standard specifiction | 2539 | M2 | 15868.75
21 | SWR33219 | 26.5 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and approved size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and pointing with cement, labour etc, complete for finished item of work. | Flooring | Polished Shabad Flooring 20mm CM(1:3) | As per relevant standard specifiction | 664 | M2 | 17596
22 | SWR33236 | 6.94 | Providing skirting with tandoor blue slabs including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Flooring | Polished Shabad Skirting CM(1:3) | As per relevant standard specifiction | 730 | M2 | 5066.2
23 | SWR33029 | 34.67 | Plain Cement contrete - Nominal Mix (1:3:6) using 40 mm metal with concrete mixture including cost and conveyance of all materials labour charges etc. complete for finished iitem of work and as directed by the engineer-in-charge. | Concrete | PCC with 40mm Metal (1:3:6) | As per relevant standard specifiction | 4541 | M3 | 157436.47
24 | SWR33030 | 6.75 | PCC(1:2:4) using 10 to 12 mm aggregate including cost and conveyance of all materials labour charges etc., complete for finished iitem of work and as directed by the engineer-in-charge. | Concrete | PCC with 20mm Metal (1:2:4) | As per relevant standard specifiction | 5656 | M3 | 38178
25 | SWR33057 | 65.92 | Supply and Spreading of 20mm machine crushed metal including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Metal | S&Spreading of 20mm HBG Metal | As per relevant standard specifiction | 1514 | M3 | 99802.88
26 | SWR33403 | 110 | Supply and fixing of fencing of welded wire mesh (1" x 2") of 3mm dia with support channels of 75x 40mm and angles around of 30x30x3 mm including cost and conveyance of all materials, fabrication charges, painting charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Welded mesh | S&F MS Security Fencing Mesh (2"X2") | As per relevant standard specifiction | 2042 | M2 | 224620
27 | SWR33333 | 107.9 | Painting with two coats of OBD over a coat of primer including cost and conveyance of all materials ,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Painting | Painting with OBD 2Coats+Primer | As per relevant standard specifiction | 109.9 | M2 | 11858.21
28 | SWR33336 | 153 | Painting with two coats of ACE paint over a coat of primer including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Painting | Painting SnowCem/Apex 2 Coats+Primer | As per relevant standard specifiction | 195.91 | M2 | 29974.23
29 | SWR33329 | 196.5 | Painting with lovely cem three coats including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Painting | Painting with SuryaCem of 3 Coat | As per relevant standard specifiction | 70.47 | M2 | 13847.355
30 | SWR33442 | 25 | S&F Conceal PVC Pipe 32mm dia in Slab including cost and conveyance of all material and labour charges complete for finished item of work | Electrification | S&F Conceal PVC Pipe 25mm dia in Slab | As per relevant standard specifiction | 85 | RMT | 2125
31 | SWR33441 | 15 | S&F Conceal PVC Pipe 20mm dia in Wall including cost and conveyance of all material and labour charges complete for finished item of work | Electrification | S&F Conceal PVC Pipe 25mm dia in Wall | As per relevant standard specifiction | 89 | RMT | 1335
32 | SWR33457 | 15 | Wiring with 2X1.0 Sqm(14/.3mm) PVC insulated flexiable copper cable in the existing metalic/Non metalic conduit pipe with 6A mini modular SP switch, mounted on metalic box covereds with appropriate front plate modules etc ceiling rose including cot and conveyance of all mateials, labour charges complete for light points, bell points and fan points in non residential builsing except circuit moving finished in all types masonary as directed by department. | Electrification | S&F Modular Switch LP,FP,EFP for NRBuild | As per relevant standard specifiction | 580 | EA | 8700
33 | SWR33461 | 2 | Supply and fixing of 6A 3/2 pin flush type plug socket with 6A flush type marked switch control on a common board with earth continuity including wire leads earth connections along with all labour charges etc. complete | Electrification | S&F Modular 3/2pin 6A Sockets | As per relevant standard specifiction | 469 | EA | 938
34 | SWR33464 | 2 | Supply and fixing of 16A 3pin flush type plug socket and 16A flush type fuse unit and 16A switch control. | Electrification | S&F Modular 3pin 16/6A Sockets | As per relevant standard specifiction | 437 | EA | 874
35 | SWR33484 | 4 | Supply and fixing of slanting holders with 100W bulb with all connections and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F Batten Holder | As per relevant standard specifiction | 116 | EA | 464
36 | SWR33545 | 4 | Supply and fixing of patty type tube light fitting with 4' 0" - 40W tube light,40W copper choke,starter,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F 20W LED Retro Tube Light | As per relevant standard specifiction | 868 | EA | 3472
37 | SWR33494 | 90 | Supply and run of 2 of 14/.3mm(1.00Sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | S&R 2 of 14/0.3mm (1.0sqmm) (FR) | As per relevant standard specifiction | 48 | RMT | 4320
38 | SWR33497 | 30 | Supply and run of 2 of 36/0.3 (2.5sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | S&R 2 of 36/0.3mm (2.5sqmm) (FR) | As per relevant standard specifiction | 95 | RMT | 2850
39 | SWR33520 | 1 | SPN Distribution board with IP-20 protection suitable for single phase 40A DP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 4Nos as out going MCBs in sheet steel enclosure including connections and cost of all material labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F 8wySPNDB IP-20,10kA-6-32A SPMCB 4No | As per relevant standard specifiction | 5038 | EA | 5038
40 | SWR33596 | 1 | Providing independent earthing for main switches,IC cutouts and motors using 40mm. Dia. B-class G.I.Pipe of 2.5' length duly providing 12mm. Dia. 6No. Holes and required bolts,nuts and washers,including filling with equal preparation of salt and charcoal in layers and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | Provd-Independent Earthing | As per relevant standard specifiction | 4891 | EA | 4891
41 | SWR33597 | 15 | Supply and run of No.8 SWG Copper wire including cost of all accessories and labour charges etc., Complete | Electrification | S&R No.8 SWG Copper Wire | As per relevant standard specifiction | 140 | RMT | 2100
42 | SWR33563 | 2 | Supply and Fixing of 48" ceiling fan of bajaj make(or equivalent make) including cost material,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F 1200mm (48'') Sweep Ceiling Fan | As per relevant standard specifiction | 2215 | EA | 4430
43 | SWR33224 | 15.8 | Supply and fixing of ceramic tiles fantacy for dadoing including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Flooring | Ceramic Tile Flooring 20mm CM(1:3) | As per relevant standard specifiction | 764 | M2 | 12071.2
44 | SWR34311 | 1 | Supply and fixing of 580mm x 440mm long Orissa pan of Parry, Neycer or Hindhusthan, make with 'P' or 'S' trap etc complete for finished item of work and as directed by the engineer-in-charge. | Sanitary | S&F Orissa Pan WC 580mmx440mm | As per relevant standard specifiction | 2178 | EA | 2178
45 | SWR34386 | 2 | Supply and Fixing 4" PVC floor trap including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F Floor Trap (Bell Mouth) 110mm | As per relevant standard specifiction | 269 | EA | 538
46 | SWR34382 | 2 | Supply,fixing 90mm dia. PVC Plain Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F 90mm dia Plain Bend PVC/SWR Pipe | As per relevant standard specifiction | 84 | EA | 168
47 | SWR34385 | 1 | Supply,fixing 90mm dia. PVC Door Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F 75mm dia Door Bend PVC/SWR Pipe | As per relevant standard specifiction | 81 | EA | 81
48 | SWR34286 | 1 | S&Fixing 150mm x 100mm SWG gully traps Ist class grating & constg brick masonry in CM (1:6) prop inter mediate chamber and fitted with CI frame etc complete. | Sanitary | S&F 150mmx100mm SWG Gully Trap | As per relevant standard specifiction | 749 | EA | 749
49 | SWR34377 | 6 | Supply and Fixing 4" dia 3M Single socket PVC pipe including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F 110mm dia 3M 1Socket PVC/SWR Pipe | As per relevant standard specifiction | 422 | RMT | 2532
50 | SWR34453 | 1 | Supply and Fixing 4" dia PVC cowl including labour charges etc. complete for finished item of work. | Plumbing | S&F 4" dia PVC Cowl | As per relevant standard specifiction | 23 | EA | 23
51 | SWR34444 | 1 | Construction of soak pit with 4' dia RCM rings upto a depth of 6' including cost and conveyance of all materials as directed by the engineer-in-charge. | Sanitary | Construct- 4' dia & 5' Ht Soak Pit | As per relevant standard specifiction | 2950 | EA | 2950
52 | SWR34361 | 20 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) 15.90mm OD Pipe - SDR 11 | Plumbing | S&F 15.90mm OD CPVC Pipe-SDR 11 | As per relevant standard specifiction | 239 | RMT | 4780
53 | SWR34362 | 100 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) 22.20mm OD Pipe - SDR 11 | Plumbing | S&F 22.20mm OD CPVC Pipe-SDR 11 | As per relevant standard specifiction | 313 | RMT | 31300
54 | SWR34363 | 100 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) 28.60mm OD Pipe - SDR 11 | Plumbing | S&F 28.60mm OD CPVC Pipe-SDR 11 | As per relevant standard specifiction | 410 | RMT | 41000
55 | SWR34344 | 18 | Supply and fixing of 15mm dia. SS coated taps including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F-15mm GM/Bronze Ball Valve | As per relevant standard specifiction | 230 | EA | 4140
56 | SWR34345 | 1 | Supply and fixing of 20mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F-20mm GM/Bronze Ball Valve | As per relevant standard specifiction | 331 | EA | 331
57 | SWR34346 | 2 | Supply and fixing of 25mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F-25mm GM/Bronze Ball Valve | As per relevant standard specifiction | 466 | EA | 932
58 | SWR34329 | 3 | Supply and fixing of 12.7mm bib tap Indian make including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F-15mm Bib Tap 400gm Full turn | As per relevant standard specifiction | 271 | EA | 813
59 | SWR34375 | 500 | Providing and placing on Terrace polyetheylene water storage tank with double layer approved brand and manufacture with cover complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F Polyethylene Water Storage Tank | As per relevant standard specifiction | 10 | L | 5000
60 | SWR34740 | 1 | Supply of steel table of size 4'x2.5'x30" with 18 mm plywood fixed with rubber beeding with drawers on right side with automatic locking arrangements etc complete for finished item of work and as directed by the engineer-in-charge. | Furniture | S-3x2ft Office Table | As per relevant standard specifiction | 5000 | EA | 5000
61 | SWR33857 | 1 | Supply of 'S' type chair with arms teakwood frame with seat back 's' type on G.I pipe including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Furniture | Supply of S-Type Chair | As per relevant standard specifiction | 3850 | EA | 3850
62 | SWR33858 | 2 | Supply of P V C chairs of Neelkamal of approved quality & make including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Furniture | Supply of PVC Chair | As per relevant standard specifiction | 1150 | EA | 2300
63 | SWR33406 | 150 | S&Fixing of R.C.C fencing poles of size 0.115mx0.115mx2.7m including cost & conveyance of all materials,labour chargesv etc complete for finished item of work. | Fencing | S&F RCC Fencing Pole 0.115mx0.115mx2.7m | As per relevant standard specifiction | 1411 | EA | 211650
64 | SWR33405 | 76 | Providing and fixing 1.80 metre long RCC fencing posts with 6 mm bar bibs of pole size 0.1x0.1x1.8m in pit size of 0.45x0.45x0.45 and filled with PCC (1:4:8) using 20mm metal including cost & conveyance of all materials, labour charges etc complete for finished item of work. | Fencing | S&F RCC Fencing Pole 0.1mx0.1mx1.8m | As per relevant standard specifiction | 1269 | EA | 96444
65 | SWR33407 | 450 | S&Fixing of barbed wire 8 straight strands and 2 cross strands including cost & conveyance of all materials, labour charges etc complete for finished item of work. | Fencing | S&F Barbed Wire 8H & 2Cross | As per relevant standard specifiction | 260.05 | M | 117022.5
66 | SWR33421 | 1.35 | Supply and Fixing of Substation name board of size 5'x3' iron sheet with angle frame and channel supports of size 75x40mm, 8' height including concreting of channel supports and painting with enamel paint complete. | Name board | S&F MS Board | As per relevant standard specifiction | 4542.3 | Sqm | 6132.105
67 | SWR33423 | 1.8 | S&F Poly Vinyl Acrylic Board including cost & conveyance of all materials, labour charges etc complete for finished item of work. | Name board | S&F Poly Vinyl Acrylic Board | As per relevant standard specifiction | 1930.48 | Sqm | 3474.864
68 | SWR33608 | 1 | Geophysical Investgation Charges | Borewell | Geophysical Investgation Charges | As per relevant standard specifiction | 5000 | EA | 5000
69 | SWR33609 | 90 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work. 0 to 90M | Borewell | Drilling-165mm Bore Well 0 to 90M | As per relevant standard specifiction | 336 | M | 30240
70 | SWR34830 | 30 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work. 90m to 120M | Borewell | Drill-165mm Bore Well 90M to 120M | As per relevant standard specifiction | 369 | M | 11070
71 | SWR34831 | 30 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work. 120m to 150M | Borewell | Drill-165mm Bore Well 120M to 150M | As per relevant standard specifiction | 369 | M | 11070
72 | SWR33611 | 30 | Suppy & fixing of 160 mm dia. 6 kg/cm2 PVC casing pipe including cost and conveyance of all materials labour charges etc complete for finished item of work | Borewell | S&F 160mm dia PVC Casing | As per relevant standard specifiction | 844 | M | 25320
73 | SWR33636 | 1 | Supply & fixing of 2HP Multistage submersible motor pumpset of approved make (Texmo or equivalent type) including cost and conveyance of all materials etc complete for finished item of work. | Borewell | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | As per relevant standard specifiction | 34237 | EA | 34237
74 | SWR33641 | 60 | S&R 3C 2.5sqmm Flat Copper Cable including cost of all materials and labour charges for finished item of work. | Borewell | S&R 3C 2.5sqmm Flat Copper Cable | As per relevant standard specifiction | 190 | EA | 11400
75 | SWR33644 | 1 | Supply and fixing of Panel box and starter including cost of all materials and labour charges for finished item of work. | Borewell | S&E D.O.L Starter 250V Single Phase | As per relevant standard specifiction | 1040 | EA | 1040
76 | SWR34203 | 1 | Supply & fixing of Flange Clamps including cost of all materials and labour charges for finished item of work. | Borewell | Supply & ixing of Flange Clamps | As per relevant standard specifiction | 182 | EA | 182
77 | SWR34410 | 178 | Suppy & fixing of HDPE pipe 1.5" dia. including cost & conveyance of all materials labour charges etc complete for finished item of work. | Borewell | S&F-HDPE Pipe 40mm dia 16kg/sqcm-SDR 9 | As per relevant standard specifiction | 160 | Rmt | 28480
78 | SWR34470 | 92.2 | Seigniorage Charges - Sand | Seigniorages | Seigniorage Charges - Sand | As per relevant standard specifiction | 40 | M3 | 3688
79 | SWR34471 | 96.5 | Seigniorage Charges - Metal | Seigniorages | Seigniorage Charges - Metal | As per relevant standard specifiction | 97.5 | M3 | 9408.75
80 | SWR34472 | 826.01 | Seigniorage Charges - Gravel | Seigniorages | Seigniorage Charges - Gravel | As per relevant standard specifiction | 30 | M3 | 24780.3
[7 empty] | Civil total |  | 3331882.7284
[7 empty] | Electrical & Civil total |  | 7293739.4674

## 5. Thimmapur SS
Thimmapur SS Electrical Schedules(WBS No: S-1744-90-06-01-01-001)
Name of the work: Estimate for erection of new 33/11 KV SS with connected 33 KV and 11 KV lines at Thimmapur (V) in Nagalgidda(M) of Jogipet Division of Sangareddy Circle
S.No | SSR Code | Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR10105 | 39 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 23400
2 | SWR10343 | 31 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 74400
3 | SWR10356 | 27.28 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt)*31 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 179475.12
4 | SWR11890 | 0.961 | ERECTION OF S.S. STRUCTURE: Coping of 0.45x0.45x0.45Mt with 1:8 slope Using form boxes (0.031Cumt.) | Civil work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | M3 | 3741.173
5 | SWR11331 | 31 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of poles with two coats of white cement (including cost of paint). | Electrical work | Paint-9.1M PSCC Poles as desc SSR | As per relevent standard specification | 485 | EA | 15035
6 | SWR11889 | 5.7 | Fabrication of 100 X 50mm MS Channel for formation of 11kV and 33kV bays: Fabrication and erection of M.S,Channel 100x50mm for forming of 33KV & 11 KV Bays as per standard specifications to facilitate stringing of bus, erection of LA sets, AB Switches bolts & Nuts etc. including painting with one coats of red oxide and two coats of Aluminium paint. GI bolts&nuts shall be used. | Electrical work | Fabr & Erect-MS Chnl 100x50mm for SS Bay | As per relevent standard specification | 6600 | TO | 37620
7 | SWR10404 | 118 | Erection of 33kV and 11kV Strung Bus with Panther (200Sqmm) ACSR Conductor: Erection of 33kV and 11kV Bus over the Substation structures with 200sqmm Panther ACSR conductor and giving Jumpers to connect the Switch gear by providing the suitable T clamps and round clamps suitable to Post type insulators & Insulators. | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 38666.24
8 | SWR10884 | 50 | Connectionof equipment to bus and or another equipmentwithsingle zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Electrical work | Conn. of equip/bus single zebra/panther | As per relevent standard specification | 224 | EA | 11200
9 | SWR10392 | 2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 9000
10 | SWR10393 | 11 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 35200
11 | SWR11742 | 3 | Supply & erection of 11 kV 400 A convential single(1/3) phasing AB switches.includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | S&E-400A 11KV ABSwth Conv 1ph(1/3) in SS | As per relevent standard specification | 4232 | EA | 12696
12 | SWR21240 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt). | Electrical work | Hoisting post ins&hrd wr 1panther 33kv | As per relevent standard specification | 781 | EA | 1562
13 | SWR21241 | 4 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 11kv | As per relevent standard specification | 507 | EA | 2028
14 | SWR10881 | 13 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 1846
15 | SWR23224 | 16.46 | Excavation of pit in all types of soils of size 2.2x2.2x0.85Mts.for Construction of Plinths for VCB (33KV & 11 KV ) | Earth work | Excavate-Pit for 33KV VCB | As per relevent standard specification | 331 | M3 | 5448.26
16 | SWR20685 | 25 | Providing of Base concreting (2.2x2.2x0.15 Mts) with 1:3:6 Concrete mix. Using form boxes, Providing of Concreting (2x2x1.0mts) with 1:3:6 Cocrete mix. Plastering of the plinth for smooth finishing with 12mm thick 1:3 cement motor and providing two coats white washing for part of the plinth above groung level. | Civil work | Cement concrete with 40MM metal VCB plin | As per relevent standard specification | 5160 | M3 | 129000
17 | SWR10461 | 5 | Erection of Switchgear complete for 11 kV VCB includes Assembling the VCB Structures and mounting the VCBs over the already erected foudation including wiring of Breaker Control Panel/CTs, erection of CTs and control pannel providing Jumpers. | Electrical work | Erection of 11kv VCB | As per relevent standard specification | 12000 | EA | 60000
18 | SWR10421 | 30 | Fixing of T-Clamps | Electrical work | Fixing of T- clamp | As per relevent standard specification | 116 | EA | 3480
19 | SWR10396 | 2 | Erection of 33KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 1760
20 | SWR10397 | 1 | Erection of 11 KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 11kv LA stn type incl earthing | As per relevent standard specification | 559 | SET | 559
21 | SWR10398 | 4 | Erection of 11 KV Lightening Arrestors line type complete including jumpering. | Electrical work | Erect of 11kvLA line type incl earthing | As per relevent standard specification | 505 | SET | 2020
22 | SMR11607 | 1 | Supply of 33kv HG fuse set including providing of jumpers | Electrical work | S-33KV HG Fuse Set excl Ins & Chnl | As per relevent standard specification | 6431 | SET | 6431
23 | SWR10394 | 1 | Erection of 33kv HG fuse set including providing of jumpers | Electrical work | Erect. of 33kv HG Fuseset incl earthing | As per relevent standard specification | 1331.81 | SET | 1331.81
24 | SMR11608 | 1 | Supply of 11kv HG fuse set including providing of jumpers | Electrical work | S-11KV HG Fuse Set | As per relevent standard specification | 1733.75 | SET | 1733.75
25 | SWR10395 | 1 | Erection of 11kv HG fuse set including providing of jumpers | Electrical work | Erect. of 11kv HG Fuseset incl earthing | As per relevent standard specification | 740.52 | SET | 740.52
26 | SMR11482 | 22 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 76692
27 | SWR10357 | 22 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 27152.4
28 | SWR10920 | 480 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification.75x8 mm MS flat for Earth mat and connecting to electrodes. | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 31200
29 | SWR10919 | 928 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification. 50x6 mm MS flat for raisers, double flat shall be run for structure poles raisers & equipment earthing. | Electrical work | Earthing for raisers of SS Flat 50x6 mm. | As per relevent standard specification | 41 | RMT | 38048
30 | SMR40033 | 2 | Providing of double earthing for neutral with flexible copper jumpers of adequate size including arrangement by fixing M.S.Channel 100x50mm. | Electrical work | SupCU Flexi jumper for Power T/F Neutral | As per relevent standard specification | 4725 | EA | 9450
31 | SWR11771 | 5 | Erection of 24 Volts Battery along with Charger on the VCB plinth and giving DC supply to VCB's. | Electrical work | Erect-24V Batery with Chrgr incl grot-SS | As per relevent standard specification | 1050 | EA | 5250
32 | SWR11474 | 750 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable includes excavation of earth and back filling with sand and earth in alternate layers . The cable termination shall be made by providing proper size lugs and shall be identified with colours. | Electrical work | Laying-4 core cable | As per relevent standard specification | 15 | RMT | 11250
33 | SWR10463 | 1 | Erection of 25 KVA Three phase Station Transformer on the Substation Structures and giving jumpers/connections on HT side to the 11kV bus. Belting angle shall be provided both sides of DTR for securing DTR firmly in position. | Electrical work | Erection of Three Phase DTRs | As per relevent standard specification | 1139.95 | EA | 1139.95
34 | SMR40045 | 1 | Supply of AC Panel Board includes: Fixing of 1 No.100A, MCCB, 10kA capacity of any standard make including material cost. Fixing of suitable panel box 3x3x1 with M.S.Sheet of 16 SWG with front door compartments inclusive of material cost & powder coating (with C Channel ). Fabrication of panel Fixing of 96x96mm analog voltmeter with VSS switch Fixing of 20A HRC fuse Fixing of 3 phase supply indicator kwith HRC fuses Supply and fixing of 6 Sqmm copper flexible wire (PVC) Fixing of Stud type TBs for outgoing feeder Fixing of Epoxy bus supports. | Electrical work | Supply of AC Supply panel complete | As per relevent standard specification | 42000 | EA | 42000
35 | SMR40044 | 1 | Supply of DC Panel Board Fixing of suitable panel box of size 6'x6'x1' with M S sheet of 16 SWG with back doors (4'x6') and on front side with provision to fix up bakelite hylam sheet size of 4'x6' including cost of the panel with powder coating. Fixing of best quality of angles for panel. Fixing of C Channelfor panel. Fabrication of control panel including making suitable holes and board Fixing of Stud type TBs for outgoing feeder Fixing of 24V DC pilot lamps of standard make Fixing of healthy trip push buttons with LED lamp Fixing of plain switches for alarm acceptance and for PTR signal Fixing of ON/OFF push buttons Fixing of digital volt meter for 11kV Fixing of VSS of standard make, Fixing of Engraved AL plates for Alarm panel of various VCB Laying of 2.5Sqmm copper flexible wire for internal wiring . Fixing of digital frequency meter Fixing of Copper lugs and ferrules for internal wiring. Fixing of 4" Gang bells 24V DC Fixing of flow diagram with rading strip Fixing of HRC fuse units | Electrical work | Supply of DC Anunc.relay panel 8 feeders | As per relevent standard specification | 42500 | EA | 42500
36 | SWR11893 | 2 | fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supplied by tenderer. | Electrical work | Erect-Contrl/Relay, AC, Announ. Panels | As per relevent standard specification | 1930 | EA | 3860
37 | SWR10342 | 8 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 12000
38 | SWR10956 | 8 | Fixing of Metal halide/LED lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5M GI pipe complete. | Electrical work | Fixing of LED/Metal halide complete. | As per relevent standard specification | 1268 | EA | 10144
39 | SWR20028 | 8 | Supply and Fixing of junction box and Providing with proper Fuse protection and required glauds suitable for Cable Terminations. The box shall be fixed on the pole. | Electrical work | 33/11kv S.S Yard lighting junction box | As per relevent standard specification | 351.9 | EA | 2815.2
40 | SWR20526 | 1 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply & fixing of marshall box | As per relevent standard specification | 3085.5 | EA | 3085.5
41 | SMR40088 | 1 | Supply and fixing of filled sand bucket set complete (4 Nos. Buckets) with stand to mount fire buckets. | Electrical work | Sup Fire Buckets Stand with Buckets | As per relevent standard specification | 1386 | SET | 1386
42 | SMR40087 | 2 | Supply and fixing of CO2 Cylinder set as per IS2878 Specifications. | Electrical work | Sup TrollyMounted Co2 Cylinders(IS-2878) | As per relevent standard specification | 9240 | EA | 18480
43 | SWR11895 | 1 | Supplying and fixing of feeder indicator board to each of the 3Nos feeder breakers and LV breaker, danger boards made of 1'x1' and properly mounted on the structures. The letters written on the borad shall be 1.5"size with blue colour and background shall be of white colour | Electrical work | S&F-33/11KV SS Feeder Indicator Board | As per relevent standard specification | 551 | SET | 551
44 | SWR20032 | 1 | Supply and fixing of wooden board of size 3'x2'.5'indicating the layout of the Switch yard. | Electrical work | Sup &fix of board ind Switchyard layout | As per relevent standard specification | 1654 | EA | 1654
45 | SMR40086 | 1 | Supply and Erection of Permanent Name Board of on 3'x4' steel sheetmounted on steel frame as described in Specification. | Electrical work | Sup 33/11kv S.S Permanent name board | As per relevent standard specification | 10238 | EA | 10238
46 | SMR40076 | 1 | Supply of Digital clamp meter. | Electrical work | Supply of Digital clamp meter. | As per relevent standard specification | 2888 | EA | 2888
47 | SMR40064 | 1 | Supply of Rechargeable LED torch light of Standard make. | Electrical work | Sup Rechargeable LED torch light. | As per relevent standard specification | 1733 | EA | 1733
48 | SMR40063 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box containing ‘D’Spanners from size 6 to 54, Hammer small and big size, Ring spanners from 6 to 28, Adjustable spanner, Pipe wrench, Cutting Plier, Nose plier, Tester, insulated Screw drive. | Electrical work | SupTaparia Tool kit complete as per Spec | As per relevent standard specification | 4925 | SET | 4925
49 | SWR22090 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Electrical work | Sup& fix safety inst/SS Op. inst board | As per relevent standard specification | 2205 | EA | 2205
50 | SMR11598 | 8 | Supply of 25 W LED lamp with fitting of philips make | Electrical work | S-25W LED fixture set | As per relevent standard specification | 3200 | EA | 25600
51 | SMR12378 | 1 | Supply of Alluminum Ladder(20 feet) | Electrical work | S-10ft Aluminium Ladder | As per relevent standard specification | 1654 | EA | 1654
52 | SMR40075 | 1 | Supply of Megger (2000 ohms, 0-2.5kv) | Electrical work | Supply of Earth megger (1000v) | As per relevent standard specification | 8085 | EA | 8085
53 | SMR40067 | 2 | Supply of Hand Gloves | Electrical work | Supply of Hand Gloves | As per relevent standard specification | 289 | SET | 578
54 | SMR40071 | 2 | Supply of Safety Helmets of standard make | Electrical work | Supply of Safety Helmet of standard make | As per relevent standard specification | 231 | EA | 462
55 | SMR11599 | 4 | Supply of Earth Discharging Rod 10' length. | Electrical work | S-Earth Rod 8ft Long 3mm Thick | As per relevent standard specification | 1000 | EA | 4000
56 | SMR11488 | 200 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 23500
57 | SMR11591 | 66 | Supply of PG clamps for panther 2 bolted 800 A. | Electrical work | S-Al. alloy three bolted PG clamps 800A | As per relevent standard specification | 130 | EA | 8580
58 | SWR20029 | 200 | Supply and Laying of 2 core/4 core cable includes excavation earth and back filling with sand and earth in alternate layers as shown in the sketch. The cable termination shall be made by providing proper size of lugs at both ends of the cable termination. | Electrical work | 33/11kv S.S laying of 2/4core for light | As per relevent standard specification | 50 | M | 10000
59 | SWR20308 | 31 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 12625.99
60 | SWR20307 | 8 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 2172.16
61 | SWR11860 | 4 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 10881.36
62 | SWR10150 | 10.42 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 6430.182
63 | SWR10206 | 10.42 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 2302.82
64 | SWR10524 | 10.42 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 1927.7
65 | SWR11220 | 350 | Loading and unwinding of Panther conductor. | Electrical work | Load-Unwinding Panther conductor | As per relevent standard specification | 3 | M | 1050
66 | SWR11221 | 350 | Unloading of Panther conductor. | Electrical work | Unload-Unwinding Panther conductor | As per relevent standard specification | 2 | M | 700
67 | SWR12416 | 2 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 4
68 | SWR10631 | 2 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 4
69 | SWR10618 | 2 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 130
70 | SWR10632 | 2 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 130
71 | SWR10212 | 2 | Loading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | LOADING of 11kv Pin/Post/Solid Core Insu | As per relevent standard specification | 1 | CRT | 2
72 | SWR10530 | 2 | Unloading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | UNLOADING of 11kv Pin/Post/Solid Core In | As per relevent standard specification | 1 | CRT | 2
73 | SWR11701 | 750 | Loading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | Load-PVC Control Cable 10C | As per relevent standard specification | 1 | M | 750
74 | SWR11712 | 750 | Unloading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | UnLoad-PVC Control Cable 10C | As per relevent standard specification | 1.02 | M | 765
75 | SWR11691 | 1 | Loading of 3Ph 25KVA Distribution Transformer. | Electrical work | Load-3Ph 25KVA DTR | As per relevent standard specification | 252 | EA | 252
76 | SWR11692 | 1 | UnLoading of 3Ph 25KVA Distribution Transformer. | Electrical work | UnLoad-3Ph 25KVA DTR | As per relevent standard specification | 202 | EA | 202
77 | SWR10200 | 1 | Loading of 33/11 KV Current Transformers/ Potential Transformers. | Electrical work | LOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 165 | EA | 165
78 | SWR10266 | 6 | Loading of 33 KV10 KA LAs Station type. | Electrical work | LOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 41 | EA | 246
79 | SWR10584 | 6 | Unloading of 33 KV10 KA LAs Station type. | Electrical work | UNLOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 35 | EA | 210
80 | SWR10265 | 12 | Loading of 11 KV10 KA LAs Line type. | Electrical work | LOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 384
81 | SWR10583 | 12 | Unloading of 11 KV10 KA LAs Line type. | Electrical work | UNLOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 384
82 | SWR10264 | 3 | Loading of 11 KV10 KA LAs Station type. | Electrical work | LOADING of 11 KV,10 KA LAs Station type | As per relevent standard specification | 32 | EA | 96
83 | SWR10582 | 3 | Unloading of 11 KV10 KA LAs Station type. | Electrical work | UNLOADING of 11 KV,10 KA LAs Station typ | As per relevent standard specification | 32 | EA | 96
84 | SWR10239 | 2 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 252
85 | SWR10557 | 2 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 158
86 | SWR10238 | 11 | loading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 880
87 | SWR10556 | 11 | Unloading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 880
88 | SWR11224 | 5 | Loading and Unloading of 12V/24V Battery Set. | Electrical work | Load/Unload-12V/24V Battery Set | As per relevent standard specification | 23 | EA | 115
89 | SWR10356 | 2.66 | ERECTION OF S.S. STRUCTURE: Providing of base concreting of size 0.76x0.76x0.15M with CC mix of ratio 1:3:6 Using form boxes(0.087Cu.Mt)x31 with 20mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 17500.14 | 1163177.275
90 | SWR10402 | 1 | Erection of 11kv Potential Transformer sets complete including jumpering. The LV side of the PT shall be provided with proper fuse protection mounted in separate marshalling boxwith proper size cable glands etc. The box shall be mounted on the Substation structure. | Electrical work | Erection of 11kv three phase PT s | As per relevent standard specification | 800 | SET | 800
91 | SWR10518 | 1 | Unloading of 33/11 KV Current Transformers/ Potential Transformers | Electrical work | UNLOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 128 | EA | 128
92 | SWR10674 | 1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
93 | SWR10356 | 4.32 | Concreting the location after erection of 8.0 Mtrs pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) ( 0.6x0.6x1.5)mtrs x 8 . | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 28421.28
94 | SWR21750 | 2 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply and fixing of PT Marshalling box | As per relevent standard specification | 1139.85 | EA | 2279.7
95 | SMR25233 | 31 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 96391.71
96 | SMR22745 | 5700 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 327465
97 | SMR12321 | 2400 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 135408
98 | SMR12322 | 2320 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 131080
99 | SMR25232 | 8 | Supply of 8.0Mtr PSCC 140 Kg Pole | Electrical work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 12640
100 | SMR12315 | 2 | Supply of 33KV 800A DB Break AB Switch | Electrical work | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 81317.56
101 | SMR12316 | 2 | Supply of 11KV 800A DB Break AB Switch | Electrical work | S-11KV 800A DB Break AB Switch | As per relevent standard specification | 30847.46 | EA | 61694.92
102 | SMR12317 | 9 | Supply of 11KV 400A DB Break AB Switch | Electrical work | S-11KV 400A DB Break AB Switch | As per relevent standard specification | 18150 | EA | 163350
103 | SMR25200 | 1 | Supply of LT Distribution Box (SMC) | Electrical work | S-LT Distribution Box (SMC) | As per relevent standard specification | 7797 | EA | 7797
104 | SWR10674 | 1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
105 | SMR40009 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for First coat of 1st GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 11995.5
106 | SWR10877 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 1st coat of Aluminium | Electrical work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 4680.5
107 | SMR40010 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for second coat of 2nd GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 7111.5
108 | SWR10879 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 2nd coat of Aluminium | Electrical work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 2651
109 | SWR22092 | 1.71 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 1308.15
110 | SWR10107 | 30 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 21000
111 | SWR10112 | 5 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | As per relevent standard specification | 1680 | EA | 8400
112 | SWR10105 | 22 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 13200
113 | SWR10978 | 35 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 145784.8
114 | SWR11083 | 22 | Erection of 9.1 Mts Sturt pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. | Electrical work | Erec of 9.1 Mts PSCC poles for stuts | As per relevent standard specification | 2400 | EA | 52800
115 | SWR10981 | 11 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Horizontal Cut point for 33 KV line | As per relevent standard specification | 1759.5 | EA | 19354.5
116 | SWR10356 | 19.026 | Concreting the location after erection of 11 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.76X0.76X1.83 Mts)* 18 = 19.026 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 125172.054
117 | SWR10366 | 1.71 | Paving of the 100 sqmm AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 12600.06 | KM | 21546.1026
118 | SMR11488 | 50 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 5875
119 | SWR11180 | 35 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 15118.95
120 | SWR20308 | 22 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 8960.38
121 | SWR10191 | 1 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 202
122 | SWR10509 | 1 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 100
123 | SWR11860 | 1 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 2720.34
124 | SWR10150 | 1 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 617.1
125 | SWR10206 | 1 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 221
126 | SWR10524 | 1 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 185
127 | SWR10211 | 10 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 30
128 | SWR10529 | 10 | Unloading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 30
129 | SWR12416 | 7 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 14
130 | SWR10631 | 7 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 14
131 | SWR10618 | 3 | Loading of 33KV Metal parts bag of 25 nos | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 195
132 | SWR10632 | 3 | Unloading of 33 KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 195
133 | SWR10252 | 25 | Loading of 33KV Top fittings | Electrical work | LOADING of 33 KV Top fittings | As per relevent standard specification | 1 | EA | 25
134 | SWR10570 | 25 | Unloading of 33 KV Top fittings | Electrical work | UNLOADING of 33 KV Top fittings | As per relevent standard specification | 1 | EA | 25
135 | SWR10319 | 46 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 75 x 8 mm MS Flat | Electrical work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31 | EA | 1426
136 | SWR10322 | 88 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 75 x 8 mm MS Flat | Electrical work | Fab Stay clamps with 75x8 mm MM Flat | As per relevent standard specification | 42 | EA | 3696
137 | SWR10378 | 35 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevent standard specification | 32 | EA | 1120
138 | SWR10354 | 11 | Erection of 33 kv Stay set complete including fixing of bow ,fixing and binding of Eye bolt, Anchor rod, guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. | Electrical work | Assembly and erection of Stay set 33kv | As per relevent standard specification | 684.53 | SET | 7529.83
139 | SWR21190 | 11 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock,Hard rock Requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 5720
140 | SMR25236 | 35 | Supply of 11Mtr PSCC 365 Kg Pole | Electrical work | S-PSCC Pole 11Mtr 365 Kg | As per relevent standard specification | 5399 | EA | 188965
141 | SMR25233 | 22 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 68407.02
142 | SMR25229 | 25 | Supply of 33KV V-Cross Arm without Clamps | Electrical work | S-33KV V-Cross Arm without Clamps | As per relevent standard specification | 1678 | EA | 41950
143 | SMR25207 | 260 | Supply of MS Angle 65X65X6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 14885
144 | SMR22745 | 380 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 21831
145 | SMR12321 | 360 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 20311.2
146 | SMR25231 | 11 | Supply of 33KV MS Stay Set with BasePlate | Electrical work | S-33KV MS Stay Set with BasePlate | As per relevent standard specification | 1035 | SET | 11385
147 | SWR22092 | 7.6 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 11 kv line. | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 5814
148 | SWR10107 | 30 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 21000
149 | SWR10112 | 5 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | As per relevent standard specification | 1680 | EA | 8400
150 | SWR10105 | 148 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 88800
151 | SWR10978 | 35 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 145784.8
152 | SWR10343 | 82 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 196800
153 | SWR11083 | 18 | Erection of 9.1Mtr pole for stuts in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | Erec of 9.1 Mts PSCC poles for stuts | As per relevent standard specification | 2400 | EA | 43200
154 | SWR10342 | 48 | Erection of 8.0 Mts PSCC Poles including fixing of 11 KV X arm and top cleats and fixing of Pin insulators complete with necessary hard ware for tangential locations excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 72000
155 | SWR10653 | 46 | Formation of 11 kv cut points (Vertical/Horizantal) including fixing of 11 KV Cross arms,clamps, strain insulators sets complete with hardware and stays (Bows and Eye-bolts), Excluding the cost of pit Excavation and pole erection. The contractor has to supply GI Bolts and Nuts. | Electrical work | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1350 | EA | 62100
156 | SWR10356 | 42.246 | Concreting the location after erection of 11/9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.76X0.76X1.83 Mts)* 35 = 36.995 Cu.Mt & (0.76X0.76X1.52 Mts)*6 = 5.262 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 277936.434
157 | SWR10365 | 4.1 | Paving of the conductor 55 Sqmm Single Circuit (3 Conductors) AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 3 Cond | As per relevent standard specification | 8500 | KM | 34850
158 | SWR10703 | 1.75 | Paving of the conductor 55 Sqmm Double Circuit (6 Conductors) AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 6 Cond | As per relevent standard specification | 16000 | KM | 28000
159 | SMR11488 | 200 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 23500
160 | SWR10206 | 3.18 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 702.78
161 | SWR10524 | 3.18 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 588.3
162 | SWR10134 | 3.18 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 1868.3136
163 | SWR11248 | 447 | Loading 11KV Polymer Pin Insulator with GI pins | Electrical work | Load-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 447
164 | SWR11249 | 447 | Unloading 11KV Polymer Pin Insulator with GI pins | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 447
165 | SWR11862 | 3 | Transport of VCB , Control pannels, current transformater, bosster etc, above 20 KM and upto 30 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 11074.14
166 | SWR10191 | 3 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 606
167 | SWR10509 | 3 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 300
168 | SWR11180 | 35 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 15118.95
169 | SWR20308 | 100 | Sub Transportation of 9.1M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 40729
170 | SWR20307 | 48 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 13032.96
171 | SWR10228 | 133 | Loading of 11 KV V - Cross arms | Electrical work | LOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 532
172 | SWR10546 | 133 | Unloading of 11 KV V - Cross arms | Electrical work | UNLOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 532
173 | SWR12402 | 12 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 576
174 | SWR12421 | 12 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 576
175 | SWR10251 | 55 | Loading of 11 KV Top fittings | Electrical work | LOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 55
176 | SWR10569 | 55 | Unloading of 11 KV Top fittings | Electrical work | UNLOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 55
177 | SWR12416 | 15 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 30
178 | SWR10631 | 15 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 30
179 | SWR10353 | 33 | Erection of 11 kv Stay set complete including fixing of bow, fixing and binding of Eye bolt,Anchor rod,guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Assembly and erection of Stay set11kv&LT | As per relevent standard specification | 606.85 | SET | 20026.05
180 | SWR21190 | 33 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In Hard Gravel and Hard murram not requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 17160
181 | SWR10319 | 132 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 75 x 8 mm MS Flat | Electrical work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31 | EA | 4092
182 | SWR10322 | 72 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 75 x 8 mm MS Flat | Electrical work | Fab Stay clamps with 75x8 mm MM Flat | As per relevent standard specification | 42 | EA | 3024
183 | SWR10320 | 107 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 50 x 6 mm MS Flat | Electrical work | Fab Back clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 15 | EA | 1605
184 | SWR10323 | 192 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 50 x 6 mm MS Flat | Electrical work | Fab Stay clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 25 | EA | 4800
185 | SWR10378 | 117 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevent standard specification | 32 | EA | 3744
186 | SMR25236 | 35 | Supply of 11Mtr PSCC 365 Kg Pole | Electrical work | S-PSCC Pole 11Mtr 365 Kg | As per relevent standard specification | 5399 | EA | 188965
187 | SMR25233 | 100 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 310941
188 | SMR25232 | 48 | Supply of 8.0Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 75840
189 | SMR25218 | 133 | Supply of 11KV V X-Arms with MS Angle 65x65x6 | Electrical work | S-11KV V X-Arms with MS Angle 65x65x6 | As per relevent standard specification | 743 | EA | 98819
190 | SMR22745 | 690 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 39640.5
191 | SMR25205 | 560 | Supply of MS Channel 75x40mm | Electrical work | S-MS Channel 75x40 mm | As per relevent standard specification | 58.45 | KG | 32732
192 | SMR25207 | 440 | Supply of MS Angle 65x65x6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 25190
193 | SMR25206 | 450 | Supply of MS Angle 50x50x6 | Electrical work | S-MS Angle 50x50x6 | As per relevent standard specification | 58.15 | KG | 26167.5
194 | SMR12321 | 580 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 32723.6
195 | SMR12322 | 460 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 25990
196 | SMR25214 | 33 | Supply of LT/11KV MS Stay Sets with Base Plate | Electrical work | S-LT/11KV MS Stay Sets with Base Plate | As per relevent standard specification | 1168 | SET | 38544
197 | SWR10392 | 3 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 13500 | 4 pole str
198 | SWR10105 | 4 | ERECTION OF 4 pole STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 2400
199 | SWR10343 | 4 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 9600
200 | SWR10356 | 2.16 | Concreting the location after erection of 9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes(0.6X0.6X1.5 Mts)*4 = 2.16 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 14210.64
201 | SMR11488 | 4 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 470
202 | SWR10206 | 0.65 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 143.65
203 | SWR10524 | 0.65 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 120.25
204 | SWR10134 | 0.65 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 381.888
205 | SWR10421 | 18 | Fixing of T-Clamps | Electrical work | Fixing of T- clamp | As per relevent standard specification | 116 | EA | 2088
206 | SWR10404 | 20 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 6553.6
207 | SWR10884 | 9 | Connection of equipment to busand or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Electrical work | Conn. of equip/bus single zebra/panther | As per relevent standard specification | 224 | EA | 2016
208 | SWR20308 | 4 | Sub Transportation of 9.1M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 1629.16
209 | SWR12402 | 1 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 48
210 | SWR12421 | 1 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 48
211 | SWR12416 | 2 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 4
212 | SWR10631 | 2 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 4
213 | SMR11482 | 2 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 6972
214 | SWR10357 | 2 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 2468.4
215 | SWR34671 | 2 | Providing of collar rings of 450mm dia at 4 pole structure | Electrical work | Collar/ Rings of 450mm dia | As per relevent standard specification | 250 | EA | 500
216 | SMR11485 | 35 | Supply of earthing GI Flat 25X3 mm including material | Electrical work | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 3675
217 | SWR10239 | 3 | Loading of 33 KV AB Switch Conventional 400/800 Amp | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 378
218 | SWR10557 | 3 | Unloading of 33 KV AB Switch Conventional 400/800 Amp | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 237
219 | SMR12315 | 3 | Supply of 33KV 800A DB Break AB Switch | Electrical work | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 121976.34
220 | SMR25233 | 4 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 12437.64
221 | SMR25207 | 30 | Supply of MS Angle 65X65X6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 1717.5
222 | SMR22745 | 500 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 28725
223 | SMR12321 | 120 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 6770.4
224 | SWR10393 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 9600 | 1 pole AB Switch
225 | SMR11488 | 6 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 705
226 | SWR10206 | 0.26 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 57.46
227 | SWR10524 | 0.26 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 48.1
228 | SWR10134 | 0.26 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 152.7552
229 | SMR11484 | 3 | Supply of C I earth pipe of size 50mm dia, 2 mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 50mm dia 2m long | As per relevent standard specification | 2441 | EA | 7323
230 | SWR11222 | 6 | Loading/Unloading of C I earth pipe of size 80/50mm dia, 2 mtrs long for earth electrode | Electrical work | Load/Unload-CI pipe 80/50 mm dia 2mt L | As per relevent standard specification | 18 | EA | 108
231 | SWR34671 | 3 | Providing of collar rings of 450mm dia at 4 pole structure | Electrical work | Collar/ Rings of 450mm dia | As per relevent standard specification | 250 | EA | 750
232 | SMR11485 | 30 | Supply of earthing GI Flat 25X3 mm including material | Electrical work | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 3150
233 | SWR10238 | 3 | Loading of 11 KV AB Switch Conventional 200/400 Amp | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 240
234 | SWR10556 | 3 | Unloading of 11 KV AB Switch Conventional 200/400 Amp | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 240
235 | SMR12317 | 3 | Supply of 11KV 400A DB Break AB Switch | Electrical work | S-11KV 400A DB Break AB Switch | As per relevent standard specification | 18150 | EA | 54450
236 | SMR25206 | 36 | Supply of MS Angle 50x50x6 | Electrical work | S-MS Angle 50x50x6 | As per relevent standard specification | 58.15 | KG | 2093.4
237 | SMR25205 | 120 | Supply of MS Channel 75x40 mm | Electrical work | S-MS Channel 75x40 mm | As per relevent standard specification | 58.45 | KG | 7014
238 | SMR12322 | 50 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 2825
[6 empty] | Electrical Total |  |  | 5445218.2224
1 | SWR34179 | 56 | Levelling the site with the help of JCB including cost, conveyance of all materials,hire charges etc complete for finished item of work. | JCB | Hire-JCB to Level & Clear the Site | As per relevant standard specifiction | 2164.1 | H | 121189.6
2 | SWR33015 | 100.79 | Earth Work Mass Excavation (Ordinary soil) to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions, labour and material charges etc., complete as directed by the engineer-incharge. | Earth Work | Excavation in Ordinary Soil | As per relevant standard specifiction | 347 | M3 | 34974.13
3 | SWR33028 | 21.17 | PCC (1:4:8) for levelling course using 40mm size hard broken Granite stone including cost and conveyance of all materials, HBG metal for foundations and leveling course and as directed by the Engineer- in - charge etc complete for finished item of work. | Concrete | PCC with 40mm Metal (1:4:8) | As per relevant standard specifiction | 4056 | M3 | 85865.52
4 | SWR33041 | 124.05 | CRS masonry in CM (1:6) using Hard Granite Stones including cost and conveyance of all materials, seignorage charges, labour charge for construction and for dressing stones to required size and shape, dewatering, scaffolding, cutting for all leads and lifts, all incidental charges etc .complete for finished item of work as directed by the Engineer - in - charge. | Masonry | CRS Masonary CM(1:6) 2nd Sort | As per relevant standard specifiction | 4435 | M3 | 550161.75
5 | SWR33068 | 19.4 | Construction of brick masonary in CM(1:6) including cost and conveyance of all materials, labour charges etc. complete for finished item of work | Masonry | Brick Masonary in CM(1:6) GFloor | As per relevant standard specifiction | 7623 | M3 | 147886.2
6 | SWR33052 | 780.26 | Supplying and filling with borrowed gravel, watering, ramming, consolidating thoroughly complying with the standard specification including cost and conveyance of all materials, labour charges,hire charges of machnery,with all leads and incidental charges etc complete for finished item work | Earth Work | S&Filling with Borrowed Gravel | As per relevant standard specifiction | 435 | M3 | 339413.1
7 | SWR33098 | 6.53 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (a) Footings | RCC | RCC Footing: M20Gr, Steel Centering | As per relevant standard specifiction | 8195 | M3 | 53513.35
8 | SWR33100 | 4.77 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (b) Columns | RCC | RCC Column GF: M20Gr, Steel Centering | As per relevant standard specifiction | 10890 | M3 | 51945.3
9 | SWR33099 | 1.65 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (c) Plinth Beams | RCC | RCC Plinth Beam: M20Gr, Steel Centering | As per relevant standard specifiction | 10615 | M3 | 17514.75
10 | SWR33107 | 0.72 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (d) Lintels | RCC | RCC Lintel GF: M20Gr, Steel Centering | As per relevant standard specifiction | 11050 | M3 | 7956
11 | SWR33114 | 11.7 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (e) Sunshade | RCC | RCC Sunshade GF: M20Gr, Steel Centering | As per relevant standard specifiction | 1160 | M2 | 13572
12 | SWR33121 | 2.35 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (f) Roof Beams | RCC | RCC Roof Beam GF: M20Gr, Steel Centering | As per relevant standard specifiction | 10626 | M3 | 24971.1
13 | SWR33128 | 6.94 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (g) Slab of 130 mm thick | RCC | RCC Roof Slab GF: M20Gr, Steel Centering | As per relevant standard specifiction | 10177 | M3 | 70628.38
14 | SWR33144 | 2.2 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) / Mild steel (MS) steel bars (Fe 415/ Fe 500 grade as per IS 1786-1979) of different diameters for RCC works complete for finished item of work in all floors.( APSS No.126) | Steel | Reinforcement Steel Fe 415/500 | As per relevant standard specifiction | 76127 | TO | 167479.4
15 | SWR33163 | 317.06 | Providing plastering of 20mm thick to all uneven faces of walls and ceiling of superstructure in two coats with base coat in CM 1:6 of 16mm thick and top coat in Cm 1:4 4mm thick with dubara sponge finish | Plastering | Plastering 20mm (16mm+4mm)GFloor | As per relevant standard specifiction | 410 | M2 | 129994.6
16 | SWR33184 | 136.5 | Raised pointing in CM(1:3) including curing, cost and conveyance of all materials and labour charges for complete item of work. | Pointing | Raised Pointing to CRS Masonary CM(1:3) | As per relevant standard specifiction | 94 | M2 | 12831
17 | SWR33156 | 54.87 | Providing impervious coat over RCC roof slab surfaces to requried slopes with 20mm thick in CM 1:3 pro mixed with approvaled brand of water proffing compound as the raet of 1 kg per bag of cement inclding cost and conveyance of all materials | Roof plastering | Impervious Coat 20mm CM(1:3) GFloor | As per relevant standard specifiction | 439 | M2 | 24087.93
18 | SWR33264 | 5.7 | Supply and fixing of Flush type Doors with 35mm Thick Flush Shutters with Bondwood solied Block Board Type Faced on Both the sides with Commercial Type Plywood for finished item work as directed by the Engineer - in- charge. | Doors | S&F MT Wood Frame & Door-Laminate | As per relevant standard specifiction | 6799.02 | M2 | 38754.414
19 | SWR33277 | 5.76 | Supply and Fixing of Aluminium sliding windows with fixed glass panels using aluminium sections 62x32x1.2mm providing 5mm plain glass fixed to frame with beading gasket and glazing clips with all accessories,locking arrangements including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Windows | S&F Aluminium Window | As per relevant standard specifiction | 3381.54 | M2 | 19477.6704
20 | SWR33310 | 6.25 | Supplying and fixing of MS safety grill with peripheral frame of ISA 25x25x4mm and horizontal & vertical 8mm square rods and including cost and coveyance of all mateirals with all leads and lifts, labour charges, painting charges complete for finished item of work | Window grills | S&F of MS Safety Grill | As per relevant standard specifiction | 2539 | M2 | 15868.75
21 | SWR33219 | 26.5 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and approved size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and pointing with cement, labour etc, complete for finished item of work. | Flooring | Polished Shabad Flooring 20mm CM(1:3) | As per relevant standard specifiction | 659 | M2 | 17463.5
22 | SWR33236 | 6.94 | Providing skirting with tandoor blue slabs including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Flooring | Polished Shabad Skirting CM(1:3) | As per relevant standard specifiction | 726 | M2 | 5038.44
23 | SWR33029 | 40.07 | Plain Cement contrete - Nominal Mix (1:3:6) using 40 mm metal with concrete mixture including cost and conveyance of all materials labour charges etc. complete for finished iitem of work and as directed by the engineer-in-charge. | Concrete | PCC with 40mm Metal (1:3:6) | As per relevant standard specifiction | 4358 | M3 | 174625.06
24 | SWR33030 | 6.75 | PCC(1:2:4) using 10 to 12 mm aggregate including cost and conveyance of all materials labour charges etc., complete for finished iitem of work and as directed by the engineer-in-charge. | Concrete | PCC with 20mm Metal (1:2:4) | As per relevant standard specifiction | 5473 | M3 | 36942.75
25 | SWR33057 | 65.92 | Supply and Spreading of 20mm machine crushed metal including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Metal | S&Spreading of 20mm HBG Metal | As per relevant standard specifiction | 1514 | M3 | 99802.88
26 | SWR33403 | 110 | Supply and fixing of fencing of welded wire mesh (1" x 2") of 3mm dia with support channels of 75x 40mm and angles around of 30x30x3 mm including cost and conveyance of all materials, fabrication charges, painting charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Welded mesh | S&F MS Security Fencing Mesh (2"X2") | As per relevant standard specifiction | 2042 | M2 | 224620
27 | SWR33333 | 107.9 | Painting with two coats of OBD over a coat of primer including cost and conveyance of all materials ,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Painting | Painting with OBD 2Coats+Primer | As per relevant standard specifiction | 109.9 | M2 | 11858.21
28 | SWR33336 | 153 | Painting with two coats of ACE paint over a coat of primer including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Painting | Painting SnowCem/Apex 2 Coats+Primer | As per relevant standard specifiction | 195.91 | M2 | 29974.23
29 | SWR33329 | 196.5 | Painting with lovely cem three coats including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Painting | Painting with SuryaCem of 3 Coat | As per relevant standard specifiction | 70.47 | M2 | 13847.355
30 | SWR33442 | 25 | S&F Conceal PVC Pipe 32mm dia in Slab including cost and conveyance of all material and labour charges complete for finished item of work | Electrification | S&F Conceal PVC Pipe 25mm dia in Slab | As per relevant standard specifiction | 85 | RMT | 2125
31 | SWR33441 | 15 | S&F Conceal PVC Pipe 20mm dia in Wall including cost and conveyance of all material and labour charges complete for finished item of work | Electrification | S&F Conceal PVC Pipe 25mm dia in Wall | As per relevant standard specifiction | 89 | RMT | 1335
32 | SWR33457 | 15 | Wiring with 2X1.0 Sqm(14/.3mm) PVC insulated flexiable copper cable in the existing metalic/Non metalic conduit pipe with 6A mini modular SP switch, mounted on metalic box covereds with appropriate front plate modules etc ceiling rose including cot and conveyance of all mateials, labour charges complete for light points, bell points and fan points in non residential builsing except circuit moving finished in all types masonary as directed by department. | Electrification | S&F Modular Switch LP,FP,EFP for NRBuild | As per relevant standard specifiction | 580 | EA | 8700
33 | SWR33461 | 2 | Supply and fixing of 6A 3/2 pin flush type plug socket with 6A flush type marked switch control on a common board with earth continuity including wire leads earth connections along with all labour charges etc. complete | Electrification | S&F Modular 3/2pin 6A Sockets | As per relevant standard specifiction | 469 | EA | 938
34 | SWR33464 | 2 | Supply and fixing of 16A 3pin flush type plug socket and 16A flush type fuse unit and 16A switch control. | Electrification | S&F Modular 3pin 16/6A Sockets | As per relevant standard specifiction | 437 | EA | 874
35 | SWR33484 | 4 | Supply and fixing of slanting holders with 100W bulb with all connections and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F Batten Holder | As per relevant standard specifiction | 116 | EA | 464
36 | SWR33545 | 4 | Supply and fixing of patty type tube light fitting with 4' 0" - 40W tube light,40W copper choke,starter,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F 20W LED Retro Tube Light | As per relevant standard specifiction | 868 | EA | 3472
37 | SWR33494 | 90 | Supply and run of 2 of 14/.3mm(1.00Sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | S&R 2 of 14/0.3mm (1.0sqmm) (FR) | As per relevant standard specifiction | 48 | RMT | 4320
38 | SWR33497 | 30 | Supply and run of 2 of 36/0.3 (2.5sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | S&R 2 of 36/0.3mm (2.5sqmm) (FR) | As per relevant standard specifiction | 95 | RMT | 2850
39 | SWR33520 | 1 | SPN Distribution board with IP-20 protection suitable for single phase 40A DP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 4Nos as out going MCBs in sheet steel enclosure including connections and cost of all material labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F 8wySPNDB IP-20,10kA-6-32A SPMCB 4No | As per relevant standard specifiction | 5038 | EA | 5038
40 | SWR33596 | 1 | Providing independent earthing for main switches,IC cutouts and motors using 40mm. Dia. B-class G.I.Pipe of 2.5' length duly providing 12mm. Dia. 6No. Holes and required bolts,nuts and washers,including filling with equal preparation of salt and charcoal in layers and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | Provd-Independent Earthing | As per relevant standard specifiction | 4891 | EA | 4891
41 | SWR33597 | 15 | Supply and run of No.8 SWG Copper wire including cost of all accessories and labour charges etc., Complete | Electrification | S&R No.8 SWG Copper Wire | As per relevant standard specifiction | 140 | RMT | 2100
42 | SWR33563 | 2 | Supply and Fixing of 48" ceiling fan of bajaj make(or equivalent make) including cost material,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F 1200mm (48'') Sweep Ceiling Fan | As per relevant standard specifiction | 2215 | EA | 4430
43 | SWR33224 | 15.8 | Supply and fixing of ceramic tiles fantacy for dadoing including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Flooring | Ceramic Tile Flooring 20mm CM(1:3) | As per relevant standard specifiction | 759 | M2 | 11992.2
44 | SWR34311 | 1 | Supply and fixing of 580mm x 440mm long Orissa pan of Parry, Neycer or Hindhusthan, make with 'P' or 'S' trap etc complete for finished item of work and as directed by the engineer-in-charge. | Sanitary | S&F Orissa Pan WC 580mmx440mm | As per relevant standard specifiction | 2178 | EA | 2178
45 | SWR34386 | 2 | Supply and Fixing 4" PVC floor trap including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F Floor Trap (Bell Mouth) 110mm | As per relevant standard specifiction | 269 | EA | 538
46 | SWR34382 | 2 | Supply,fixing 90mm dia. PVC Plain Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F 90mm dia Plain Bend PVC/SWR Pipe | As per relevant standard specifiction | 84 | EA | 168
47 | SWR34385 | 1 | Supply,fixing 90mm dia. PVC Door Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F 75mm dia Door Bend PVC/SWR Pipe | As per relevant standard specifiction | 81 | EA | 81
48 | SWR34286 | 1 | S&Fixing 150mm x 100mm SWG gully traps Ist class grating & constg brick masonry in CM (1:6) prop inter mediate chamber and fitted with CI frame etc complete. | Sanitary | S&F 150mmx100mm SWG Gully Trap | As per relevant standard specifiction | 749 | EA | 749
49 | SWR34377 | 6 | Supply and Fixing 4" dia 3M Single socket PVC pipe including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F 110mm dia 3M 1Socket PVC/SWR Pipe | As per relevant standard specifiction | 422 | RMT | 2532
50 | SWR34453 | 1 | Supply and Fixing 4" dia PVC cowl including labour charges etc. complete for finished item of work. | Plumbing | S&F 4" dia PVC Cowl | As per relevant standard specifiction | 23 | EA | 23
51 | SWR34444 | 1 | Construction of soak pit with 4' dia RCM rings upto a depth of 6' including cost and conveyance of all materials as directed by the engineer-in-charge. | Sanitary | Construct- 4' dia & 5' Ht Soak Pit | As per relevant standard specifiction | 2950 | EA | 2950
52 | SWR34361 | 20 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) 15.90mm OD Pipe - SDR 11 | Plumbing | S&F 15.90mm OD CPVC Pipe-SDR 11 | As per relevant standard specifiction | 239 | RMT | 4780
53 | SWR34362 | 100 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) 22.20mm OD Pipe - SDR 11 | Plumbing | S&F 22.20mm OD CPVC Pipe-SDR 11 | As per relevant standard specifiction | 313 | RMT | 31300
54 | SWR34363 | 100 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007) 28.60mm OD Pipe - SDR 11 | Plumbing | S&F 28.60mm OD CPVC Pipe-SDR 11 | As per relevant standard specifiction | 410 | RMT | 41000
55 | SWR34344 | 18 | Supply and fixing of 15mm dia. SS coated taps including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F-15mm GM/Bronze Ball Valve | As per relevant standard specifiction | 230 | EA | 4140
56 | SWR34345 | 1 | Supply and fixing of 20mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F-20mm GM/Bronze Ball Valve | As per relevant standard specifiction | 331 | EA | 331
57 | SWR34346 | 2 | Supply and fixing of 25mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F-25mm GM/Bronze Ball Valve | As per relevant standard specifiction | 466 | EA | 932
58 | SWR34329 | 3 | Supply and fixing of 12.7mm bib tap Indian make including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F-15mm Bib Tap 400gm Full turn | As per relevant standard specifiction | 271 | EA | 813
59 | SWR34375 | 500 | Providing and placing on Terrace polyetheylene water storage tank with double layer approved brand and manufacture with cover complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F Polyethylene Water Storage Tank | As per relevant standard specifiction | 10 | L | 5000
60 | SWR34740 | 1 | Supply of steel table of size 4'x2.5'x30" with 18 mm plywood fixed with rubber beeding with drawers on right side with automatic locking arrangements etc complete for finished item of work and as directed by the engineer-in-charge. | Furniture | S-3x2ft Office Table | As per relevant standard specifiction | 5000 | EA | 5000
61 | SWR33857 | 1 | Supply of 'S' type chair with arms teakwood frame with seat back 's' type on G.I pipe including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Furniture | Supply of S-Type Chair | As per relevant standard specifiction | 3850 | EA | 3850
62 | SWR33858 | 2 | Supply of P V C chairs of Neelkamal of approved quality & make including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Furniture | Supply of PVC Chair | As per relevant standard specifiction | 1150 | EA | 2300
63 | SWR33406 | 150 | S&Fixing of R.C.C fencing poles of size 0.115mx0.115mx2.7m including cost & conveyance of all materials,labour chargesv etc complete for finished item of work. | Fencing | S&F RCC Fencing Pole 0.115mx0.115mx2.7m | As per relevant standard specifiction | 1411 | EA | 211650
64 | SWR33405 | 76 | Providing and fixing 1.80 metre long RCC fencing posts with 6 mm bar bibs of pole size 0.1x0.1x1.8m in pit size of 0.45x0.45x0.45 and filled with PCC (1:4:8) using 20mm metal including cost & conveyance of all materials, labour charges etc complete for finished item of work. | Fencing | S&F RCC Fencing Pole 0.1mx0.1mx1.8m | As per relevant standard specifiction | 1269 | EA | 96444
65 | SWR33407 | 275 | S&Fixing of barbed wire 8 straight strands and 2 cross strands including cost & conveyance of all materials, labour charges etc complete for finished item of work. | Fencing | S&F Barbed Wire 8H & 2Cross | As per relevant standard specifiction | 260.05 | M | 71513.75
66 | SWR33421 | 1.35 | Supply and Fixing of Substation name board of size 5'x3' iron sheet with angle frame and channel supports of size 75x40mm, 8' height including concreting of channel supports and painting with enamel paint complete. | Name board | S&F MS Board | As per relevant standard specifiction | 4542.3 | Sqm | 6132.105
67 | SWR33423 | 1.8 | S&F Poly Vinyl Acrylic Board including cost and conveyance of all labour and material charges complete. | Name board | S&F Poly Vinyl Acrylic Board | As per relevant standard specifiction | 1930.48 | Sqm | 3474.864
68 | SWR33608 | 1 | Geophysical Investgation Charges | Borewell | Geophysical Investgation Charges | As per relevant standard specifiction | 5000 | EA | 5000
69 | SWR33609 | 90 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work. 0 to 90M | Borewell | Drilling-165mm Bore Well 0 to 90M | As per relevant standard specifiction | 336 | M | 30240
70 | SWR34830 | 30 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work. 90m to 120M | Borewell | Drill-165mm Bore Well 90M to 120M | As per relevant standard specifiction | 369 | M | 11070
71 | SWR34831 | 30 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work. 120m to 150M | Borewell | Drill-165mm Bore Well 120M to 150M | As per relevant standard specifiction | 394 | M | 11820
72 | SWR33611 | 30 | Suppy & fixing of 160 mm dia. 6 kg/cm2 PVC casing pipe including cost and conveyance of all materials labour charges etc complete for finished item of work | Borewell | S&F 160mm dia PVC Casing | As per relevant standard specifiction | 844 | M | 25320
73 | SWR33636 | 1 | Supply & fixing of 2HP Multistage submersible motor pumpset of approved make (Texmo or equivalent type) including cost and conveyance of all materials etc complete for finished item of work. | Borewell | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | As per relevant standard specifiction | 34237 | EA | 34237
74 | SWR33641 | 60 | S&R 3C 2.5sqmm Flat Copper Cable including cost of all materials and labour charges for finished item of work. | Borewell | S&R 3C 2.5sqmm Flat Copper Cable | As per relevant standard specifiction | 190 | EA | 11400
75 | SWR33644 | 1 | Supply and fixing of Panel box and starter including cost of all materials and labour charges for finished item of work. | Borewell | S&E D.O.L Starter 250V Single Phase | As per relevant standard specifiction | 1040 | EA | 1040
76 | SWR34203 | 1 | Supply & fixing of Flange Clamps including cost of all materials and labour charges for finished item of work. | Borewell | Supply & ixing of Flange Clamps | As per relevant standard specifiction | 182 | EA | 182
77 | SWR34410 | 178 | Suppy & fixing of HDPE pipe 1.5" dia. including cost & conveyance of all materials labour charges etc complete for finished item of work. | Borewell | S&F-HDPE Pipe 40mm dia 16kg/sqcm-SDR 9 | As per relevant standard specifiction | 160 | Rmt | 28480
78 | SWR34470 | 97.7 | Seigniorage Charges - Sand | Seigniorages | Seigniorage Charges - Sand | As per relevant standard specifiction | 40 | M3 | 3908
79 | SWR34471 | 96.5 | Seigniorage Charges - Metal | Seigniorages | Seigniorage Charges - Metal | As per relevant standard specifiction | 97.5 | M3 | 9408.75
80 | SWR34472 | 780.26 | Seigniorage Charges - Gravel | Seigniorages | Seigniorage Charges - Gravel | As per relevant standard specifiction | 30 | M3 | 23407.8
[8 empty] | Civil Total | 3289179.8384
[8 empty] | Elec & Civil Total | 8734398.0608

## 6. Sadasivapet SS
Sadashivapet SS Schedules(WBS No: S-1383-90-06-01-01-001).
Name of the work:Revised estimate for erection of new 33/11 KV SS with connected 33 KV and 11 KV lines at Sadashivpet (Vg) in Sadashivpet (M)of Sangareddy Division of Sangareddy Circle .
S.No | SSR Codes | Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR10105 | 39 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 23400
2 | SWR10343 | 31 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 74400
3 | SWR10356 | 27.28 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt)*31 = 27.28 cu mtr with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 179475.12
4 | SWR11890 | 0.96 | ERECTION OF S.S. STRUCTURE: Coping of 0.45x0.45x0.45Mt with 1:8 slope Using form boxes (0.031Cumt.) | Civil work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | M3 | 3737.28
5 | SWR11331 | 31 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of poles with two coats of white cement (including cost of paint). | Electrical work | Paint-9.1M PSCC Poles as desc SSR | As per relevent standard specification | 485 | EA | 15035
6 | SWR11889 | 5.5 | Fabrication of 100 X 50mm MS Channel for formation of 11kV and 33kV bays: Fabrication and erection of M.S,Channel 100x50mm for forming of 33KV & 11 KV Bays as per standard specifications to facilitate stringing of bus, erection of LA sets, AB Switches bolts & Nuts etc. including painting with one coats of red oxide and two coats of Aluminium paint. GI bolts&nuts shall be used. | Electrical work | Fabr & Erect-MS Chnl 100x50mm for SS Bay | As per relevent standard specification | 6600 | TO | 36300
7 | SWR10404 | 115 | Erection of 33kV and 11kV Strung Bus with Panther (200Sqmm) ACSR Conductor: Erection of 33kV and 11kV Bus over the Substation structures with 200sqmm Panther ACSR conductor and giving Jumpers to connect the Switch gear by providing the suitable T clamps and round clamps suitable to Post type insulators & Insulators. | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 37683.2
8 | SWR10392 | 2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 9000
9 | SWR10393 | 10 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 32000
10 | SWR11742 | 3 | Supply & erection of 11 kV 400 A convential single(1/3) phasing AB switches.includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company | Electrical work | S&E-400A 11KV ABSwth Conv 1ph(1/3) in SS | As per relevent standard specification | 4232 | EA | 12696
11 | SWR21240 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 33kv | As per relevent standard specification | 781 | EA | 1562
12 | SWR21241 | 4 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 11kv | As per relevent standard specification | 507 | EA | 2028
13 | SWR10881 | 12 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 1704
14 | SWR23224 | 16.46 | Excavation of pit in all types of soils of size 2.2x2.2x0.85Mts.for Construction of Plinths for VCB (33KV & 11 KV ) | Earth work | Excavate-Pit for 33KV VCB | As per relevent standard specification | 331 | M3 | 5448.26
15 | SWR20685 | 22.24 | Providing of Base concreting (2.2x2.2x0.15 Mts) = 0.726 *4 = 2.904 with 1:3:6 Concrete mix. Using form boxes, Providing of Concreting (2.2x2.2x1.0) = 4.84 *4 = 19.36 Cu mts with 1:3:6 Cocrete mix. Plastering of the plinth for smooth finishing with 12mm thick 1:3 cement motor and providing two coats white washing for part of the plinth above groung level. | Civil work | Cement concrete with 40MM metal VCB plin | As per relevent standard specification | 5160 | M3 | 114758.4
16 | SWR10461 | 4 | Erection of Switchgear complete for 11 kV VCB includes Assembling the VCB Structures and mounting the VCBs over the already erected foudation including wiring of Breaker Control Panel/CTs, erection of CTs and control pannel providing Jumpers. | Electrical work | Erection of 11kv VCB | As per relevent standard specification | 12000 | EA | 48000
17 | SWR10396 | 2 | Erection of 33KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 1760
18 | SWR10397 | 1 | Erection of 11 KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 11kv LA stn type incl earthing | As per relevent standard specification | 559 | SET | 559
19 | SWR10398 | 3 | Erection of 11 KV Lightening Arrestors line type complete including jumpering. | Electrical work | Erect of 11kvLA line type incl earthing | As per relevent standard specification | 505 | SET | 1515
20 | SMR11607 | 1 | Supply of 33kv HG fuse set including providing of jumpers | Electrical work | S-33KV HG Fuse Set excl Ins & Chnl | As per relevent standard specification | 6431 | SET | 6431
21 | SWR10394 | 1 | Erection of 33kv HG fuse set including providing of jumpers | Electrical work | Erect. of 33kv HG Fuseset incl earthing | As per relevent standard specification | 1331.81 | SET | 1331.81
22 | SMR11608 | 1 | Supply of 11kv HG fuse set including providing of jumpers | Electrical work | S-11KV HG Fuse Set | As per relevent standard specification | 1733.75 | SET | 1733.75
23 | SWR10395 | 1 | Erection of 11kv HG fuse set including providing of jumpers | Electrical work | Erect. of 11kv HG Fuseset incl earthing | As per relevent standard specification | 740.52 | SET | 740.52
24 | SMR11482 | 22 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 76692
25 | SWR10357 | 22 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 27152.4
26 | SWR10920 | 500 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification.75x8 mm MS flat for Earth mat and connecting to electrodes | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 32500
27 | SWR10919 | 950 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification. 50x6 mm MS flat for raisers, double flat shall be run for structure poles raisers & equipment earthing. | Electrical work | Earthing for raisers of SS Flat 50x6 mm. | As per relevent standard specification | 41 | RMT | 38950
28 | SMR40033 | 2 | Providing of double earthing for neutral with flexible copper jumpers of adequate size including arrangement by fixing M.S.Channel 100x50mm. | Electrical work | SupCU Flexi jumper for Power T/F Neutral | As per relevent standard specification | 4725 | EA | 9450
29 | SWR11771 | 4 | Erection of 24 Volts Battery along with Charger on the VCB plinth and giving DC supply to VCB's. | Electrical work | Erect-24V Batery with Chrgr incl grot-SS | As per relevent standard specification | 1050 | EA | 4200
30 | SWR11474 | 600 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable includes excavation of earth and back filling with sand and earth in alternate layers . The cable termination shall be made by providing proper size lugs and shall be identified with colours. | Electrical work | Laying-4 core cable | As per relevent standard specification | 15 | RMT | 9000
31 | SWR10463 | 1 | Erection of 25 kVA Three phase Station Transformer on the Substation Structures and giving jumpers/connections on HT side to the 11kV bus. Belting angle shall be provided both sides of DTR for securing DTR firmly in position. | Electrical work | Erection of Three Phase DTRs | As per relevent standard specification | 1139.95 | EA | 1139.95
32 | SMR40045 | 1 | Supply of AC Panel Board includes: Fixing of 1 No.100A, MCCB, 10kA capacity of any standard make including material cost. Fixing of suitable panel box 3x3x1 with M.S.Sheet of 16 SWG with front door compartments inclusive of material cost & powder coating (with C Channel ). Fabrication of panel Fixing of 96x96mm analog voltmeter with VSS switch Fixing of 20A HRC fuse Fixing of 3 phase supply indicator kwith HRC fuses Supply and fixing of 6 Sqmm copper flexible wire (PVC) Fixing of Stud type TBs for outgoing feeder Fixing of Epoxy bus supports | Electrical work | Supply of AC Supply panel complete | As per relevent standard specification | 42000 | EA | 42000
33 | SMR40044 | 1 | Supply of DC Panel Board Fixing of suitable panel box of size 6'x6'x1' with M S sheet of 16 SWG with back doors (4'x6') and on front side with provision to fix up bakelite hylam sheet size of 4'x6' including cost of the panel with powder coating. Fixing of best quality of angles for panel. Fixing of C Channelfor panel. Fabrication of control panel including making suitable holes and board Fixing of Stud type TBs for outgoing feeder Fixing of 24V DC pilot lamps of standard make Fixing of healthy trip push buttons with LED lamp Fixing of plain switches for alarm acceptance and for PTR signal Fixing of ON/OFF push buttons Fixing of digital volt meter for 11kV Fixing of VSS of standard make, Fixing of Engraved AL plates for Alarm panel of various VCB Laying of 2.5Sqmm copper flexible wire for internal wiring . Fixing of digital frequency meter Fixing of Copper lugs and ferrules for internal wiring. Fixing of 4" Gang bells 24V DC Fixing of flow diagram with rading strip Fixing of HRC fuse units | Electrical work | Supply of DC Anunc.relay panel 8 feeders | As per relevent standard specification | 42500 | EA | 42500
34 | SWR11893 | 2 | fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supplied by tenderer. | Electrical work | Erect-Contrl/Relay, AC, Announ. Panels | As per relevent standard specification | 1930 | EA | 3860
35 | SWR10342 | 8 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 12000
36 | SWR10956 | 8 | Fixing of Metal halide/LED lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5M GI pipe complete. | Electrical work | Fixing of LED/Metal halide complete. | As per relevent standard specification | 1268 | EA | 10144
37 | SWR20028 | 8 | Supply and Fixing of junction box and Providing with proper Fuse protection and required glauds suitable for Cable Terminations. The box shall be fixed on the pole. | Electrical work | 33/11kv S.S Yard lighting junction box | As per relevent standard specification | 351.9 | EA | 2815.2
38 | SWR20526 | 1 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply & fixing of marshall box | As per relevent standard specification | 3085.5 | EA | 3085.5
39 | SMR40088 | 1 | Supply and fixing of filled sand bucket set complete (4 Nos. Buckets) with stand to mount fire buckets. | Electrical work | Sup Fire Buckets Stand with Buckets | As per relevent standard specification | 1386 | SET | 1386
40 | SMR40087 | 2 | Supply and fixing of CO2 Cylinder set as per IS2878 Specifications. | Electrical work | Sup TrollyMounted Co2 Cylinders(IS-2878) | As per relevent standard specification | 9240 | EA | 18480
41 | SWR11895 | 1 | Supplying and fixing of feeder indicator board to each of the 3Nos feeder breakers and LV breaker, danger boards made of 1'x1' and properly mounted on the structures. The letters written on the borad shall be 1.5"size with blue colour and background shall be of white colour | Electrical work | S&F-33/11KV SS Feeder Indicator Board | As per relevent standard specification | 551 | SET | 551
42 | SWR20032 | 1 | Supply and fixing of wooden board of size 3'x2'.5'indicating the layout of the Switch yard. | Electrical work | Sup &fix of board ind Switchyard layout | As per relevent standard specification | 1654 | EA | 1654
43 | SMR40086 | 1 | Supply and Erection of Permanent Name Board of on 3'x4' steel sheetmounted on steel frame as described in Specification. | Electrical work | Sup 33/11kv S.S Permanent name board | As per relevent standard specification | 10238 | EA | 10238
44 | SMR40076 | 1 | Supply of Digital clamp meter. | Electrical work | Supply of Digital clamp meter. | As per relevent standard specification | 2888 | EA | 2888
45 | SMR40064 | 1 | Supply of Rechargeable LED torch light of Standard make | Electrical work | Sup Rechargeable LED torch light. | As per relevent standard specification | 1733 | EA | 1733
46 | SMR40063 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box containing ‘D’Spanners from size 6 to 54, Hammer small and big size, Ring spanners from 6 to 28, Adjustable spanner, Pipe wrench, Cutting Plier, Nose plier, Tester, insulated Screw drive. | Electrical work | SupTaparia Tool kit complete as per Spec | As per relevent standard specification | 4925 | SET | 4925
47 | SWR22090 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Electrical work | Sup& fix safety inst/SS Op. inst board | As per relevent standard specification | 2205 | EA | 2205
48 | SMR11598 | 8 | Supply of 25 W LED lamp with fitting of philips make | Electrical work | S-25W LED fixture set | As per relevent standard specification | 3200 | EA | 25600
49 | SMR12378 | 1 | Supply of Alluminum Ladder(20 feet) | Electrical work | S-10ft Aluminium Ladder | As per relevent standard specification | 1654 | EA | 1654
50 | SMR40075 | 1 | Supply of Megger (2000 ohms, 0-2.5kv) | Electrical work | Supply of Earth megger (1000v) | As per relevent standard specification | 8085 | EA | 8085
51 | SMR11599 | 4 | Supply of Earth Discharging Rod 10' length. | Electrical work | S-Earth Rod 8ft Long 3mm Thick | As per relevent standard specification | 1000 | EA | 4000
52 | SMR11488 | 200 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 23500
53 | SMR11591 | 66 | Supply of PG clamps for panther 2 bolted 600 A | Electrical work | S-Al. alloy three bolted PG clamps 800A | As per relevent standard specification | 130 | EA | 8580
54 | SWR20029 | 350 | Supply and Laying of 2 core/4 core cable includes excavation earth and back filling with sand and earth in alternate layers as shown in the sketch. The cable termination shall be made by providing proper size of lugs at both ends of the cable termination. | Electrical work | 33/11kv S.S laying of 2/4core for light | As per relevent standard specification | 50 | M | 17500
55 | SWR20308 | 31 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 12625.99
56 | SWR20307 | 8 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 2172.16
57 | SWR11860 | 2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 5440.68
58 | SWR10150 | 10.5 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 6479.55
59 | SWR10206 | 10.5 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 2320.5
60 | SWR10524 | 10.5 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 1942.5
61 | SWR11220 | 350 | Loading and unwinding of Panther conductor | Electrical work | Load-Unwinding Panther conductor | As per relevent standard specification | 3 | M | 1050
62 | SWR11221 | 350 | Unloading of Panther conductor | Electrical work | Unload-Unwinding Panther conductor | As per relevent standard specification | 2 | M | 700
63 | SWR12416 | 2 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 4
64 | SWR10631 | 2 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 4
65 | SWR10618 | 2 | Loading of 33KV Metal parts bag of 25 nos | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 130
66 | SWR10632 | 2 | Unloading of 33 KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 130
67 | SWR10212 | 2 | Loading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators | Electrical work | LOADING of 11kv Pin/Post/Solid Core Insu | As per relevent standard specification | 1 | CRT | 2
68 | SWR10530 | 2 | Unloading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators | Electrical work | UNLOADING of 11kv Pin/Post/Solid Core In | As per relevent standard specification | 1 | CRT | 2
69 | SWR11701 | 600 | Loading of PVC Copper Control Cable 4 core and 10 core | Electrical work | Load-PVC Control Cable 10C | As per relevent standard specification | 1 | M | 600
70 | SWR11712 | 600 | Unloading of PVC Copper Control Cable 4 core and 10 core | Electrical work | UnLoad-PVC Control Cable 10C | As per relevent standard specification | 1.02 | M | 612
71 | SWR11691 | 1 | Loading of 3Ph 25KVA Distribution Transformer | Electrical work | Load-3Ph 25KVA DTR | As per relevent standard specification | 252 | EA | 252
72 | SWR11692 | 1 | UnLoading of 3Ph 25KVA Distribution Transformer | Electrical work | UnLoad-3Ph 25KVA DTR | As per relevent standard specification | 202 | EA | 202
73 | SWR10200 | 1 | Loading of 33/11 KV Current Transformers/ Potential Transformers | Electrical work | LOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 165 | EA | 165
74 | SWR10266 | 6 | Loading of 33 KV10 KA LAs Station type | Electrical work | LOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 41 | EA | 246
75 | SWR10584 | 6 | Unloading of 33 KV10 KA LAs Station type | Electrical work | UNLOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 35 | EA | 210
76 | SWR10265 | 9 | Loading of 11 KV10 KA LAs Line type | Electrical work | LOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 288
77 | SWR10583 | 9 | Unloading of 11 KV10 KA LAs Line type | Electrical work | UNLOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 288
78 | SWR10264 | 3 | Loading of 11 KV10 KA LAs Station type | Electrical work | LOADING of 11 KV,10 KA LAs Station type | As per relevent standard specification | 32 | EA | 96
79 | SWR10582 | 3 | Unloading of 11 KV10 KA LAs Station type | Electrical work | UNLOADING of 11 KV,10 KA LAs Station typ | As per relevent standard specification | 32 | EA | 96
80 | SWR10239 | 2 | Loading of 33 KV AB Switch Conventional 400/800 Amp | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 252
81 | SWR10557 | 2 | Unloading of 33 KV AB Switch Conventional 400/800 Amp | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 158
82 | SWR10238 | 10 | loading of 11 KV AB Switch Conventional 200/400 Amp | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 800
83 | SWR10556 | 10 | Unloading of 11 KV AB Switch Conventional 200/400 Amp | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 800
84 | SWR11224 | 4 | Loading and Unloading of 12V/24V Battery Set | Electrical work | Load/Unload-12V/24V Battery Set | As per relevent standard specification | 23 | EA | 92
85 | SWR10356 | 2.66 | ERECTION OF S.S. STRUCTURE: Providing of base concreting of size 0.76x0.76x0.15M with CC mix of ratio 1:3:6 Using form boxes(0.087Cu.Mt)x31 with 20mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 17500.14
86 | SWR10402 | 1 | Erection of 11kv Potential Transformer sets complete including jumpering. The LV side of the PT shall be provided with proper fuse protection mounted in separate marshalling boxwith proper size cable glands etc. The box shall be mounted on the Substation structure. | Electrical work | Erection of 11kv three phase PT s | As per relevent standard specification | 800 | SET | 800
87 | SWR10518 | 1 | Unloading of 33/11 KV Current Transformers/ Potential Transformers | Electrical work | UNLOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 128 | EA | 128
88 | SWR10674 | 1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
89 | SWR10356 | 4.32 | Concreting the location after erection of 8.0 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.6X0.6X1.5 Mts)* 8 = 4.32 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 28421.28
90 | SMR40067 | 2 | Supply of Hand Gloves | Electrical work | Supply of Hand Gloves | As per relevent standard specification | 289 | SET | 578
91 | SMR40071 | 2 | Supply of Safety Helmet of standard make | Electrical work | Supply of Safety Helmet of standard make | As per relevent standard specification | 231 | EA | 462
92 | SWR21750 | 2 | Supply and fixing of PT Marshalling box | Electrical work | Supply and fixing of PT Marshalling box | As per relevent standard specification | 1139.85 | EA | 2279.7
93 | SMR25233 | 31 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 96391.71
94 | SMR22745 | 5500 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 315975
95 | SMR12321 | 2350 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 132587
96 | SMR12322 | 2280 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 128820
97 | SMR25232 | 8 | Supply of 8.0Mtr PSCC 140 Kg Pole | Electrical work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 12640
98 | SMR12315 | 2 | Supply of 33KV 800A DB Break AB Switch | Electrical work | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 81317.56
99 | SMR12316 | 3 | Supply of 11KV 800A DB Break AB Switch | Electrical work | S-11KV 800A DB Break AB Switch | As per relevent standard specification | 30847.46 | EA | 92542.38
100 | SMR12317 | 7 | Supply of 11KV 400A DB Break AB Switch | Electrical work | S-11KV 400A DB Break AB Switch | As per relevent standard specification | 18150 | EA | 127050
101 | SMR25200 | 1 | Supply of LT Distribution Box (SMC) | Electrical work | S-LT Distribution Box (SMC) | As per relevent standard specification | 7797 | EA | 7797
102 | SWR10674 | 1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
103 | SMR40009 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for First coat of 1st GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 11995.5
104 | SWR10877 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 1st coat of Aluminium | Electrical work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 4680.5
105 | SMR40010 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for second coat of 2nd GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 7111.5
106 | SWR10879 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 2nd coat of Aluminium | Electrical work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 2651
107 | SWR22092 | 2.01 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 1537.65
108 | SWR10107 | 3 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11.0 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 2100
109 | SWR10109 | 37 | Excavation of Pole pits of size 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") 1.94 cum for spun Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In Hard Gravel and Hard murram not requiring blasting. | Earth work | EXCAVATION OF PIT(3.0" x 3.0" x 7.6") | As per relevent standard specification | 842.78 | EA | 31182.86
110 | SWR11039 | 10 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11.0 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In Hard Gravel and Hard murram not requiring blasting. | Earth work | EXCAV. OF PIT HARD W/O Blast 0.76 x 0.76 x 1.83 M | As per relevent standard specification | 840 | EA | 8400
111 | SWR10350 | 37 | Erection of spun pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Spun poles 12.5 Mtrs / 12.9Mtrs PSCC | Electrical work | Erection of Spun pole 12.5Mt | As per relevent standard specification | 4115.7 | EA | 152280.9
112 | SWR10978 | 17 | Erection of 11 M long PSCC pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 70809.76
113 | SWR10343 | 6 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 14400
114 | SWR10981 | 10 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Horizontal Cut point for 33 KV line | As per relevent standard specification | 1759.5 | EA | 17595
115 | SWR10356 | 28.88 | Concreting the location after erection of 12.5 mt spun pole/11.0 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.76X0.76X2.5 Mts)* 20 = 28.88 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 190001.52
116 | SWR10366 | 2.01 | Paving of the 100 sqmm AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 12600.06 | KM | 25326.1206
117 | SMR11488 | 160 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 18800
118 | SWR11185 | 37 | Sub Transportation of Spun Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt any Spun Pole incl. L&UL<10KM | As per relevent standard specification | 771.38 | EA | 28541.06
119 | SWR11180 | 17 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 7343.49
120 | SWR20308 | 6 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 2443.74
121 | SWR10191 | 2 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 404
122 | SWR10509 | 2 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 200
123 | SWR11860 | 2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 5440.68
124 | SWR10150 | 3.15 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 1943.865
125 | SWR10206 | 3.15 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 696.15
126 | SWR10524 | 3.15 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 582.75
127 | SWR10211 | 12 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 36
128 | SWR10529 | 12 | Unloading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 36
129 | SWR12416 | 6 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 12
130 | SWR10631 | 6 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 12
131 | SWR10618 | 3 | Loading of 33KV Metal parts bag of 25 nos | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 195
132 | SWR10632 | 3 | Unloading of 33 KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 195
133 | SWR10354 | 9 | Erection of 33 kv Stay set complete including fixing of bow ,fixing and binding of Eye bolt, Anchor rod, guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. | Electrical work | Assembly and erection of Stay set 33kv | As per relevent standard specification | 684.53 | SET | 6160.77
134 | SWR21190 | 9 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In Hard Gravel and Hard murram not requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 4680
135 | SWR11980 | 100 | Laying of 33KV 3x400sqmm XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. | Electrical work | Lay-DR 33KV 3x400sqmm UG Cb CC/BT Compsr | As per relevent standard specification | 1388.84 | M | 138884
136 | SWR12004 | 60 | Raising of Double cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (pipe cost extra) | Electrical work | Raise-DR 33KV 3x400sqmm UG Cb on support | As per relevent standard specification | 323.85 | M | 19431
137 | SMR22222 | 8 | Supply 33KV 3x400Sqmm Outdoor End Kit | Electrical work | Supply of 33KV 3x400Sqmm O/D End Kit | As per relevent standard specification | 5867 | EA | 46936
138 | SMR22223 | 1 | Supply of 33KV 3x400SQmm Straight through joint kit | Electrical work | Supply of 33KV3x400Sqmm Straight thr kit | As per relevent standard specification | 21472 | EA | 21472
139 | SWR10387 | 8 | Making of Outdoor/Indoor End Termination with 33 KV 3x400 Sqmm Cable | Electrical work | OD/Idoor end termination 33kv 3x400 xlpe | As per relevent standard specification | 2764.76 | EA | 22118.08
140 | SWR10382 | 1 | Making of straight through joint kit 33KV XLPE Out-Door End kit (3x400sqmm) | Electrical work | Straight through joint 33kv 3x400 xlpe | As per relevent standard specification | 5700.78 | EA | 5700.78
141 | SWR11171 | 8 | Loading of 11/33 KV In Door and Out door kits | Electrical work | Loading of 11/33 KV IN/OUT door kits | As per relevent standard specification | 6 | EA | 48
142 | SWR11152 | 8 | Unloading of 11/33 KV In Door and Out door kits | Electrical work | Un-loading of 11/33 KV IN/OUT door kits | As per relevent standard specification | 4 | EA | 32
143 | SWR11172 | 1 | Loading of 11/33KV Straight through joint kit | Electrical work | Loading 11/33KV Straight thr jointkit | As per relevent standard specification | 8 | EA | 8
144 | SWR11153 | 1 | Un-loading of 11/33KV Straight through joint kit | Electrical work | Un-loading 11/33KV Straight thr jointkit | As per relevent standard specification | 4 | EA | 4
145 | SMR40081 | 16 | Supply of 6" B class GI pipe | Electrical work | S-6" B Class GI pipe 5mm thck 20Kg/M | As per relevent standard specification | 1044 | M | 16704
146 | SWR10356 | 2.304 | Concreting the stay location with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.45X0.45X1.265 Mts)* 9 = 2.304 Cu.Mt | Electrical work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 15158.016
147 | SMR25238 | 37 | Supply of 12.5Mtr spun Pole | Electrical work | S-PSCC Spun Pole 12.5Mtr | As per relevent standard specification | 15635.59 | EA | 578516.83
148 | SMR25236 | 17 | Supply of 11Mtr PSCC 365 Kg Pole | Electrical work | S-PSCC Pole 11Mtr 365 Kg | As per relevent standard specification | 5399 | EA | 91783
149 | SMR25233 | 6 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 18656.46
150 | SMR25229 | 1 | Supply of 33KV V-Cross Arm without Clamps | Electrical work | S-33KV V-Cross Arm without Clamps | As per relevent standard specification | 1678 | EA | 1678
151 | SMR25207 | 850 | Supply of MS Angle 65X65X6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 48662.5
152 | SMR22745 | 1500 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 86175
153 | SMR12321 | 800 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 45136
154 | SMR25231 | 9 | Supply of 33KV MS Stay Set with BasePlate | Electrical work | S-33KV MS Stay Set with BasePlate | As per relevent standard specification | 1035 | SET | 9315
155 | SWR22092 | 4.13 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 11 kv line. | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 3159.45
156 | SWR10107 | 40 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11.0 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 28000
157 |  | 14 | Raising of Double cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (pipe cost extra) | Earth work | EXCAV. OF PIT HARD W/O Blast 0.76 x 0.76 x 1.83 M | As per relevent standard specification | 840 | EA | 11760
158 | SWR10978 | 54 | Erection of 11 M long PSCC pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 224925.12
159 | SWR10343 | 34 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 81600
160 | SWR10653 | 24 | Formation of 11 kv cut points (Vertical/Horizantal) including fixing of 11 KV Cross arms,clamps, strain insulators sets complete with hardware and stays (Bows and Eye-bolts), Excluding the cost of pit Excavation and pole erection. The contractor has to supply GI Bolts and Nuts. | Electrical work | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1350 | EA | 32400
161 | SWR10356 | 38.25 | Concreting the location after erection of 11.0 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes(0.75X0.75X2 Mts)*34 = 38.25 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 251646.75
162 | SWR10365 | 4.13 | Paving of the conductor 55 Sqmm AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 3 Cond | As per relevent standard specification | 8500 | KM | 35105
163 | SMR11488 | 108 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 12690
164 | SWR10206 | 0.7 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 154.7
165 | SWR10524 | 0.7 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 129.5
166 | SWR11248 | 330 | Loading 11KV Polymer Pin Insulator- with GI pins | Electrical work | Load-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 330
167 | SWR11249 | 330 | Unloading 11KV Polymer Pin Insulator with GI pins | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 330
168 | SWR10134 | 0.7 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 411.264
169 | SWR11862 | 2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 20 KM and upto 30 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 7382.76
170 | SWR10191 | 2 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 404
171 | SWR10509 | 2 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 200
172 | SWR11180 | 54 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 23326.38
173 | SWR20308 | 34 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 13847.86
174 | SWR10228 | 40 | Loading of 11 KV V - Cross arms | Electrical work | LOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 160
175 | SWR10546 | 40 | Unloading of 11 KV V - Cross arms | Electrical work | UNLOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 160
176 | SWR12402 | 5 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 240
177 | SWR12421 | 5 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 240
178 | SWR10251 | 40 | Loading of 11 KV Top fittings | Electrical work | LOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 40
179 | SWR10569 | 40 | Unloading of 11 KV Top fittings | Electrical work | UNLOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 40
180 | SWR12416 | 17 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 34
181 | SWR10631 | 17 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 34
182 | SWR10353 | 17 | Erection of 11 kv Stay set complete including fixing of bow, fixing and binding of Eye bolt,Anchor rod,guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Assembly and erection of Stay set11kv&LT | As per relevent standard specification | 606.85 | SET | 10316.45
183 | SWR21190 | 17 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In Hard Gravel and Hard murram not requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 8840
184 | SWR10356 | 4.352 | Concreting the stay location with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.45X0.45X1.265 Mts)* 17 = 4.352 Cu.Mt | Electrical work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 28631.808
185 | SMR25236 | 54 | Supply of 11Mtr PSCC 365 Kg Pole | Electrical work | S-PSCC Pole 11Mtr 365 Kg | As per relevent standard specification | 5399 | EA | 291546
186 | SMR25233 | 34 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 105719.94
187 | SMR25218 | 40 | Supply of 11KV V X-Arms with MS Angle 65x65x6 | Electrical work | S-11KV V X-Arms with MS Angle 65x65x6 | As per relevent standard specification | 743 | EA | 29720
188 | SMR25205 | 350 | Supply of MS Channel 75x40 mm | Electrical work | S-MS Channel 75x40 mm | As per relevent standard specification | 58.45 | KG | 20457.5
189 | SMR25206 | 60 | Supply of MS Angle 50x50x6 | Electrical work | S-MS Angle 50x50x6 | As per relevent standard specification | 58.15 | KG | 3489
190 | SMR12321 | 500 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 28210
191 | SMR12322 | 100 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 5650
192 | SMR25214 | 17 | Supply of LT/11KV MS Stay Sets with Base Plate | Electrical work | S-LT/11KV MS Stay Sets with Base Plate | As per relevent standard specification | 1168 | SET | 19856
[6 empty] | Electrical total |  |  | 5211806.8436
1 | SWR34179 | 12 | Cutting and Levelling the site with the help of JCB including cost,conveyance of all materials,hire charges etc complete for finished item of work. | JCB | Hire-JCB to Level & Clear the Site | As per relevant standard specification | 893 | H | 10716
2 | SWR33015 | 101.3 | Earth Work Mass Excavation (Ordinary rock not requiring blasting) to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions, labour and material charges etc., complete as directed by the engineer-incharge. | Earth Work | Excavation in Ordinary Soil | As per relevant standard specification | 331 | M3 | 33530.3
3 | SWR33028 | 17.9 | PCC (1:4:8) for levelling course using 40mm size hard broken Granite stone including cost and conveyance of all materials, HBG metal for foundations and leveling course and as directed by the Engineer- in - charge etc complete for finished item of work. | PCC | PCC with 40mm Metal (1:4:8) | As per relevant standard specification | 4587 | M3 | 82107.3
4 | SWR33041 | 125.1 | CRS masonry in CM (1:6) using Hard Granite Stones including cost and conveyance of all materials, seignorage charges, labour charge for construction and for dressing stones to required size and shape, dewatering, scaffolding, cutting for all leads and lifts, all incidental charges etc. complete for finished item of work as directed by the Engineer - in - charge. | Masonry | CRS Masonary CM(1:6) 2nd Sort | As per relevant standard specification | 5184 | M3 | 648518.4
5 | SWR33068 | 19.5 | Construction of brick masonary in CM(1:6) including cost and conveyance of all materials, labour charges etc. complete for finished item of work | Masonry | Brick Masonary in CM(1:6) GFloor | As per relevant standard specification | 8255 | M3 | 160972.5
6 | SWR33052 | 688.6 | Supplying and filling with borrowed gravel, watering, ramming, consolidating thoroughly complying with the standard specification including cost and conveyance of all materials, labour charges, hire charges of machinery, with all leads and incidental charges etc complete for finished item work | Gravel | S&Filling with Borrowed Gravel | As per relevant standard specification | 437 | M3 | 300918.2
7 | SWR33098 | 6.6 | RCC M20 GRADE Nominal Mix (a) Footings | RCC | RCC Footing: M20Gr, Steel Centering | As per relevant standard specification | 9231 | M3 | 60924.6
8 | SWR33100 | 4.7 | RCC M20 GRADE Nominal Mix (b) Columns | RCC | RCC Column GF: M20Gr, Steel Centering | As per relevant standard specification | 12819 | M3 | 60249.3
9 | SWR33099 | 1.7 | RCC M20 GRADE Nominal Mix (c) Plinth Beams | RCC | RCC Plinth Beam: M20Gr, Steel Centering | As per relevant standard specification | 11975 | M3 | 20357.5
10 | SWR33107 | 0.6 | RCC M20 GRADE Nominal Mix (d) Lintels | RCC | RCC Lintel GF: M20Gr, Steel Centering | As per relevant standard specification | 12647 | M3 | 7588.2
11 | SWR33114 | 11.6 | RCC M20 GRADE Nominal Mix (e) Sunshade | RCC | RCC Sunshade GF: M20Gr, Steel Centering | As per relevant standard specification | 1327 | M2 | 15393.2
12 | SWR33121 | 2.4 | RCC M20 GRADE Nominal Mix (f) Roof Beams | RCC | RCC Roof Beam GF: M20Gr, Steel Centering | As per relevant standard specification | 11891 | M3 | 28538.4
13 | SWR33128 | 7 | RCC M20 GRADE Nominal Mix (g) Slab | RCC | RCC Roof Slab GF: M20Gr, Steel Centering | As per relevant standard specification | 11375 | M3 | 79625
14 | SWR33144 | 2.3 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) / Mild steel (MS) steel bars (Fe 415/ Fe 500 grade as per IS 1786-1979) of different diameters for RCC works complete for finished item of work in all floors.( APSS No.126) | Steel | Reinforcement Steel Fe 415/500 | As per relevant standard specification | 70030 | TO | 161069
15 | SWR33163 | 348.86 | Providing plastering of 20mm thick to all uneven faces of walls and ceiling of superstructure in two coats with base coat in CM 1:6 of 16mm thick and top coat in Cm 1:4 4mm thick with dubara sponge finish | Plastering | Plastering 20mm (16mm+4mm)GFloor | As per relevant standard specification | 528 | M2 | 184198.08
16 | SWR33184 | 123 | Raised pointing in CM(1:3) including curing, cost and conveyance of all materials and labour charges for complete item of work. | Plastering | Raised Pointing to CRS Masonary CM(1:3) | As per relevant standard specification | 117 | M2 | 14391
17 | SWR33156 | 52.44 | Providing impervious coat over RCC roof slab surfaces to requried slopes with 20mm thick in CM 1:3 pro mixed with approvaled brand of water proffing compound as the raet of 1 kg per bag of cement inclding cost and conveyance of all materials | Plastering | Impervious Coat 20mm CM(1:3) GFloor | As per relevant standard specification | 551 | M2 | 28894.44
18 | SWR33264 | 5.7 | Supply and fixing of Flush type Doors with 35mm Thick Flush Shutters with Bondwood solied Block Board Type Faced on Both the sides with Commercial Type Plywood for finished item work as directed by the Engineer - in- charge. | Doors | S&F MT Wood Frame & Door-Laminate | As per relevant standard specification | 6881 | M2 | 39221.7
19 | SWR33277 | 5.76 | Supply and Fixing of Aluminium sliding windows with fixed glass panels using aluminium sections 62x32x1.2mm providing 5mm plain glass fixed to frame with beading gasket and glazing clips with all accessories, locking arrangements including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Windows | S&F Aluminium Window | As per relevant standard specification | 3243 | M2 | 18679.68
20 | SWR33310 | 6.25 | Supplying and fixing of MS safety grill with peripheral frame of ISA 25x25x4mm and horizontal & vertical 8mm square rods and including cost and coveyance of all mateirals with all leads and lifts, labour charges, painting charges complete for finished item of work | Windows | S&F of MS Safety Grill | As per relevant standard specification | 2491 | M2 | 15568.75
21 | SWR33219 | 29 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and approved size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and pointing with cement, labour etc, complete for finished item of work. | Flooring | Polished Shabad Flooring 20mm CM(1:3) | As per relevant standard specification | 761 | M2 | 22069
22 | SWR33236 | 10.7 | Providing skirting with tandoor blue slabs including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Flooring | Polished Shabad Skirting CM(1:3) | As per relevant standard specification | 847 | M2 | 9062.9
23 | SWR33029 | 29.8 | Plain Cement contrete - Nominal Mix (1:3:6) using 40 mm metal with concrete mixture including cost and conveyance of all materials labour charges etc. complete for finished iitem of work and as directed by the engineer-in-charge. | PCC | PCC with 40mm Metal (1:3:6) | As per relevant standard specification | 4889 | M3 | 145692.2
24 | SWR33030 | 6.8 | PCC(1:2:4) using 10 to 12 mm aggregate including cost and conveyance of all materials labour charges etc., complete for finished iitem of work and as directed by the engineer-in-charge. | PCC | PCC with 20mm Metal (1:2:4) | As per relevant standard specification | 5957 | M3 | 40507.6
25 | SWR33057 | 49.5 | Supply and Spreading of 20mm machine crushed metal including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | HBG metal | S&Spreading of 20mm HBG Metal | As per relevant standard specification | 1506 | M3 | 74547
26 | SWR33403 | 110 | Supply and fixing of fencing of welded wire mesh (2"x2") of 3mm dia with support channels of 75x 40mm and angles around of 30x30x3 mm including cost and conveyance of all materials, fabrication charges, painting charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Welded mesh | S&F MS Security Fencing Mesh (2"X2") | As per relevant standard specification | 2013 | M2 | 221430
27 | SWR33333 | 121 | Painting with two coats of OBD over a coat of primer including cost and conveyance of all materials ,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Paint | Painting with OBD 2Coats+Primer | As per relevant standard specification | 105 | M2 | 12705
28 | SWR33336 | 178.4 | Painting with two coats of ACE paint over a coat of primer including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Paint | Painting SnowCem/Apex 2 Coats+Primer | As per relevant standard specification | 188 | M2 | 33539.2
29 | SWR33329 | 175.9 | Painting with lovely cem three coats including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Paint | Painting with SuryaCem of 3 Coat | As per relevant standard specification | 69 | M2 | 12137.1
30 | SWR33404 | 10.07 | Supply and fixing of MS gates of approved design including cost and conveyance of all materials,fabrication charges etc complete for finished item of work. | Gate | S&F MS Gate | As per relevant standard specification | 4503 | M2 | 45345.21
31 | SWR33442 | 30 | S&F Conceal PVC Pipe 32mm dia in Slab | Electrification | S&F Conceal PVC Pipe 32mm dia in Slab | As per relevant standard specification | 75 | RMT | 2250
32 | SWR33441 | 20 | S&F Conceal PVC Pipe 20mm dia in Wall | Electrification | S&F Conceal PVC Pipe 25mm dia in Wall | As per relevant standard specification | 99 | RMT | 1980
33 | SWR33457 | 15 | Wiring with 2X1.0 Sqm(14/.3mm) PVC insulated flexiable copper cable in the existing metalic/Non metalic conduit pipe with 6A mini modular SP switch, mounted on metalic box covereds with appropriate front plate modules etc ceiling rose including cot and conveyance of all mateials, labour charges complete for light points, bell points and fan points in non residential builsing except circuit moving finished in all types masonary as directed by department. | Electrification | S&F Modular Switch LP,FP,EFP for NRBuild | As per relevant standard specification | 557 | EA | 8355
34 | SWR33461 | 2 | Supply and fixing of 6A 3/2 pin flush type plug socket with 6A flush type marked switch control on a common board with earth continuity including wire leads earth connections along with all labour charges etc. complete | Electrification | S&F Modular 3/2pin 6A Sockets | As per relevant standard specification | 455 | EA | 910
35 | SWR33464 | 2 | Supply and fixing of 16A 3pin flush type plug socket and 16A flush type fuse unit and 16A switch control. | Electrification | S&F Modular 3pin 16/6A Sockets | As per relevant standard specification | 428 | EA | 856
36 | SWR33484 | 4 | Supply and fixing of slanting holders with 100W bulb with all connections and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F Batten Holder | As per relevant standard specification | 113 | EA | 452
37 | SWR33545 | 4 | Supply and fixing of patty type tube light fitting with 4' 0" - 40W tube light,40W copper choke,starter,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F 20W LED Retro Tube Light | As per relevant standard specification | 704 | EA | 2816
38 | SWR33494 | 90 | Supply and run of 2 of 14/.3mm(1.00Sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | S&R 2 of 14/0.3mm (1.0sqmm) (FR) | As per relevant standard specification | 45 | RMT | 4050
39 | SWR33497 | 30 | Supply and run of 2 of 36/0.3 (2.5sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | S&R 2 of 36/0.3mm (2.5sqmm) (FR) | As per relevant standard specification | 90 | RMT | 2700
40 | SWR33520 | 1 | SPN Distribution board with IP-20 protection suitable for single phase 40A DP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 4Nos as out going MCBs in sheet steel enclosure including connections and cost of all material labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F 8wySPNDB IP-20,10kA-6-32A SPMCB 4No | As per relevant standard specification | 4793 | EA | 4793
41 | SWR33596 | 1 | Providing independent earthing for main switches,IC cutouts and motors using 40mm. Dia. B-class G.I.Pipe of 2.5' length duly providing 12mm. Dia. 6No. Holes and required bolts,nuts and washers,including filling with equal preparation of salt and charcoal in layers and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | Provd-Independent Earthing | As per relevant standard specification | 3783 | EA | 3783
42 | SWR33597 | 15 | Supply and run of No.8 SWG Copper wire including cost of all accessories and labour charges etc., Complete | Electrification | S&R No.8 SWG Copper Wire | As per relevant standard specification | 132 | RMT | 1980
43 | SWR33563 | 2 | Supply and Fixing of 48" ceiling fan of bajaj make(or equivalent make) including cost material,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Flooring | S&F 1200mm (48'') Sweep Ceiling Fan | As per relevant standard specification | 3205 | EA | 6410
44 | SWR33224 | 13.7 | Supply and fixing of ceramic tiles fantacy for dadoing including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | Ceramic Tile Flooring 20mm CM(1:3) | As per relevant standard specification | 884 | M2 | 12110.8
45 | SWR34311 | 1 | Supply and fixing of 580mm x 440mm long Orissa pan of Parry, Neycer or Hindhusthan, make with 'P' or 'S' trap etc complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F Orissa Pan WC 580mmx440mm | As per relevant standard specification | 2101 | EA | 2101
46 | SWR34386 | 2 | Supply and Fixing 4" PVC floor trap including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F Floor Trap (Bell Mouth) 110mm | As per relevant standard specification | 259 | EA | 518
47 | SWR34382 | 2 | Supply,fixing 90mm dia. PVC Plain Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F 90mm dia Plain Bend PVC/SWR Pipe | As per relevant standard specification | 81 | EA | 162
48 | SWR34385 | 1 | Supply,fixing 90mm dia. PVC Door Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F 75mm dia Door Bend PVC/SWR Pipe | As per relevant standard specification | 78 | EA | 78
49 | SWR34286 | 1 | S&Fixing 150mm x 100mm SWG gully traps Ist class grating & const. brick masonry in CM (1:6) prop inter mediate chamber and fitted with CI frame etc complete. | Plumbing | S&F 150mmx100mm SWG Gully Trap | As per relevant standard specification | 722 | EA | 722
50 | SWR34377 | 6 | Supply and Fixing 4" dia 3M Single socket PVC pipe including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F 110mm dia 3M 1Socket PVC/SWR Pipe | As per relevant standard specification | 412 | RMT | 2472
51 | SWR34453 | 1 | Supply and Fixing 4" dia PVC cowl including labour charges etc. complete for finished item of work. | Plumbing | S&F 4" dia PVC Cowl | As per relevant standard specification | 20 | EA | 20
52 | SWR34444 | 1 | Construction of soak pit with 4' dia RCM rings upto a depth of 6' including cost and conveyance of all materials as directed by the engineer-in-charge. | Plumbing | Construct- 4' dia & 5' Ht Soak Pit | As per relevant standard specification | 2950 | EA | 2950
53 | SWR34362 | 100 | CPVC Pipes and Fittings b) 22.20mm OD Pipe - SDR 11 | Plumbing | S&F 22.20mm OD CPVC Pipe-SDR 11 | As per relevant standard specification | 201 | RMT | 20100
54 | SWR34363 | 100 | CPVC Pipes and Fittings c) 28.60mm OD Pipe - SDR 11 | Plumbing | S&F 28.60mm OD CPVC Pipe-SDR 11 | As per relevant standard specification | 241 | RMT | 24100
55 | SWR34344 | 24 | Supply and fixing of 15mm dia. SS coated taps including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F 15mm GM Ball Valve | As per relevant standard specification | 221 | EA | 5304
56 | SWR34345 | 1 | Supply and fixing of 20mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F 20mm GM Ball Valve | As per relevant standard specification | 319 | EA | 319
57 | SWR34346 | 2 | Supply and fixing of 25mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F 25mm GM Ball Valve | As per relevant standard specification | 449 | EA | 898
58 | SWR34329 | 4 | Supply and fixing of 12.7mm bib tap Indian make including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F 12.7mm Bib Tap 400grams | As per relevant standard specification | 261 | EA | 1044
59 | SWR34375 | 500 | Providing and placing on Terrace polyetheylene water storage tank with double layer approved brand and manufacture with cover complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F Polyethylene Water Storage Tank | As per relevant standard specification | 9 | L | 4500
60 | SWR34740 | 1 | Supply of steel table of size 4'x2.5'x30" with 18 mm plywood fixed with rubber beeding with drawers on right side with automatic locking arrangements etc complete for finished item of work and as directed by the engineer-in-charge. | Furniture | S-3x2ft Office Table | As per relevant standard specification | 5000 | EA | 5000
61 | SWR33857 | 1 | Supply of 'S' type chair with arms teakwood frame with seat back 's' type on G.I pipe including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Furniture | Supply of S-Type Chair | As per relevant standard specification | 3700 | EA | 3700
62 | SWR33858 | 2 | Supply of P V C chairs of Neelkamal of approved quality & make including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Furniture | Supply of PVC Chair | As per relevant standard specification | 1100 | EA | 2200
63 | SWR33422 | 2.16 | S&F Glow Sign Board | Board | S&F Glow Sign Board | As per relevant standard specification | 3449 | M2 | 7449.84
64 | SWR34656 | 759 | S-LDPE Sheet 500Micron | LDPE sheet | S-LDPE Sheet 500Micron | As per relevant standard specification | 95 | M2 | 72105
65 | SWR33054 | 71.42 | S&Filling with Borrowed Stone Dust | Stone Dust | S&Filling with Borrowed Stone Dust | As per relevant standard specification | 971 | M3 | 69348.82
66 | SWR33415 | 7.3 | Manufacture, supply ,laying and fixing of 450mm dia. NP3 class R.C.C. socket and spigot pipes (rate per meter of effective length) including transportaion ,taxes and duties etc. complete for finished item of work and as directed by the Engineer-in-charge. | Hume pipe | S&F RCC Hume Pipe of 450mm dia | As per relevant standard specification | 1403 | Rmt | 10241.9
67 | SWR33406 | 130 | S&F RCC Fencing Pole 0.115mx0.115mx2.7m in pits of size 0.5x0.5x0.5 m and refilled with P.C.C(1:4:8) using 20 mm HBG metal including cost & conveyance of all materials, labour charges etc complete for finished item of work. | Fencing poles | S&F RCC Fencing Pole 0.115mx0.115mx2.7m | As per relevant standard specification | 1411 | EA | 183430
68 | SWR33405 | 25 | S&F RCC Fencing Pole 0.1mx0.1mx1.8m in pits of size 0.5x0.5x0.5 m and refilled with P.C.C(1:4:8) using 20 mm HBG metal including cost & conveyance of all materials, labour charges etc complete for finished item of work. | Fencing poles | S&F RCC Fencing Pole 0.1mx0.1mx1.8m | As per relevant standard specification | 1269 | EA | 31725
69 | SWR33407 | 275 | S&Fixing of barbed wire 8 straight strands and 2 cross strands including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Barbed wire | S&F Barbed Wire 8H & 2Cross | As per relevant standard specification | 252 | Rmt | 69300
70 | SWR33425 | 1 | Prov supply of electricity to the site | Power Supply | Provd-Supply of Electricity to Site | As per relevant standard specification | 5408 | EA | 5408
71 | SWR33608 | 1 | Geophysical Investgation Charges | Borewell | Geophysical Investgation Charges | As per relevant standard specification | 2500 | EA | 2500
72 | SWR33609 | 90 | Drilling-165mm Bore Well 0 to 90M | Borewell | Drilling-165mm Bore Well 0 to 90M | As per relevant standard specification | 305 | M | 27450
73 | SWR34830 | 80 | Drilling-165mm Bore Well 90m & above | Borewell | Drill-165mm Bore Well 90M to 120M | As per relevant standard specification | 369 | M | 29520
74 | SWR33611 | 30 | S&F 160mm dia PVC Casing | Borewell | S&F 160mm dia PVC Casing | As per relevant standard specification | 787 | M | 23610
75 | SWR33636 | 1 | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | Borewell | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | As per relevant standard specification | 33214 | EA | 33214
76 | SWR33641 | 200 | S&R 3C 2.5sqmm Flat Copper Cable | Borewell | S&R 3C 2.5sqmm Flat Copper Cable | As per relevant standard specification | 106 | EA | 21200
77 | SWR33644 | 1 | S&E D.O.L Starter 250V Single Phase | Borewell | S&E D.O.L Starter 250V Single Phase | As per relevant standard specification | 1403 | EA | 1403
78 | SWR34203 | 1 | Supply & fixing of Flange Clamps | Borewell | Supply & fixing of Flange Clamps | As per relevant standard specification | 175 | EA | 175
79 | SWR34410 | 168 | S&F HDPE Pipe 40mm dia 6kg/sqcm | Borewell | S&F HDPE Pipe 40mm dia 6kg/sqcm | As per relevant standard specification | 205 | Rmt | 34440
80 | SWR34470 | 164 | Seigniorage Charges - Sand | Seignorages | Seigniorage Charges - Sand | As per relevant standard specification | 40 | M3 | 6560
81 | SWR34471 | 151.5 | Seigniorage Charges - Metal | Seignorages | Seigniorage Charges - Metal | As per relevant standard specification | 97.5 | M3 | 14771.25
82 | SWR34472 | 688.6 | Seigniorage Charges - Gravel | Seignorages | Seigniorage Charges - Gravel | As per relevant standard specification | 30 | M3 | 20658
[7 empty] | Civil total |  | 3382640.37
[7 empty] | Electrical & Civil total |  | 8594447.2136

## 7. Symphony SS
Symphony SS Electrical Estimate-WBS No: S-1610-90-06-01-01-001
Name of the work: Estimate for erection of new 33/11 KV Indoor SS with connected 33 KV and 11 KV lines at Symphony Park Homes in Patancheru (T) at Patancheru Division of Sangareddy Circle .
S.No | SSR Code | Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR10463 | 1 | Erection of 3 Ph DTRs upto 25KVA | Electrical work | Erection of Three Phase DTRs | As per relevent standard specification | 1139.95 | EA | 1139.95
2 | SWR10194 | 1 | Loading of 10,15 & 25 KVA DTR | Electrical work | LOADING of 15&25kva DTR | As per relevent standard specification | 129 | EA | 129
3 | SWR10512 | 1 | Un loading of 10,15 & 25 KVA DTR | Electrical work | UNLOADING of 15&25kva DTR | As per relevent standard specification | 129 | EA | 129
4 | SWR21843 | 1 | RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Electrical work | Column type DTR Plinth topslab 4'x4'x6" | As per relevent standard specification | 25967.57 | EA | 25967.57
5 | SWR10395 | 1 | Erection of 11 KV HG Fuse set including earthing | Electrical work | Erect. of 11kv HG Fuseset incl earthing | As per relevent standard specification | 740.52 | SET | 740.52
6 | SWR10231 | 1 | Loading of 11 KV HG Fuse Sets | Electrical work | LOADING of 11 KV HG Fuse Sets | As per relevent standard specification | 18 | EA | 18
7 | SWR10549 | 1 | Un loading of 11 KV HG Fuse Sets | Electrical work | UNLOADING of 11 KV HG Fuse Sets | As per relevent standard specification | 18 | EA | 18
8 | SWR10393 | 1 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 3200
9 | SWR10272 | 1 | Loading of 11 KV Tilting type AB Switch spares Fixed / Moving contacts | Electrical work | LOADING of 11 KV TT AB Sw F/M contacts | As per relevent standard specification | 30 | SET | 30
10 | SWR10556 | 1 | Un loading of 11KV AB Switch Conventional type | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | SET | 80
11 | SWR10674 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
12 | SWR11923 | 90 | LT 3 1/2 x 185 Sqmm Cable | Electrical work | Lay-SR LT 3.5x185sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 377.63 | M | 33986.7
13 | SWR11959 | 10 | LT 3 1/2 x 185 Sqmm Cable | Electrical work | Raise-SR LT 3.5x185sqmm UG Cb on support | As per relevent standard specification | 85.43 | M | 854.3
14 | SWR11920 | 85 | 11KV 3x185 Sqmm Cable | Electrical work | Lay-SR 11KV 3x185sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 465.46 | M | 39564.1
15 | SWR11956 | 15 | 11 KV 3x185 Sqmm Cable | Electrical work | Raise-SR 11KV 3x185sqmm UG Cb on support | As per relevent standard specification | 126.23 | M | 1893.45
16 | SWR10390 | 2 | Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | Electrical work | OD/Idoor end termination 11kv 3x185 xlpe | As per relevent standard specification | 2370.63 | EA | 4741.26
17 | SWR21321 | 2 | Erection of 8 MVA PTR. |  | Erec 33/11 KV, 8 MVA PTR as per Spec | As per relevent standard specification | 49480.2 | EA | 98960.4
18 | SWR11868 | 2 | 0 to 100 KM | Electrical work | Trans-PTR 3.15-8.0MVA upto 100Km(<20MT) | As per relevent standard specification | 1600 | EA | 3200
19 | SWR10613 | 2 | Loading of 8MVA PTR | Electrical work | LOADING of 8 MVA PTR | As per relevent standard specification | 5805.84 | EA | 11611.68
20 | SWR10627 | 2 | Unloading of 8MVA PTR | Electrical work | UNLOADING of 8 MVA PTR | As per relevent standard specification | 5805.84 | EA | 11611.68
21 | SWR11166 | 1 | Loading of 220 V Batterry with charger | Electrical work | Loading 220 V Battery with Charger | As per relevent standard specification | 1612 | SET | 1612
22 | SWR11147 | 1 | Un loading of 220 V Batterry with charger | Electrical work | Un-loading 220 V Battery with Charger | As per relevent standard specification | 1024 | SET | 1024
23 | SWR11395 | 1 | Expofyn/Dubas 220V Battery charger service charges | Electrical work | 220V Battery charger service charges | As per relevent standard specification | 5720 | EA | 5720
24 | SWR10931 | 16 | Erection of 11KV indoor switch gear panel/indoor PT panel / Bus section panel / Bus raiser panel/Capacitor panel/Switch fuse panel for DTR. | Electrical work | Erection of 11KV indoor switchgear panel | As per relevent standard specification | 8894 | EA | 142304
25 | SWR10199 | 16 | Loading of 11 KV VCBs along with Panel boards | Electrical work | LOADING of 11 KV VCBs&Panel boards | As per relevent standard specification | 1024 | EA | 16384
26 | SWR10517 | 16 | Un loading of 11 KV VCBs along with Panel boards | Electrical work | UNLOADING of 11 KV VCBs&Panel boards | As per relevent standard specification | 1044.48 | EA | 16711.68
27 | SWR10930 | 10 | Erection of 33KV indoor switch gear panel/33KV indoor PT panel / Bus section panel / Bus raiser panel | Electrical work | Erection of 33KV indoor switchgear panel | As per relevent standard specification | 9847 | EA | 98470
28 | SWR10198 | 10 | Loading of 33 KV VCBs along with Panel boards | Electrical work | LOADING of 33 KV VCBs&Panel boards | As per relevent standard specification | 1024 | EA | 10240
29 | SWR10516 | 10 | Un loading of 33 KV VCBs along with Panel boards | Electrical work | UNLOADING of 33 KV VCBs&Panel boards | As per relevent standard specification | 1044.48 | EA | 10444.8
30 | SMR40009 | 9.6 | Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Electrical work | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 20937.6
31 | SWR10877 | 9.6 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Electrical work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 8169.6
32 | SMR40010 | 9.6 | (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Electrical work | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 12412.8
33 | SWR10879 | 9.6 | (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Electrical work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 4627.2
34 | SWR10963 | 50 | Painting of Name Plates for any equipment | Electrical work | Painting of Name Plates for any equipmen | As per relevent standard specification | 122 | EA | 6100
35 | SWR10881 | 1 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 142
36 | SMR40051 | 6 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Electrical work | Supply 9mtrs tubular poles single way | As per relevent standard specification | 13913 | EA | 83478
37 | SWR10955 | 6 | Erection of tubular poles | Electrical work | Errection of tubular poles | As per relevent standard specification | 1379 | EA | 8274
38 | SMR24635 | 6 | S-Metal Handle Lamp 150W | Electrical work | S-Metal Handle Lamp 150W | As per relevent standard specification | 6450 | EA | 38700
39 | SWR10956 | 6 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Electrical work | Fixing of LED/Metal halide complete. | As per relevent standard specification | 1268 | EA | 7608
40 | SMR40033 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. | Electrical work | SupCU Flexi jumper for Power T/F Neutral | As per relevent standard specification | 4725 | EA | 9450
41 | SWR11879 | 1700 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Electrical work | Lay-4C/10C 2.5Sqmm Control Cable | As per relevent standard specification | 27 | M | 45900
42 | SMR40045 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. | Electrical work | Supply of AC Supply panel complete | As per relevent standard specification | 42000 | EA | 42000
43 | SWR24835 | 1 | Erection of Control panel | Electrical work | Erect-Control Panel | As per relevent standard specification | 1800 | LS | 1800
44 | SWR10873 | 750 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Electrical work | Supply,fabricati of 6mm Checkerd plates | As per relevent standard specification | 83 | KG | 62250
45 | SMR40068 | 12 | Rubber mats ( 6’x3’) size for indoor SS | Electrical work | SupRubber mats( 6’x3’)size for indoorSS | As per relevent standard specification | 1386 | EA | 16632
46 | SMR40062 | 1 | Sup Alluminium Ladder for indoor works | Electrical work | Sup Alluminium Ladder for indoor works | As per relevent standard specification | 4410 | EA | 4410
47 | SMR40087 | 2 | Trolley mounted CO2 (6.5Kgs) | Electrical work | Sup TrollyMounted Co2 Cylinders(IS-2878) | As per relevent standard specification | 9240 | EA | 18480
48 | SMR40088 | 2 | Fire bucket stand with 3 buckets (8 -10 ltr capacity) | Electrical work | Sup Fire Buckets Stand with Buckets | As per relevent standard specification | 1386 | SET | 2772
49 | SMR40089 | 6 | Room fire extinguisher (2 ltrs capacity) for control room | Electrical work | Sup Fire Extinguisher for Control Room | As per relevent standard specification | 4620 | EA | 27720
50 | SMR40071 | 4 | Safety Helmets of standard make | Electrical work | Supply of Safety Helmet of standard make | As per relevent standard specification | 231 | EA | 924
51 | SMR40066 | 4 | Earth Rods (8ft) Screw & clamp type | Electrical work | Sup Earth Rods (8ft) Screw & clamp type | As per relevent standard specification | 578 | EA | 2312
52 | SMR40067 | 4 | Hand Gloves | Electrical work | Supply of Hand Gloves | As per relevent standard specification | 289 | SET | 1156
53 | SMR40069 | 1 | Standard basic cell phone with charger | Electrical work | Sup Stand basic cell phone with charger | As per relevent standard specification | 1386 | EA | 1386
54 | SMR40061 | 1 | Steel almarah(61/2 X 3ft) Godrej | Electrical work | Sup Steel almarah(61/2 X 3ft) Godrej | As per relevent standard specification | 9818 | EA | 9818
55 | SMR40057 | 1 | Table (3x6ft) Godrej | Electrical work | Supply of Table (3x6ft) Godrej | As per relevent standard specification | 6050 | EA | 6050
56 | SMR40058 | 4 | S type chairs (Godrej) | Electrical work | Supply of S type chairs (Godrej) | As per relevent standard specification | 924 | EA | 3696
57 | SMR40060 | 1 | Angle racks(18x36.6inches) Godrej | Electrical work | Sup Angle racks(18x36.6inches) Godrej | As per relevent standard specification | 1733 | EA | 1733
58 | SMR40070 | 10 | Danger boards with clamps | Electrical work | Supply of Danger boards with clamps | As per relevent standard specification | 116 | EA | 1160
59 | SMR40086 | 1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) | Electrical work | Sup 33/11kv S.S Permanent name board | As per relevent standard specification | 10238 | EA | 10238
60 | SMR40059 | 1 | Wall clock standard make | Electrical work | Supply of Wall clock standard make | As per relevent standard specification | 578 | EA | 578
61 | SMR40063 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. | Electrical work | SupTaparia Tool kit complete as per Spec | As per relevent standard specification | 4925 | SET | 4925
62 | SMR40064 | 1 | Rechargeable LED torch light of Standard make | Electrical work | Sup Rechargeable LED torch light. | As per relevent standard specification | 1733 | EA | 1733
63 | SMR40065 | 1 | Hack saw (12 inches) | Electrical work | Supply of Hack saw (12 inches) | As per relevent standard specification | 289 | EA | 289
64 | SMR40072 | 8 | LC Boards | Electrical work | Supply of LC Boards | As per relevent standard specification | 116 | EA | 928
65 | SMR40073 | 2 | Gum Boots (Pair) | Electrical work | Supply of Gum Boots | As per relevent standard specification | 693 | EA | 1386
66 | SMR40076 | 1 | Digital clamp meter. | Electrical work | Supply of Digital clamp meter. | As per relevent standard specification | 2888 | EA | 2888
67 | SMR40074 | 1 | 5000v megger | Electrical work | Supply of 5000v megger | As per relevent standard specification | 13860 | EA | 13860
68 | SMR12378 | 1 | S-10ft Aluminium Ladder | Electrical work | S-10ft Aluminium Ladder | As per relevent standard specification | 1654 | EA | 1654
69 | SWR20032 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard | Electrical work | Sup &fix of board ind Switchyard layout | As per relevent standard specification | 1654 | EA | 1654
70 | SWR22090 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Electrical work | Sup& fix safety inst/SS Op. inst board | As per relevent standard specification | 2205 | EA | 2205
71 | SMR11482 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 125496
72 | SMR11480 | 2 | Supply of GI eath pipe with 40 mm dia,3mm thcikness with 2.0 M Length | Electrical work | S-GI pipe earthing 40mm dia 2m long | As per relevent standard specification | 698 | EA | 1396
73 | SWR10920 | 377.6 | 75x 8mm MS Flat / GI Flat. | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 24544
74 | SWR11765 | 375 | Laying of MS Flat 50 x 6 mm (without excavation) in existing Substation | Electrical work | Earth-50x6mm MS Flat in SS (w/o excavte) | As per relevent standard specification | 17 | M | 6375
75 | SWR11880 | 4 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Electrical work | Lay-Cable Terminations to Switchgear | As per relevent standard specification | 34.43 | LS | 137.72
76 | SWR22088 | 2 | Fabrication and laying of ladder in cable trench | Electrical work | Fab & laying of ladder in cable trench | As per relevent standard specification | 788 | EA | 1576
77 | SWR10345 | 2 | Rail pole 105 lbs | Electrical work | Erection of Rail Pole 105Lbs | As per relevent standard specification | 3319 | EA | 6638
78 | SMR22718 | 700 | S/o rail poles 90/105lb (250x2N) | Electrical work | S/o rail poles 90/105lb (250x2N) | As per relevent standard specification | 47.27 | KG | 33089
79 | SWR10105 | 10 | 8.0Mtrs PSCC Poles - 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | Electrical work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 6000
80 | SWR10356 | 15.84 | Including the cost of cement | Earth Work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 104211.36
81 | SWR11890 | 0.558 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Earth Work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | EA | 2172.294
82 | SWR10869 | 2.05 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Electrical work | Fabrication of struc.with welding. | As per relevent standard specification | 3426 | TO | 7023.3
83 | SWR10204 | 6 | Loading of R.S. Joists 175 x 85 mm | Electrical work | LOADING of R.S. Joists 175 x 85 mm | As per relevent standard specification | 76 | EA | 456
84 | SWR10522 | 6 | Un loading of R.S. Joists 175 x 85 mm | Electrical work | UNLOADING of R.S. Joists 175 x 85 mm | As per relevent standard specification | 50 | EA | 300
85 | SWR10642 | 6 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Electrical work | Fabrication of 175x85/150x75mm RS joist | As per relevent standard specification | 512.55 | EA | 3075.3
86 | SWR11266 | 3 | Box pole 9/10/11 Mtr | Electrical work | Erection of 9/10/11Meter Box pole | As per relevent standard specification | 2643.83 | EA | 7931.49
87 | SWR10147 | 3.25 | Upto 10 KM | Electrical work | TRANSPORT OF STEEL MATERIAL UPTO 10KM | As per relevent standard specification | 332.52 | TO | 1080.69
88 | SWR10206 | 1.75 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 386.75
89 | SWR10524 | 1.75 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 323.75
90 | SWR11213 | 2 | Loading/Unloading of PTR and Erection/Dismantle on Plinth with crane | Electrical work | Unload & Erect-PTR with crane | As per relevent standard specification | 10500 | LS | 21000
91 | SWR11972 | 150 | 33 KV 3x400 Sqmm Cable | Electrical work | Lay-DR 33KV 3x400sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 751.16 | M | 112674
92 | SWR11973 | 250 | 11 KV 3x300 Sqmm Cable | Electrical work | Lay-DR 11KV 3x300sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 631.06 | M | 157765
93 | SWR10988 | 400 | Laying of 2nd cable in excavated trench | Electrical work | Lay-2nd Cable in Excavated Trench | As per relevent standard specification | 204.1 | M | 81640
94 | SMR25200 | 1 | Supply of LT Distribution Box (SMC) | Electrical work | S-LT Distribution Box (SMC) | As per relevent standard specification | 7797 | EA | 7797
95 | SMR12324 | 1 | Supply of 11KV HG fuse set for station transformer | Electrical work | S-11KV HG FuseSet for StationTransformer | As per relevent standard specification | 1974 | EA | 1974
96 | SMR12318 | 1 | Supply of 11 kV 200 A Tilting type AB switch | Electrical work | S-11KV 200A Tilting Type AB Switch | As per relevent standard specification | 8991 | EA | 8991 | 33KV line
97 | SMR12321 | 600 | Supply of MS Flat 75x8 mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 33852
98 | SMR12322 | 600 | Supply of MS Flat 50x6 mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 33900
99 | SMR22745 | 550 | Supply of MS Channel 100X50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KG | 31597.5
100 | SMR25204 | 100 | S-LT XLPE Cable 3 1/2 C 185 sqmm | Electrical work | S-LT XLPE Cable 3 1/2 C 185 sqmm | As per relevent standard specification | 547 | M | 54700
101 | SMR25201 | 1 | S-11KV 3x185 Heat Shble O/d End Term Kit | Electrical work | S-11KV 3x185 Heat Shble O/d End Term Kit | As per relevent standard specification | 1182.97 | EA | 1182.97
102 | SMR25202 | 1 | S-11KV 3x185 Heat Shble I/d End Term Kit | Electrical work | S-11KV 3x185 Heat Shble I/d End Term Kit | As per relevent standard specification | 1085 | EA | 1085
103 | SMR12302 | 1000 | Supply of RS Joist girder Poles (150X150mm) | Electrical work | S-RS Joist Grider Pole (150x150mm) | As per relevent standard specification | 59.25 | KG | 59250
104 | SMR12303 | 500 | supply of RS Joist Poles (175X85mm) | Electrical work | S-RS Joist Pole (175x85mm) | As per relevent standard specification | 60.75 | KG | 30375
105 | SMR25208 | 2 | S-11KV 3x300 Heat Shble O/d End Term Kit | Electrical work | S-11KV 3x300 Heat Shble O/d End Term Kit | As per relevent standard specification | 1372.88 | EA | 2745.76
106 | SMR25209 | 2 | S-11KV 3x300 Heat Shble I/d End Term Kit | Electrical work | S-11KV 3x300 Heat Shble I/d End Term Kit | As per relevent standard specification | 1459.83 | EA | 2919.66
107 | SMR22222 | 2 | Supply 33KV 3x400Sqmm Outdoor | Electrical work | Supply of 33KV 3x400Sqmm O/D End Kit | As per relevent standard specification | 4554 | EA | 9108
108 | SMR11506 | 2 | Supply 33KV 3x400Sqmm Indoor | Electrical work | S-of 33KV 3x400Sqmm Indoor end kit | As per relevent standard specification | 3589.96 | EA | 7179.92
109 | SWR11980 | 120 | 33 KV 3x400 Sqmm Cable | Electrical work | Lay-DR 33KV 3x400sqmm UG Cb CC/BT Compsr | As per relevent standard specification | 1388.84 | EA | 166660.8
110 | SWR11988 | 80 | 33 KV 3x400 Sqmm Cable | Electrical work | Lay-DR 33KV 3x400sqmm UG Cb CC/BT RdCrsg | As per relevent standard specification | 1587.07 | EA | 126965.6
111 | SWR11954 | 100 | 33 KV 3x400 Sqmm Cable | Electrical work | Raise-SR 33KV 3x400sqmm UG Cb on support | As per relevent standard specification | 135.66 | M | 13566
112 | SWR10988 | 200 | Laying of 2nd cable in excavated trench | Electrical work | Lay-2nd Cable in Excavated Trench | As per relevent standard specification | 204.1 | M | 40820
113 | SWR10387 | 16 | Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination | Electrical work | OD/Idoor end termination 33kv 3x400 xlpe | As per relevent standard specification | 2764.76 | EA | 44236.16
114 | SWR10382 | 5 | 33 KV 3x400 Sqmm Cable | Electrical work | Straight through joint 33kv 3x400 xlpe | As per relevent standard specification | 5700.78 | EA | 28503.9
115 | SMR40081 | 100 | Supply of 6" B class GI pipe | Electrical work | S-6" B Class GI pipe 5mm thck 20Kg/M | As per relevent standard specification | 1044 | M | 104400
116 | SMR11610 | 150 | supply of 6" DWC pipe | Electrical work | S-6" DWC pipe | As per relevent standard specification | 1012 | M | 151800
117 | SMR40078 | 50 | Supply of 150 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | Electrical work | Supply of 150 mm Hume pipe of class NP3 | As per relevent standard specification | 303 | M | 15150
118 | SWR10392 | 4 | Erection of 33 KV AB Switch including alignment and earthing | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 18000
119 | SWR10105 | 10 | 8.0Mtrs PSCC Poles - 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | Electrical work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 6000
120 | SWR10642 | 1 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Electrical work | Fabrication of 175x85/150x75mm RS joist | As per relevent standard specification | 512.55 | EA | 512.55
121 | SWR11266 | 1 | Box pole 9/10/11 Mtr | Electrical work | Erection of 9/10/11Meter Box pole | As per relevent standard specification | 2643.83 | EA | 2643.83
122 | SWR10921 | 100 | GI Flat 25 x 3 mm (including material) | Electrical work | Laying of earth mat,excavation 25x3mm | As per relevent standard specification | 68 | RMT | 6800
123 | SMR11482 | 8 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 27888
124 | SMR11483 | 8 | Supply of CI eath pipe with 80mm dia,2.0 M Length | Electrical work | S-CI Pipe earthing 80mm dia 2.75m long | As per relevent standard specification | 2789 | EA | 22312
125 | SWR11230 | 3 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Electrical work | Load-11/33KV XLPE UG Cable for all sizes | As per relevent standard specification | 1024 | DR | 3072
126 | SWR11231 | 3 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Electrical work | Unload-11/33KV XLPE UG Cable all sizes | As per relevent standard specification | 1024 | DR | 3072
127 | SWR11860 | 2 | Upto 10 Km with Lorry for each trip | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | KM | 5440.68
128 | SWR10206 | 0.6 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 132.6
129 | SWR10524 | 0.6 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 111
130 | SWR10204 | 1 | Loading of R.S. Joists 175 x 85 mm | Electrical work | LOADING of R.S. Joists 175 x 85 mm | As per relevent standard specification | 76 | EA | 76
131 | SWR10640 | 1 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Electrical work | Painting of RS Joist(1C RO, 2C Al.Paint) | As per relevent standard specification | 1132 | EA | 1132
132 | SWR10396 | 6 | Erection of 33 KV LAS station/Line type including earthing | Electrical work | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 5280
133 | SWR10522 | 1 | Un loading of R.S. Joists 175 x 85 mm | Electrical work | UNLOADING of R.S. Joists 175 x 85 mm | As per relevent standard specification | 50 | EA | 50
134 | SWR10356 | 6.16 | Including the cost of cement | Earth Work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 40526.64
135 | SWR10266 | 6 | Loading of 33 KV, 10 KA LAs Station type | Electrical work | LOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 41 | EA | 246
136 | SWR10584 | 6 | Un loading of 33 KV, 10 KA LAs Station type | Electrical work | UNLOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 35 | EA | 210
137 | SMR40009 | 1.2 | Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Electrical work | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 2617.2
138 | SWR10877 | 1.2 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Electrical work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 1021.2
139 | SMR40010 | 1.2 | (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Electrical work | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 1551.6
140 | SWR10879 | 1.2 | (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Electrical work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 578.4
141 | SMR11487 | 50 | Supply of MS bolts & nuts and washers etc of all sizes | Electrical work | S-MS Bolts & Nuts,Washers etc., | As per relevent standard specification | 91.25 | KG | 4562.5
142 | SWR11890 | 0.217 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Earth Work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | EA | 844.781
143 | SWR10320 | 50 | Back clamps with 50 x 6 mm MS Flat | Electrical work | Fab Back clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 15 | EA | 750
144 | SWR10920 | 21.28 | 75x 8mm MS Flat / GI Flat. | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 1383.2 | 11 KV line
145 | SWR10147 | 1.1 | Upto 10 KM | Electrical work | TRANSPORT OF STEEL MATERIAL UPTO 10KM | As per relevent standard specification | 332.52 | TO | 365.772
146 | SWR24701 | 30 | Road Cutting - CC Road in GHMC/R&B | Earth Work | Road Cutting - CC Road in GHMC/R&B | As per relevent standard specification | 1844 | M | 55320
147 | SMR22222 | 8 | Supply 33KV 3x400Sqmm Outdoor | Electrical work | Supply of 33KV 3x400Sqmm O/D End Kit | As per relevent standard specification | 4554 | EA | 36432
148 | SMR11506 | 8 | Supply 33KV 3x400Sqmm Indoor | Electrical work | S-of 33KV 3x400Sqmm Indoor end kit | As per relevent standard specification | 3589.96 | EA | 28719.68
149 | SMR22223 | 5 | Supply of 33KV 3x400SQmm Straight Through Joint Kit | Electrical work | Supply of 33KV3x400Sqmm Straight thr kit | As per relevent standard specification | 24151 | EA | 120755
150 | SMR12303 | 4000 | supply of RS Joist Poles (175X85mm) | Electrical work | S-RS Joist Pole (175x85mm) | As per relevent standard specification | 60.75 | KG | 243000
151 | SMR22745 | 500 | Supply of MS Channel 100X50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KG | 28725
152 | SMR25207 | 200 | S-MS Angle 65X65X6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 11450
153 | SMR12321 | 200 | Supply of MS Flat 75x8 mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 11284
154 | SMR12322 | 200 | Supply of MS Flat 50x6 mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 11300
155 | SMR25205 | 500 | S-MS Channel 75x40 mm | Electrical work | S-MS Channel 75x40 mm | As per relevent standard specification | 58.45 | KG | 29225
156 | SWR11230 | 4 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Electrical work | Load-11/33KV XLPE UG Cable for all sizes | As per relevent standard specification | 1024 | DR | 4096
157 | SWR11231 | 4 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Electrical work | Unload-11/33KV XLPE UG Cable all sizes | As per relevent standard specification | 1024 | DR | 4096
158 | SWR11860 | 4 | Upto 10 Km with Lorry for each trip | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 10881.36
159 | SWR10386 | 4 | 11 KV 3x300 Sqmm Cable | Electrical work | Straight through joint 11kv 3x300 xlpe | As per relevent standard specification | 3725.45 | EA | 14901.8
160 | SMR40080 | 800 | Supply of 4" B class GI pipe | Electrical work | S-4" BClass GI pipe 3.65mm thck 12.2Kg/M | As per relevent standard specification | 740 | M | 592000
161 | SMR11609 | 500 | supply of 4" DWC pipe | Electrical work | S-4" DWC pipe | As per relevent standard specification | 759 | M | 379500
162 | SWR10204 | 6 | Loading of R.S. Joists 175 x 85 mm | Electrical work | LOADING of R.S. Joists 175 x 85 mm | As per relevent standard specification | 76 | EA | 456
163 | SWR10522 | 6 | Un loading of R.S. Joists 175 x 85 mm | Electrical work | UNLOADING of R.S. Joists 175 x 85 mm | As per relevent standard specification | 50 | EA | 300
164 | SWR10105 | 6 | 8.0Mtrs PSCC Poles - 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | Electrical work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 3600
165 | SWR10356 | 7.04 | Including the cost of cement | Earth Work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 46316.16
166 | SWR11890 | 0.248 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Earth Work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | EA | 965.464
167 | SWR12331 | 8 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Electrical work | AB Switch Coil Earthing GI No. 8 Wire | As per relevent standard specification | 146.63 | EA | 1173.04
168 | SWR10642 | 6 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Electrical work | Fabrication of 175x85/150x75mm RS joist | As per relevent standard specification | 512.55 | EA | 3075.3
169 | SWR11266 | 6 | Box pole 9/10/11 Mtr | Electrical work | Erection of 9/10/11Meter Box pole | As per relevent standard specification | 2643.83 | EA | 15862.98
170 | SMR11483 | 6 | Supply of CI eath pipe with 80mm dia,2.0 M Length | Electrical work | S-CI Pipe earthing 80mm dia 2.75m long | As per relevent standard specification | 2789 | EA | 16734
171 | SWR10357 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Electrical work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 7405.2
172 | SMR11480 | 12 | Supply of GI eath pipe with 40 mm dia,3mm thcikness with 2.0 M Length | Electrical work | S-GI pipe earthing 40mm dia 2m long | As per relevent standard specification | 698 | EA | 8376
173 | SWR11765 | 100 | Laying of MS Flat 50 x 6 mm (without excavation) in existing Substation | Electrical work | Earth-50x6mm MS Flat in SS (w/o excavte) | As per relevent standard specification | 17 | M | 1700
174 | SMR40009 | 1 | Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Electrical work | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 2181
175 | SWR10877 | 1 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Electrical work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 851
176 | SMR40010 | 1 | (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Electrical work | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 1293
177 | SWR10879 | 1 | (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Electrical work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 482
178 | SWR10869 | 1 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Electrical work | Fabrication of struc.with welding. | As per relevent standard specification | 3426 | TO | 3426
179 | SWR10320 | 100 | Back clamps with 50 x 6 mm MS Flat | Electrical work | Fab Back clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 15 | EA | 1500
180 | SWR10921 | 100 | GI Flat 25 x 3 mm (including material) | Electrical work | Laying of earth mat,excavation 25x3mm | As per relevent standard specification | 68 | RMT | 6800
181 | SWR10206 | 0.5 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 110.5
182 | SWR10524 | 0.5 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 92.5
183 | SWR10147 | 4 | Upto 10 KM | Electrical work | TRANSPORT OF STEEL MATERIAL UPTO 10KM | As per relevent standard specification | 332.52 | TO | 1330.08
184 | SWR10963 | 8 | Painting of Name Plates for any equipment | Electrical work | Painting of Name Plates for any equipmen | As per relevent standard specification | 122 | EA | 976
185 | SWR12054 | 0 | 11 KV 3x300 Sqmm Cable | Electrical work | Lay-5R 11KV 3x300sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 1122 | M | 0
186 | SWR12058 | 0 | 11 KV 3x300 Sqmm Cable | Electrical work | Lay-5R 11KV 3x300sqmm UG Cb CC/BT Compsr | As per relevent standard specification | 2047.65 | M | 0
187 | SWR12062 | 0 | 11 KV 3x300 Sqmm Cable | Electrical work | Lay-5R 11KV 3x300sqmm UG Cb CC/BT RdCrsg | As per relevent standard specification | 2103.75 | M | 0
188 | SWR12042 | 0 | 11 KV 3x300 Sqmm Cable | Electrical work | Lay-4R 11KV 3x300sqmm UG Cb CC/BT Compsr | As per relevent standard specification | 2033.63 | M | 0
189 | SWR12031 | 0 | 11 KV 3x300 Sqmm Cable | Electrical work | Lay-TR 11KV 3x300sqmm UG Cb FootPath GI | As per relevent standard specification | 710.18 | M | 0
190 | SWR11973 | 0 | 11 KV 3x300 Sqmm Cable | Electrical work | Lay-DR 11KV 3x300sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 631.06 | M | 0
191 | SWR11004 | 0 | Laying of11KV XLPE UG cable Double Run of Size in Hard Rock(1.05*0.5x1=0.525cum) | Electrical work | Laying of 11kV UG 2Run in Hard rock. | As per relevent standard specification | 1194 | RMT | 0
192 | SWR11981 | 480 | 11 KV 3x300 Sqmm Cable | Electrical work | Lay-DR 11KV 3x300sqmm UG Cb CC/BT Compsr | As per relevent standard specification | 1264.64 | M | 607027.2
193 | SWR11989 | 0 | 11 KV 3x300 Sqmm Cable | Electrical work | Lay-DR 11KV 3x300sqmm UG Cb CC/BT RdCrsg | As per relevent standard specification | 1449.06 | M | 0
194 | SWR11997 | 0 | 11 KV 3x300 Sqmm Cable | Electrical work | Lay-DR 11KV 3x300sqmm UG Cb FootPath GI | As per relevent standard specification | 571.2 | M | 0
195 | SWR11928 | 0 | 11 KV 3x300 Sqmm Cable | Electrical work | Lay-SR 11KV 3x300sqmm UG Cb CC/BT Compsr | As per relevent standard specification | 1073.94 | M | 0
196 | SWR11937 | 60 | 11 KV 3x300 Sqmm Cable | Electrical work | Lay-SR 11KV 3x300sqmm UG Cb CC/BT RdCrsg | As per relevent standard specification | 1199.4 | M | 71964
197 | SWR10988 | 480 | Laying of 2nd cable in excavated trench | Electrical work | Lay-2nd Cable in Excavated Trench | As per relevent standard specification | 204.1 | M | 97968
198 | SWR11955 | 0 | 11 KV 3x300 Sqmm Cable | Electrical work | Raise-SR 11KV 3x300sqmm UG Cb on support | As per relevent standard specification | 144.08 | M | 0
199 | SWR12005 | 180 | 11 KV 3x300 Sqmm Cable | Electrical work | Raise-DR 11KV 3x300sqmm UG Cb on support | As per relevent standard specification | 275.4 | M | 49572
200 | SWR10391 | 24 | Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination | Electrical work | OD/Idoor end termination 11kv 3x300 xlpe | As per relevent standard specification | 2370.63 | EA | 56895.12
201 | SWR10640 | 6 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Electrical work | Painting of RS Joist(1C RO, 2C Al.Paint) | As per relevent standard specification | 1132 | EA | 6792
202 | SMR11487 | 50 | Supply of MS bolts & nuts and washers etc of all sizes | Electrical work | S-MS Bolts & Nuts,Washers etc., | As per relevent standard specification | 91.25 | KG | 4562.5
203 | SMR25210 | 4 | S-11KV 3x300 Heat Shble str thr JointKit | Electrical work | S-11KV 3x300 Heat Shble str thr JointKit | As per relevent standard specification | 4110.17 | EA | 16440.68
204 | SMR25208 | 15 | S-11KV 3x300 Heat Shble O/d End Term Kit | Electrical work | S-11KV 3x300 Heat Shble O/d End Term Kit | As per relevent standard specification | 1372.88 | EA | 20593.2
205 | SMR25209 | 5 | S-11KV 3x300 Heat Shble I/d End Term Kit | Electrical work | S-11KV 3x300 Heat Shble I/d End Term Kit | As per relevent standard specification | 1459.83 | EA | 7299.15
206 | SWR22092 | 1.5 | survey line&cabl inc peg mark&tree clear | Electrical work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 1147.5
207 | SWR10105 | 20 | 8.0Mtrs PSCC Poles - 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | Electrical work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 12000
208 | SWR10110 | 10 | 8.0Mtrs PSCC Pole 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | Electrical work | EXCAV. OF PIT HARD (2.6" x 2.6" x 5.0') | As per relevent standard specification | 1440 | EA | 14400
209 | SWR10350 | 30 | Spun poles 12.5 Mtrs / 12.9Mtrs PSCC | Electrical work | Erection of Spun pole 12.5Mt | As per relevent standard specification | 4115.7 | EA | 123471
210 | SWR10190 | 30 | Loading of Spun poles 12.5 M | Electrical work | LOADING of 12.5M SPUN POLE | As per relevent standard specification | 548 | EA | 16440
211 | SWR10508 | 30 | Un loading of Spun poles 12.5 M | Electrical work | UNLOADING of 12.5M SPUN POLE | As per relevent standard specification | 363 | EA | 10890
212 | SWR10343 | 10 | 9.1 M long PSCC pole | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 24000
213 | SWR10981 | 10 | Formation of Cut point for 33 KV Single Circuit line excluding pole erection and stays | Electrical work | Horizontal Cut point for 33 KV line | As per relevent standard specification | 1759.5 | EA | 17595
214 | SWR10356 | 15 | Including the cost of cement | Earth Work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 98685
215 | SWR10366 | 1.5 | 100 Sqmm Single Circuit (3 Conductors) | Electrical work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 12600.06 | KM | 18900.09
216 | SMR11488 | 100 | Supply of GI Bolts & Nuts etc | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 11750
217 | SWR10188 | 10 | Loading of PSCC Poles 9.1 M | Electrical work | LOADING of 9.1M PSCC POLE | As per relevent standard specification | 182 | EA | 1820
218 | SWR10506 | 10 | Un loading of PSCC Poles 9.1 M | Electrical work | UNLOADING of 9.1M PSCC POLE | As per relevent standard specification | 91 | EA | 910
219 | SWR20308 | 10 | 9.1 Mtrs long PSCC Poles | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 4072.9
220 | SWR10191 | 2 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 404
221 | SWR10509 | 2 | Un loading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 200
222 | SWR11860 | 2 | Upto 10 Km with Lorry for each trip | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 5440.68
223 | SWR10150 | 1.6 | Above 30 KM and upto 50 KM | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 987.36
224 | SWR10206 | 1.6 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 353.6
225 | SWR10524 | 1.6 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 296
226 | SWR10211 | 90 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 270
227 | SWR10529 | 90 | Un loading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 270
228 | SWR12416 | 33 | Loading of 33 & 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 66
229 | SWR10631 | 33 | Un loading of 33 & 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 66
230 | SWR10618 | 1 | Loading of 33 KV Metal parts | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 65
231 | SWR10632 | 1 | Un loading of 33 KV Metal parts | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 65
232 | SWR21190 | 20 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits any and leveling the site with out any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Electrical work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 10400
233 | SWR10354 | 20 | 33 KV | Electrical work | Assembly and erection of Stay set 33kv | As per relevent standard specification | 684.53 | SET | 13690.6
234 | SMR25238 | 30 | S-PSCC Spun Pole 12.5Mtr | Electrical work | S-PSCC Spun Pole 12.5Mtr | As per relevent standard specification | 15635.59 | EA | 469067.7
235 | SMR25233 | 10 | S-PSCC Pole 9.1Mtr 280kg | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 31094.1
236 | SMR25229 | 28 | S-33KV V-Cross Arm without Clamps | Electrical work | S-33KV V-Cross Arm without Clamps | As per relevent standard specification | 1678 | EA | 46984
237 | SMR25228 | 50 | S-33KV M.S.Back Clamps | Electrical work | S-33KV M.S.Back Clamps | As per relevent standard specification | 248 | SET | 12400
238 | SMR25230 | 28 | S-33KV Top Cleat with Clamps | Electrical work | S-33KV Top Cleat with Clamps | As per relevent standard specification | 461 | EA | 12908
239 | SMR25207 | 100 | S-MS Angle 65X65X6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 5725
240 | SMR22745 | 1000 | Supply of MS Channel 100X50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KG | 57450
241 | SMR12321 | 500 | Supply of MS Flat 75x8 mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 28210
242 | SMR25231 | 20 | S-33KV MS Stay Set with BasePlate | Electrical work | S-33KV MS Stay Set with BasePlate | As per relevent standard specification | 1035 | SET | 20700
243 | SWR22092 | 4 | survey line&cabl inc peg mark&tree clear | Electrical work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 3060
244 | SWR10105 | 51 | 8.0Mtrs PSCC Poles - 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | Earth Work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 30600
245 | SWR10110 | 29 | 8.0Mtrs PSCC Pole 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | Earth Work | EXCAV. OF PIT HARD (2.6" x 2.6" x 5.0') | As per relevent standard specification | 1440 | EA | 41760
246 | SWR10349 | 80 | Spun poles 11Mtrs PSCC | Electrical work | Erection of Spun pole 11Mt | As per relevent standard specification | 3570 | EA | 285600
247 | SWR10343 | 23 | 9.1 M long PSCC pole | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 55200
248 | SWR21590 | 0 | 8.0 m long PSCC poles for Strut | Electrical work | Erection of 8.0Mts PSCC Poles for stuts | As per relevent standard specification | 1500 | EA | 0
249 | SWR10653 | 34 | Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays | Electrical work | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1350 | EA | 45900
250 | SWR10356 | 64.294 | Including the cost of cement | Earth Work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 422990.226
251 | SWR10703 | 4 | 55 Sqmm Double Circuit (6 Conductors) | Electrical work | Stringing of 55sqmm 33/11kv Line 6 Cond | As per relevent standard specification | 16000 | KM | 64000
252 | SMR11488 | 200 | Supply of GI Bolts & Nuts etc | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 23500
253 | SWR10206 | 1 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 221
254 | SWR10524 | 1 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 185
255 | SWR11248 | 255 | Loading of 11KV Polymer Pin Insulators with GI pins | Electrical work | Load-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 255
256 | SWR11249 | 255 | Un loading of 11KV Polymer Pin Insulators with GI pins | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 255
257 | SWR10134 | 1 | Above 30 KM and upto 50 KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 587.52
258 | SWR11862 | 3 | Above 20 Km and upto 30 Km with Lorry for each trip | Electrical work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 11074.14
259 | SWR10191 | 3 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 606
260 | SWR10509 | 3 | Un loading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 300
261 | SWR11180 | 80 | 11 Mtrs long PSCC Poles | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 34557.6
262 | SWR20308 | 23 | 9.1 Mtrs long PSCC Poles | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 9367.67
263 | SWR20307 | 0 | 8 Mtrs long PSCC Poles | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 0
264 | SWR10228 | 71 | Loading of 11 KV V - Cross arms | Electrical work | LOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 284
265 | SWR10546 | 71 | Un loading of 11 KV V - Cross arms | Electrical work | UNLOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 284
266 | SWR12402 | 171 | Loading of 11 KV Metal parts | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 8208
267 | SWR12421 | 171 | Un loading of 11 KV Metal parts | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 8208
268 | SWR10251 | 80 | Loading of 11 KV Top fittings | Electrical work | LOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 80
269 | SWR10569 | 80 | Un loading of 11 KV Top fittings | Electrical work | UNLOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 80
270 | SWR12416 | 171 | Loading of 33 & 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 342
271 | SWR10631 | 171 | Un loading of 33 & 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 342
272 | SWR10353 | 10 | 11 KV and LT | Electrical work | Assembly and erection of Stay set11kv&LT | As per relevent standard specification | 606.85 | SET | 6068.5
273 | SWR21190 | 10 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits any and leveling the site with out any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth Work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 5200
274 | SWR12411 | 0 | Loading of Stay / Back clamps | Electrical work | LOADING of Stay / Back clamps | As per relevent standard specification | 1 | EA | 0
275 | SWR10568 | 0 | Un loading of Stay / Back clamps | Electrical work | UNLOADING of Stay / Back clamps | As per relevent standard specification | 1 | EA | 0
276 | SWR12198 | 1 | Dismantle-3Ph 100KVA DTR Plinth | Electrical work | Dismantle-3Ph 100KVA DTR Plinth | As per relevent standard specification | 1160.25 | EA | 1160.25
277 | SWR20077 | 1 | Dismantle-DTR Single Pole Structure | Electrical work | Dismantle-DTR Single Pole Structure | As per relevent standard specification | 637.5 | EA | 637.5
278 | SWR11743 | 1 | Dismantling of all types of 33 kV AB switches | Electrical work | Dismantle-AB Swithces (all types) | As per relevent standard specification | 1281.38 | EA | 1281.38
279 | SWR11745 | 1 | Dismantling of 11 KV HG fuse set including earthing | Electrical work | Dimantle-11KV HG Fuse Set incl earthing | As per relevent standard specification | 353.43 | EA | 353.43
280 | smr11485 | 20 | Supply of GI Flat 25X3 mm | Electrical work | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | kg | 2100
281 | SMR25236 | 90 | S-PSCC Pole 11Mtr 365 Kg | Electrical work | S-PSCC Pole 11Mtr 365 Kg | As per relevent standard specification | 5399 | EA | 485910
282 | SMR25233 | 23 | S-PSCC Pole 9.1Mtr 280kg | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 71516.43
283 | SMR25232 | 0 | S-PSCC Pole 8Mtr 140kg | Electrical work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 0
284 | SMR25218 | 71 | S-11KV V X-Arms with MS Angle 65x65x6 | Electrical work | S-11KV V X-Arms with MS Angle 65x65x6 | As per relevent standard specification | 743 | EA | 52753
285 | SMR25212 | 0 | S-MS Back Clamps for 8 M PSCC Pole | Electrical work | S-MS Back Clamps for 8 M PSCC Pole | As per relevent standard specification | 79 | KG | 0
286 | SMR12321 | 250 | Supply of MS Flat 75x8 mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 14105
287 | SMR25227 | 90 | S-11KV Middle Phase Raiser | Electrical work | S-11KV Middle Phase Raiser | As per relevent standard specification | 519 | EA | 46710
288 | SMR25205 | 550 | S-MS Channel 75x40 mm | Electrical work | S-MS Channel 75x40 mm | As per relevent standard specification | 58.45 | KG | 32147.5
289 | SMR25223 | 20 | S-11KV Horizontal Cross Arms | Electrical work | S-11KV Horizontal Cross Arms | As per relevent standard specification | 528 | EA | 10560
290 | SMR25206 | 200 | S-MS Angle 50x50x6 | Electrical work | S-MS Angle 50x50x6 | As per relevent standard specification | 58.15 | KG | 11630
291 | SMR12322 | 0 | Supply of MS Flat 50x6 mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | M | 0
292 | SMR25215 | 10 | S-LT MS Stay Sets without Base Plate | Electrical work | S-LT MS Stay Sets without Base Plate | As per relevent standard specification | 335 | SET | 3350
[6 empty] | Electrical Total |  |  | 8388379.427
1 | SWR34179 | 6 | Hire-JCB to Level & Clear the Site | JCB | NA | As per relevant standard specification | 2164.1 | H | 12984.6
2 | SWR33015 | 353.14 | Excavation in Ordinary Soil | Earth Work | NA | As per relevant standard specification | 347 | M3 | 122539.58
3 | SWR33028 | 56.19 | PCC with 40mm Metal (1:4:8) | PCC | NA | As per relevant standard specification | 4084 | M3 | 229479.96
4 | SWR33029 | 24.3 | PCC with 40mm Metal (1:3:6) | PCC | NA | As per relevant standard specification | 4391 | M3 | 106701.3
5 | SWR33030 | 3.9 | PCC with 20mm Metal (1:2:4) | PCC | NA | As per relevant standard specification | 5524 | M3 | 21543.6
6 | SWR33098 | 30.25 | RCC Footing: M20Gr, Steel Centering | RCC | NA | As per relevant standard specification | 8247 | M3 | 249471.75
7 | SWR33100 | 17.19 | RCC Column GF: M20Gr, Steel Centering | RCC | NA | As per relevant standard specification | 10942 | M3 | 188092.98
8 | SWR33099 | 6.47 | RCC Plinth Beam: M20Gr, Steel Centering | RCC | NA | As per relevant standard specification | 10667 | M3 | 69015.49
9 | SWR33107 | 2.35 | RCC Lintel GF: M20Gr, Steel Centering | RCC | NA | As per relevant standard specification | 11102 | M3 | 26089.7
10 | SWR33114 | 7.43 | RCC Sunshade GF: M20Gr, Steel Centering | RCC | NA | As per relevant standard specification | 1164 | M2 | 8648.52
11 | SWR33121 | 14.32 | RCC Roof Beam GF: M20Gr, Steel Centering | RCC | NA | As per relevant standard specification | 10677 | M2 | 152894.64
12 | SWR33128 | 36.87 | RCC Roof Slab GF: M20Gr, Steel Centering | RCC | NA | As per relevant standard specification | 10228 | M3 | 377106.36
13 | SWR33144 | 15 | Reinforcement Steel Fe 415/500 | Steel | NA | As per relevant standard specification | 74027 | TO | 1110405
14 | SWR33041 | 144.16 | CRS Masonary CM(1:6) 2nd Sort | Masonry | NA | As per relevant standard specification | 4451 | M3 | 641656.16
15 | SWR33184 | 86.1 | Raised Pointing to CRS Masonary CM(1:3) | Plastering | NA | As per relevant standard specification | 94 | M2 | 8093.4
16 | SWR33068 | 87.6 | Brick Masonary in CM(1:6) GFloor | Masonry | NA | As per relevant standard specification | 7633 | M3 | 668650.8
17 | SWR33052 | 394.2 | S&Filling with Borrowed Gravel | Gravel | NA | As per relevant standard specification | 435 | M3 | 171477
18 | SWR33163 | 1848.9 | Plastering 20mm (16mm+4mm)GFloor | Plastering | NA | As per relevant standard specification | 411 | M2 | 759897.9
19 | SWR33156 | 228 | Impervious Coat 20mm CM(1:3) GFloor | Plastering | NA | As per relevant standard specification | 441 | M2 | 100548
20 | SWR33203 | 52.56 | RCM Drop Wall 40mm CM(1:2) Gfloor | Drop | NA | As per relevant standard specification | 2447 | M2 | 128614.32
21 | SWR33277 | 17.28 | S&F Aluminium Window | Window | NA | As per relevant standard specification | 3381.54 | M2 | 58433.0112
22 | SWR33310 | 18.75 | S&F of MS Safety Grill | Safety grill | NA | As per relevant standard specification | 2539 | M2 | 47606.25
23 | SWR33411 | 9.3 | S&F Collapsible steel shutter | Collapsible | NA | As per relevant standard specification | 4017 | M2 | 37358.1
24 | SWR33264 | 5.04 | S&F MT Wood Frame & Door-Laminate | Doors | NA | As per relevant standard specification | 6799.02 | M2 | 34267.0608
25 | SWR33224 | 26.8 | Ceramic tile Flooring 20 mm CM (1:3) | Ceramic tiles | NA | As per relevant standard specification | 734 | M2 | 19671.2
26 | SWR33219 | 137.53 | Polished Shabad Flooring 20mm CM(1:3) | Flooring | NA | As per relevant standard specification | 660 | M2 | 90769.8
27 | SWR33236 | 10.4 | Polished Shabad Skirting CM(1:3) | Skirting | NA | As per relevant standard specification | 727 | M2 | 7560.8
28 | SWR33333 | 582.37 | Painting with OBD 2Coats+Primer | Paint | NA | As per relevant standard specification | 109.9 | M2 | 64002.463
29 | SWR33336 | 535.1 | Painting SnowCem/Apex 2 Coats+Primer | Paint | NA | As per relevant standard specification | 195.91 | M3 | 104831.441
30 | SWR33270 | 5.83 | S&F Aliminium Double Leaf Door | Doors | NA | As per relevant standard specification | 6912.4 | M2 | 40299.292
31 | SWR33145 | 4746 | S&F structural Steel Angles etc., | Structural Steel | NA | As per relevant standard specification | 104 | Kg | 493584
32 | SWR33404 | 47.54 | S&F of MS gate | Ms Gate | NA | As per relevant standard specification | 4579.89 | M2 | 217727.9706
33 | SWR33438 | 90 | S&F Surfc pvc pipe 25mm dia. 1.5mmthk | Electrification | NA | As per relevant standard specification | 83 | M | 7470
34 | SWR33441 | 2 | S&F Conceal pvc pipe 25mm dia. in wall | Electrification | NA | As per relevant standard specification | 89 | M | 178
35 | SWR33523 | 2 | S&F 8wySPN DB IP-42 | Electrification | NA | As per relevant standard specification | 5624 | EA | 11248
36 | SWR33462 | 10 | S&F Modular 3pin 6A sockets | Electrification | NA | As per relevant standard specification | 276 | EA | 2760
37 | SWR33464 | 4 | S&F Modular 3pin 16/6A sockets | Electrification | NA | As per relevant standard specification | 437 | EA | 1748
38 | SWR33460 | 44 | S&F Flush type switch LP,FP,EFP RBuild | Electrification | NA | As per relevant standard specification | 487 | EA | 21428
39 | SWR33553 | 20 | S&F 20W LED Tubelight Batten | Electrification | NA | As per relevant standard specification | 531 | EA | 10620
40 | SWR33571 | 4 | S&F 12" light duty exhaust fan | Electrification | NA | As per relevant standard specification | 2068 | EA | 8272
41 | SWR33496 | 360 | S&R 2 of 22/0.3mm (1.5 sq.mm) (FR) | Electrification | NA | As per relevant standard specification | 67 | Rmt | 24120
42 | SWR33497 | 270 | S&R 2 of 36/0.3mm (2.5 sq.mm) (FR) | Electrification | NA | As per relevant standard specification | 95 | Rmt | 25650
43 | SWR33484 | 15 | S&F Batten Holder | Electrification | NA | As per relevant standard specification | 116 | EA | 1740
44 | SWR33563 | 10 | S&F of 1200mm (48'') sweep Ceiling fan | Electrification | NA | As per relevant standard specification | 2215 | EA | 22150
45 | SWR33596 | 12 | Providing independent Earthing | Electrification | NA | As per relevant standard specification | 4891 | EA | 58692
46 | SWR34284 | 12 | S&F 152.4mm SWG SP-1 pipes -3ft depth | Plumbing | NA | As per relevant standard specification | 763 | Rmt | 9156
47 | SWR34297 | 2 | Cnstrn. Of 1'6"x1'6" brick CHAMBERS | Plumbing | NA | As per relevant standard specification | 4610 | EA | 9220
48 | SWR34383 | 2 | S&F 90mm dia Door Bend PVC/SWR pipe | Plumbing | NA | As per relevant standard specification | 113 | EA | 226
49 | SWR34382 | 2 | S&F 90mm dia Plain Bend PVC/SWR pipe | Plumbing | NA | As per relevant standard specification | 84 | EA | 168
50 | SWR34377 | 6 | S&F 110mm dia 3M 1socket PVC/SWR pipe | Plumbing | NA | As per relevant standard specification | 422 | Rmt | 2532
51 | SWR34378 | 6 | S&F 90mm dia 3M 1socket PVC/SWR pipe | Plumbing | NA | As per relevant standard specification | 370.67 | Rmt | 2224.02
52 | SWR34286 | 1 | S&F 150 mm x 100 mm SWG gully trap | Plumbing | NA | As per relevant standard specification | 749 | Ea | 749
53 | SWR34314 | 1 | S&F European Water Closet of 1st quality | Plumbing | NA | As per relevant standard specification | 2081 | EA | 2081
54 | SWR34315 | 1 | S&F Indian make plastic seat and lid | Plumbing | NA | As per relevant standard specification | 1280 | EA | 1280
55 | SWR34328 | 2 | S&F 12.7mm stop cock 400 grams | Plumbing | NA | As per relevant standard specification | 669 | EA | 1338
56 | SWR34329 | 2 | S&F 12.7mm bib tap 400 grams | Plumbing | NA | As per relevant standard specification | 271 | EA | 542
57 | SWR34316 | 1 | S&F Flat Back Wash Hand Basin | Plumbing | NA | As per relevant standard specification | 1508 | EA | 1508
58 | SWR34428 | 3 | S&F 38.1 mm C.P waste coupling | Plumbing | NA | As per relevant standard specification | 257 | EA | 771
59 | SWR34426 | 3 | S&F 31.75mm PVC flexible waste pipe 0.9m | Plumbing | NA | As per relevant standard specification | 33 | EA | 99
60 | SWR34387 | 3 | S&F 101.6 mm Nahany Trap | Plumbing | NA | As per relevant standard specification | 134 | EA | 402
61 | SWR34313 | 1 | S&F porcelain flushing tank 10 Lit | Plumbing | NA | As per relevant standard specification | 3137 | EA | 3137
62 | SWR34375 | 1000 | S&F Polyethylene water storage tank | Plumbing | NA | As per relevant standard specification | 10 | L | 10000
63 | SWR34361 | 5 | S&F15.90mm OD CPVC Pipe - SDR 11 | Plumbing | NA | As per relevant standard specification | 239 | Rmt | 1195
64 | SWR34362 | 60 | S&F 22.20mm OD CPVC Pipe - SDR 11 | Plumbing | NA | As per relevant standard specification | 313 | Rmt | 18780
65 | SWR34363 | 35 | S&F 28.60mm OD CPVC Pipe - SDR 11 | Plumbing | NA | As per relevant standard specification | 410 | Rmt | 14350
66 | SWR34346 | 1 | S&F 25mm GM Ball valve | Plumbing | NA | As per relevant standard specification | 466 | EA | 466
67 | SWR34345 | 1 | S&F 20mm GM Ball valve | Plumbing | NA | As per relevant standard specification | 331 | EA | 331
68 | SWR34430 | 1 | S&Fsteel towel rod of 600 mm long | Plumbing | NA | As per relevant standard specification | 437 | EA | 437
69 | SWR34429 | 1 | S&F CP brass soap dish | Plumbing | NA | As per relevant standard specification | 623 | EA | 623
70 | SWR33608 | 1 | Geophysical Investgation Charges | Borewell | NA | As per relevant standard specification | 5000 | EA | 5000
71 | SWR33609 | 90 | Drilling-165mm Bore Well 0 to 90M | Borewell | NA | As per relevant standard specification | 336 | M | 30240
72 | SWR34830 | 30 | Drill-165mm Bore Well 90M to 120M | Borewell | NA | As per relevant standard specification | 369 | M | 11070
73 | SWR33611 | 30 | S&F 160mm dia PVC Casing | Borewell | NA | As per relevant standard specification | 844 | M | 25320
74 | SWR33636 | 1 | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | Borewell | NA | As per relevant standard specification | 34237 | M | 34237
75 | SWR34410 | 175 | S&F HDPE Pipe 40mm dia 6kg/sqcm | Borewell | NA | As per relevant standard specification | 160 | EA | 28000
76 | SWR33644 | 1 | S&E D.O.L Starter 250V Single Phase | Borewell | NA | As per relevant standard specification | 1040 | Rmt | 1040
77 | SWR33641 | 200 | S&R 3C 2.5sqmm Flat Copper Cable | Borewell | NA | As per relevant standard specification | 190 | EA | 38000
78 | SWR33423 | 2.21 | S&F poly vinyl acrylic board | Name board | NA | As per relevant standard specification | 1930.48 | EA | 4266.3608
79 | SWR33425 | 1 | Prov supply of electricity to the site | Power supply | NA | As per relevant standard specification | 5677.88 | M2 | 5677.88
80 | SWR33058 | 3.6 | Supply&Spreading 12mm HBG metal | HBG metal | NA | As per relevant standard specification | 1463 | EA | 5266.8
81 | SWR34470 | 198.4 | Seigniorage Charges - Sand | Seignorages | NA | As per relevant standard specification | 40 | M3 | 7936
82 | SWR34471 | 34.2 | Seigniorage Charges - Metal | Seignorages | NA | As per relevant standard specification | 97.5 | Sft | 3334.5
83 | SWR34472 | 394.2 | Seigniorage Charges - Gravel | Seignorages | NA | As per relevant standard specification | 30 | M3 | 11826
84 | SWR33426 | 7358.7456 | Provd 2Sets of Structural Drawings | Drawings | NA | As per relevant standard specification | 4.5 | M | 33114.3552
85 | SWR34831 | 30 | Drill-165mm Bore Well 120M to 150M | Borewell | NA | As per relevant standard specification | 394 | M | 11820
[7 empty] | Civil total |  | 6903862.3646
[7 empty] | Electrical & Civil total |  | 15292241.7916

## 8. pocharam SS
Pocharam SS Schedules
Name of the work: Estimate for erection of new 33/11 KV SS with connected 33 KV and 11 KV lines at Pocharam (V) in Patancheru (M) at Patancheru Division of Sangareddy Circle(WBS No: S-1740-90-06-03-02-001)
S.No | SSR Code | Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR10105 | 49 | ERECTION OF S.S. STRUCTURE: Coping of 0.45x0.45x0.45Mt with 1:8 slope Using form boxes (0.031Cumt.) | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 29400
2 | SWR10343 | 41 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 98400
3 | SWR10356 | 3.53 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x0.15M with CC mix of ratio 1:3:6 Using form boxes (0.086 Cu.Mt)*41 = 3.53 M3 with 40mm HBG metal. | Civil Work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 23223.87
4 | SWR10356 | 36.08 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt)*41 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 237370.32
5 | SWR11890 | 1.27 | ERECTION OF S.S. STRUCTURE: Coping of 0.45x0.45x0.45Mt with 1:8 slope Using form boxes (0.031Cumt.) | Civil work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | M3 | 4944.11
6 | SWR11331 | 41 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of poles with two coats of white cement (including cost of paint). | Electrical work | Paint-9.1M PSCC Poles as desc SSR | As per relevent standard specification | 485 | EA | 19885
7 | SWR11889 | 9.3 | Fabrication of 100 X 50mm MS Channel for formation of 11kV and 33kV bays: Fabrication and erection of M.S,Channel 100x50mm for forming of 33KV & 11 KV Bays as per standard specifications to facilitate stringing of bus, erection of LA sets, AB Switches bolts & Nuts etc. including painting with one coats of red oxide and two coats of Aluminium paint. GI bolts&nuts shall be used. | Electrical work | Fabr & Erect-MS Chnl 100x50mm for SS Bay | As per relevent standard specification | 6600 | TO | 61380
8 | SWR10404 | 217 | Erection of 33kV and 11kV Strung Bus with Panther (200Sqmm) ACSR Conductor: Erection of 33kV and 11kV Bus over the Substation structures with 200sqmm Panther ACSR conductor and giving Jumpers to connect the Switch gear by providing the suitable T clamps and round clamps suitable to Post type insulators & Insulators. | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 71106.56
9 | SWR10884 | 100 | Connection of equipment to busand or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Electrical work | Conn. of equip/bus single zebra/panther | As per relevent standard specification | 224 | EA | 22400
10 | SWR10392 | 7 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 31500
11 | SWR10393 | 15 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 48000
12 | SWR10393 | 1 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 3200
13 | SWR21240 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt). | Electrical work | Hoisting post ins&hrd wr 1panther 33kv | As per relevent standard specification | 781 | EA | 1562
14 | SWR21241 | 4 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 11kv | As per relevent standard specification | 507 | EA | 2028
15 | SWR10881 | 22 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 3124
16 | SWR23224 | 73 | Excavation of pit in all types of soils of size 2.2x2.2x0.85Mts.for Construction of Plinths for VCB (33KV & 11 KV ) | Earth work | Excavate-Pit for 33KV VCB | As per relevent standard specification | 331 | M3 | 24163
17 | SWR20685 | 76 | Providing of Base concreting (2.2x2.2x0.15 Mts) with 1:3:6 Concrete mix. Using form boxes, Providing of Concreting (2x2x1.0mts) with 1:3:6 Cocrete mix. Plastering of the plinth for smooth finishing with 12mm thick 1:3 cement motor and providing two coats white washing for part of the plinth above groung level. | Civil work | Cement concrete with 40MM metal VCB plin | As per relevent standard specification | 5160 | M3 | 392160
18 | SWR10460 | 3 | Erection of 33kv VCB: Assembling the VCB Structures and mounting the VCBs over the already erected foudation including wiring of Breaker Control Panel/CTs, erection of CTs and control pannel providing Jumpers. | Electrical work | Erection of 33kv VCB | As per relevent standard specification | 12500 | EA | 37500
19 | SWR10461 | 8 | Erection of Switchgear complete for 11 kV VCB includes Assembling the VCB Structures and mounting the VCBs over the already erected foudation including wiring of Breaker Control Panel/CTs, erection of CTs and control pannel providing Jumpers. | Electrical work | Erection of 11kv VCB | As per relevent standard specification | 12000 | EA | 96000
20 | SWR10396 | 2 | Erection of 33KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 1760
21 | SWR10397 | 1 | Erection of 11 KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 11kv LA stn type incl earthing | As per relevent standard specification | 559 | SET | 559
22 | SWR10398 | 6 | Erection of 11 KV Lightening Arrestors line type complete including jumpering. | Electrical work | Erect of 11kvLA line type incl earthing | As per relevent standard specification | 505 | SET | 3030
23 | SMR11482 | 32 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 111552
24 | SWR10357 | 32 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 39494.4
25 | SWR10920 | 655 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification.75x8 mm MS flat for Earth mat and connecting to electrodes. | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 42575
26 | SWR10919 | 1280 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification. 50x6 mm MS flat for raisers, double flat shall be run for structure poles raisers & equipment earthing. | Electrical work | Earthing for raisers of SS Flat 50x6 mm. | As per relevent standard specification | 41 | RMT | 52480
27 | SMR40033 | 4 | Providing of double earthing for neutral with flexible copper jumpers of adequate size including arrangement by fixing M.S.Channel 100x50mm. | Electrical work | SupCU Flexi jumper for Power T/F Neutral | As per relevent standard specification | 4725 | EA | 18900
28 | SWR11771 | 11 | Erection of 24 Volts Battery along with Charger on the VCB plinth and giving DC supply to VCB's. | Electrical work | Erect-24V Batery with Chrgr incl grot-SS | As per relevent standard specification | 1050 | EA | 11550
29 | SWR11879 | 1700 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable includes excavation of earth and back filling with sand and earth in alternate layers . The cable termination shall be made by providing proper size lugs and shall be identified with colours. | Electrical work | Lay-4C/10C 2.5Sqmm Control Cable | As per relevent standard specification | 27 | M | 45900
30 | SWR10463 | 1 | Erection of 25 kVA Three phase Station Transformer on the Substation Structures and giving jumpers/connections on HT side to the 11kV bus. Belting angle shall be provided both sides of DTR for securing DTR firmly in position. | Electrical work | Erection of Three Phase DTRs | As per relevent standard specification | 1139.95 | EA | 1139.95
31 | SWR10674 | 1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
32 | SMR40045 | 1 | Supply of AC Panel Board includes: Fixing of 1 No.100A, MCCB, 10kA capacity of any standard make including material cost. Fixing of suitable panel box 3x3x1 with M.S.Sheet of 16 SWG with front door compartments inclusive of material cost & powder coating (with C Channel ). Fabrication of panel Fixing of 96x96mm analog voltmeter with VSS switch Fixing of 20A HRC fuse Fixing of 3 phase supply indicator kwith HRC fuses Supply and fixing of 6 Sqmm copper flexible wire (PVC) Fixing of Stud type TBs for outgoing feeder Fixing of Epoxy bus supports. | Electrical work | Supply of AC Supply panel complete | As per relevent standard specification | 42000 | EA | 42000
33 | SMR40044 | 1 | Supply of DC Panel Board Fixing of suitable panel box of size 6'x6'x1' with M S sheet of 16 SWG with back doors (4'x6') and on front side with provision to fix up bakelite hylam sheet size of 4'x6' including cost of the panel with powder coating. Fixing of best quality of angles for panel. Fixing of C Channelfor panel. Fabrication of control panel including making suitable holes and board Fixing of Stud type TBs for outgoing feeder Fixing of 24V DC pilot lamps of standard make Fixing of healthy trip push buttons with LED lamp Fixing of plain switches for alarm acceptance and for PTR signal Fixing of ON/OFF push buttons Fixing of digital volt meter for 11kV Fixing of VSS of standard make, Fixing of Engraved AL plates for Alarm panel of various VCB Laying of 2.5Sqmm copper flexible wire for internal wiring . Fixing of digital frequency meter Fixing of Copper lugs and ferrules for internal wiring. Fixing of 4" Gang bells 24V DC Fixing of flow diagram with rading strip Fixing of HRC fuse units | Electrical work | Supply of DC Anunc.relay panel 8 feeders | As per relevent standard specification | 42500 | EA | 42500
34 | SWR20025 | 1 | fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supplied by tenderer. | Electrical work | 33/11kv S.S Erection of AC&DC Panel | As per relevent standard specification | 7871.85 | SET | 7871.85
35 | SWR10342 | 8 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 12000
36 | SWR10956 | 8 | Fixing of Metal halide/LED lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5M GI pipe complete. | Electrical work | Fixing of LED/Metal halide complete. | As per relevent standard specification | 1268 | EA | 10144
37 | SWR20028 | 8 | Supply and Fixing of junction box and Providing with proper Fuse protection and required glauds suitable for Cable Terminations. The box shall be fixed on the pole. | Electrical work | 33/11kv S.S Yard lighting junction box | As per relevent standard specification | 351.9 | EA | 2815.2
38 | SWR21750 | 4 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply and fixing of PT Marshalling box | As per relevent standard specification | 1139.85 | EA | 4559.4
39 | SMR40088 | 1 | Supply and fixing of filled sand bucket set complete (4 Nos. Buckets) with stand to mount fire buckets. | Electrical work | Sup Fire Buckets Stand with Buckets | As per relevent standard specification | 1386 | SET | 1386
40 | SMR40087 | 2 | Supply and fixing of CO2 Cylinder set as per IS2878 Specifications. | Electrical work | Sup TrollyMounted Co2 Cylinders(IS-2878) | As per relevent standard specification | 9240 | EA | 18480
41 | SWR11895 | 1 | Supplying and fixing of feeder indicator board to each of the 3Nos feeder breakers and LV breaker, danger boards made of 1'x1' and properly mounted on the structures. The letters written on the borad shall be 1.5"size with blue colour and background shall be of white colour | Electrical work | S&F-33/11KV SS Feeder Indicator Board | As per relevent standard specification | 551 | SET | 551
42 | SWR20032 | 1 | Supply and fixing of wooden board of size 3'x2'.5'indicating the layout of the Switch yard. | Electrical work | Sup &fix of board ind Switchyard layout | As per relevent standard specification | 1654 | EA | 1654
43 | SMR40086 | 1 | Supply and Erection of Permanent Name Board of on 3'x4' steel sheetmounted on steel frame as described in Specification. | Electrical work | Sup 33/11kv S.S Permanent name board | As per relevent standard specification | 10238 | EA | 10238
44 | SMR40076 | 1 | Supply of Digital clamp meter. | Electrical work | Supply of Digital clamp meter. | As per relevent standard specification | 2888 | EA | 2888
45 | SMR40064 | 1 | Supply of Rechargeable LED torch light of Standard make. | Electrical work | Sup Rechargeable LED torch light. | As per relevent standard specification | 1733 | EA | 1733
46 | SMR40063 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box containing ‘D’Spanners from size 6 to 54, Hammer small and big size, Ring spanners from 6 to 28, Adjustable spanner, Pipe wrench, Cutting Plier, Nose plier, Tester, insulated Screw drive. | Electrical work | SupTaparia Tool kit complete as per Spec | As per relevent standard specification | 4925 | SET | 4925
47 | SWR22090 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Electrical work | Sup& fix safety inst/SS Op. inst board | As per relevent standard specification | 2205 | EA | 2205
48 | SMR11598 | 8 | Supply of 25 W LED lamp with fitting of philips make | Electrical work | S-25W LED fixture set | As per relevent standard specification | 3200 | EA | 25600
49 | SMR12378 | 1 | Supply of Alluminum Ladder(20 feet) | Electrical work | S-10ft Aluminium Ladder | As per relevent standard specification | 1654 | EA | 1654
50 | SMR40075 | 1 | Supply of Megger (2000 ohms, 0-2.5kv) | Electrical work | Supply of Earth megger (1000v) | As per relevent standard specification | 8085 | EA | 8085
51 | SMR11599 | 4 | Supply of Earth Discharging Rod 8 feet length, 3 mm thickness. | Electrical work | S-Earth Rod 8ft Long 3mm Thick | As per relevent standard specification | 1000 | EA | 4000
52 | SMR11488 | 240 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 28200
53 | SMR11591 | 72 | Supply of PG clamps for panther 2 bolted 800 A. | Electrical work | S-Al. alloy three bolted PG clamps 800A | As per relevent standard specification | 130 | EA | 9360
54 | SWR20029 | 250 | Supply and Laying of 2 core/4 core cable includes excavation earth and back filling with sand and earth in alternate layers as shown in the sketch. The cable termination shall be made by providing proper size of lugs at both ends of the cable termination. | Electrical work | 33/11kv S.S laying of 2/4core for light | As per relevent standard specification | 50 | M | 12500
55 | SWR20308 | 41 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 16698.89
56 | SWR20307 | 8 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 2172.16
57 | SWR11860 | 11 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 29923.74
58 | SWR10150 | 14.7 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 9071.37
59 | SWR10206 | 14.7 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 3248.7
60 | SWR10524 | 14.7 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 2719.5
61 | SWR11220 | 650 | Loading and unwinding of Panther conductor. | Electrical work | Load-Unwinding Panther conductor | As per relevent standard specification | 3 | M | 1950
62 | SWR11221 | 650 | Unloading and unwinding of Panther conductor. | Electrical work | Unload-Unwinding Panther conductor | As per relevent standard specification | 2 | M | 1300
63 | SWR12416 | 3 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 6
64 | SWR10631 | 3 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 6
65 | SWR10618 | 3 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 195
66 | SWR10632 | 3 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 195
67 | SWR10212 | 3 | Loading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | LOADING of 11kv Pin/Post/Solid Core Insu | As per relevent standard specification | 1 | CRT | 3
68 | SWR10530 | 3 | Unloading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | UNLOADING of 11kv Pin/Post/Solid Core In | As per relevent standard specification | 1 | CRT | 3
69 | SWR11701 | 1700 | Loading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | Load-PVC Control Cable 10C | As per relevent standard specification | 1 | M | 1700
70 | SWR11712 | 1700 | Unloading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | UnLoad-PVC Control Cable 10C | As per relevent standard specification | 1.02 | M | 1734
71 | SWR11691 | 1 | Loading of 3Ph 25KVA Distribution Transformer. | Electrical work | Load-3Ph 25KVA DTR | As per relevent standard specification | 252 | EA | 252
72 | SWR11692 | 1 | UnLoading of 3Ph 25KVA Distribution Transformer. | Electrical work | UnLoad-3Ph 25KVA DTR | As per relevent standard specification | 202 | EA | 202
73 | SWR10200 | 2 | Loading of 33/11 KV Current Transformers/ Potential Transformers. | Electrical work | LOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 165 | EA | 330
74 | SWR10266 | 6 | Loading of 33 KV10 KA LAs Station type. | Electrical work | LOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 41 | EA | 246
75 | SWR10584 | 6 | Unloading of 33 KV10 KA LAs Station type. | Electrical work | UNLOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 35 | EA | 210
76 | SWR10265 | 18 | Loading of 11 KV10 KA LAs Line type. | Electrical work | LOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 576
77 | SWR10583 | 18 | Unloading of 11 KV10 KA LAs Line type. | Electrical work | UNLOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 576
78 | SWR10264 | 3 | Loading of 11 KV10 KA LAs Station type. | Electrical work | LOADING of 11 KV,10 KA LAs Station type | As per relevent standard specification | 32 | EA | 96
79 | SWR10582 | 3 | Unloading of 11 KV10 KA LAs Station type. | Electrical work | UNLOADING of 11 KV,10 KA LAs Station typ | As per relevent standard specification | 32 | EA | 96
80 | SWR10239 | 7 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 882
81 | SWR10557 | 7 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 553
82 | SWR10238 | 12 | loading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 960
83 | SWR10556 | 12 | Unloading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 960
84 | SWR11224 | 11 | Loading and Unloading of 12V/24V Battery Set. | Electrical work | Load/Unload-12V/24V Battery Set | As per relevent standard specification | 23 | EA | 253
85 | SWR10402 | 1 | Erection of 11kv Potential Transformer sets complete including jumpering. The LV side of the PT shall be provided with proper fuse protection mounted in separate marshalling boxwith proper size cable glands etc. The box shall be mounted on the Substation structure. | Electrical work | Erection of 11kv three phase PT s | As per relevent standard specification | 800 | SET | 800
86 | SWR10518 | 2 | Unloading of 33/11 KV Current Transformers/ Potential Transformers | Electrical work | UNLOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 128 | EA | 256
87 | SWR10401 | 1 | Erection of 33 KV single phase PTs | Electrical work | Erection of 33kv single phase PT s | As per relevent standard specification | 1079 | SET | 1079
88 | SMR11608 | 1 | Supply of 11kv HG fuse set including providing of jumpers | Electrical work | S-11KV HG Fuse Set | As per relevent standard specification | 1733.75 | SET | 1733.75
89 | SWR10395 | 1 | Erection of 11kv HG fuse set including providing of jumpers | Electrical work | Erect. of 11kv HG Fuseset incl earthing | As per relevent standard specification | 740.52 | SET | 740.52
90 | SMR40067 | 2 | Supply of Hand Gloves | Electrical work | Supply of Hand Gloves | As per relevent standard specification | 289 | SET | 578
91 | SMR40071 | 2 | Supply of Safety Helmets of standard make | Electrical work | Supply of Safety Helmet of standard make | As per relevent standard specification | 231 | EA | 462
92 | SMR25233 | 41 | Supply of PSCC Pole 9.1Mtr 280kg | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 127485.81
93 | SMR22745 | 8700 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KG | 499815
94 | SMR12321 | 3275 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 184775.5
95 | SMR12322 | 3200 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 180800
96 | SMR25232 | 8 | Supply of PSCC Pole 8Mtr 140kg | Electrical work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 12640
97 | SMR12315 | 7 | Supply of 33KV 800A DB Break AB Switch | Electrical work | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 284611.46
98 | SMR12316 | 3 | Supply of 11KV 800A DB Break AB Switch | Electrical work | S-11KV 800A DB Break AB Switch | As per relevent standard specification | 30847.46 | EA | 92542.38
99 | SMR12317 | 12 | Supply of 11KV 400A DB Break AB Switch | Electrical work | S-11KV 400A DB Break AB Switch | As per relevent standard specification | 18150 | EA | 217800
100 | SMR25211 | 1 | Supply of 11KV 400A Conv ABSwitch with Insulator | Electrical work | S-11KV 400A Conv ABSwitch with Insulator | As per relevent standard specification | 11754 | EA | 11754
101 | SWR22092 | 0.83 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 634.95
102 | SWR12087 | 9 | Excavation of Pole pits of size 2.4"x2.4"x8.2" (0.75M x 0.75M x 2.5M) 1.406 cum for 12.5mtrs Spun Poles including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except hard rock requiring blasting. | Earth work | Excvt Pit ext HardBlst 0.75Mx0.75Mx2.5M | As per relevent standard specification | 990 | EA | 8910
103 | SWR10107 | 5 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 3500
104 | SWR10112 | 5 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | As per relevent standard specification | 1680 | EA | 8400
105 | SWR10105 | 6 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 3600
106 | SWR10350 | 9 | Erection of Spun PSCC poles 12.5 Mtrs in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical work | Erection of Spun pole 12.5Mt | As per relevent standard specification | 4115.7 | EA | 37041.3
107 | SWR10978 | 10 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 41652.8
108 | SWR11083 | 6 | Erection of 9.1 M long PSCC poles for Strut in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical work | Erec of 9.1 Mts PSCC poles for stuts | As per relevent standard specification | 2400 | EA | 14400
109 | SWR10981 | 6 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Horizontal Cut point for 33 KV line | As per relevent standard specification | 1759.5 | EA | 10557
110 | SWR10653 | 2 | Formation of 11 kv cut points (Vertical/Horizantal) including fixing of 11 KV Cross arms,clamps, strain insulators sets complete with hardware and stays (Bows and Eye-bolts), Excluding the cost of pit Excavation and pole erection. The contractor has to supply GI Bolts and Nuts. | Electrical work | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1350 | EA | 2700
111 | SWR10356 | 13.634 | Concreting the location after erection of 12.5Mtrs/11 Mtrs pole/9.1 Mtrs poles with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole. Using form boxes for 4 No's spun poles (0.75x0.75x1.95 Mts) *4 = 5.776 cu mtr , 4 No's11.0 mtr poles (0.76x0.76x1.83mtrs)*4 = 4.228 cu mtr and 6 No's 9.1 mtr poles (0.6x0.6x1.5mtrs)*6 = 3.24 cu mtr. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 89698.086
112 | SWR10366 | 0.83 | Paving of the 100 sqmm AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 12600.06 | KM | 10458.0498
113 | SWR10703 | 0.45 | Paving of the 55 Sqmm AAA Conductor for Double Circuit (6 Conductors) and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location.) | Electrical work | Stringing of 55sqmm 33/11kv Line 6 Cond | As per relevent standard specification | 16000 | KM | 7200
114 | SMR11488 | 40 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 4700
115 | SWR11185 | 9 | Sub Transportation of Spun Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt any Spun Pole incl. L&UL<10KM | As per relevent standard specification | 771.38 | EA | 6942.42
116 | SWR11180 | 10 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 4319.7
117 | SWR20308 | 6 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 2443.74
118 | SWR10191 | 2 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 404
119 | SWR10509 | 2 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 200
120 | SWR11860 | 2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 5440.68
121 | SWR10150 | 1.568 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 967.6128
122 | SWR10206 | 1.568 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 346.528
123 | SWR10524 | 1.568 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 290.08
124 | SWR10211 | 7 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 21
125 | SWR10529 | 7 | Unloading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 21
126 | SWR11248 | 54 | Loading of 11KV Polymer Pin Insulators with GI pins | Electrical work | Load-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 54
127 | SWR11249 | 54 | Unloading of 11KV Polymer Pin Insulators with GI pins | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 54
128 | SWR12416 | 4 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 8
129 | SWR10631 | 4 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 8
130 | SWR10618 | 2 | Loading of 33KV Metal parts bag of 25 nos | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 130
131 | SWR10632 | 2 | Unloading of 33 KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 130
132 | SWR12402 | 2 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 96
133 | SWR12421 | 2 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 96
134 | SWR10319 | 71 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 75 x 8 mm MS Flat | Electrical work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31 | EA | 2201
135 | SWR10322 | 40 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 75 x 8 mm MS Flat | Electrical work | Fab Stay clamps with 75x8 mm MM Flat | As per relevent standard specification | 42 | EA | 1680
136 | SWR10320 | 44 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 50 x6 mm MS Flat | Electrical work | Fab Back clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 15 | EA | 660
137 | SWR10378 | 21 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevent standard specification | 32 | EA | 672
138 | SWR10354 | 5 | Erection of 33 kv Stay set complete including fixing of bow ,fixing and binding of Eye bolt, Anchor rod, guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. | Electrical work | Assembly and erection of Stay set 33kv | As per relevent standard specification | 684.53 | SET | 3422.65
139 | SWR21190 | 5 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock,Hard rock Requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 2600
140 | SMR25238 | 19 | Supply of PSCC Spun Pole 12.5Mtr | Electrical work | S-PSCC Spun Pole 12.5Mtr | As per relevent standard specification | 15635.59 | EA | 297076.21
141 | SMR25236 | 8 | Supply of PSCC Pole 11Mtr 365 Kg | Electrical work | S-PSCC Pole 11Mtr 365 Kg | As per relevent standard specification | 5399 | EA | 43192
142 | SMR25233 | 4 | Supply of PSCC Pole 9.1Mtr 280kg | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 12437.64
143 | SMR22745 | 600 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KG | 34470
144 | SMR12321 | 420 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 23696.4
145 | SMR25205 | 500 | Supply of MS Channel 75x40 mm | Electrical work | S-MS Channel 75x40 mm | As per relevent standard specification | 58.45 | KG | 29225
146 | SMR12322 | 250 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 14125
147 | SMR25207 | 310 | Supply of MS Angle 65X65X6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 17747.5
148 | SMR25206 | 160 | Supply of MS Angle 50x50x6 | Electrical work | S-MS Angle 50x50x6 | As per relevent standard specification | 58.15 | KG | 9304
149 | SMR25231 | 5 | Supply of 33KV MS Stay Set with BasePlate | Electrical work | S-33KV MS Stay Set with BasePlate | As per relevent standard specification | 1035 | SET | 5175
150 | SWR22092 | 2.35 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 11 kv line. | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 1797.75
151 | SWR10107 | 3 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mtrs PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 2100
152 | SWR10112 | 2 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | As per relevent standard specification | 1680 | EA | 3360
153 | SWR10105 | 25 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1/8.0 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 15000
154 | SWR10978 | 5 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 20826.4
155 | SWR10343 | 19 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 45600
156 | SWR11083 | 6 | Erection of 9.1 M long PSCC poles for Strut in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical work | Erec of 9.1 Mts PSCC poles for stuts | As per relevent standard specification | 2400 | EA | 14400
157 | SWR10342 | 28 | Erection of 8.0 Mts PSCC Poles including fixing of 11 KV X arm and top cleats and fixing of Pin insulators complete with necessary hard ware for tangential locations excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 42000
158 | SWR10653 | 26 | Formation of 11 kv cut points (Vertical/Horizantal) including fixing of 11 KV Cross arms,clamps, strain insulators sets complete with hardware and stays (Bows and Eye-bolts), Excluding the cost of pit Excavation and pole erection. The contractor has to supply GI Bolts and Nuts. | Electrical work | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1350 | EA | 35100
159 | SWR10356 | 15.545 | Concreting the location after erection of 11 / 9.1/8.0 Mtrs pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole. Using form boxes for 1 No's 11 poles (0.75x0.75x2 Mts) *1 = 1.125 cu mtr , 6 No's 9.1 mtr poles (0.6x0.6x1.5mtrs)*6 = 3.24 cu mtr and 21 No's 8.0 mtr poles (0.6x0.6x1.5mtrs)*21 = 11.34 cu mtr | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 102270.555
160 | SWR10365 | 1 | Paving of the conductor 55 Sqmm Single Circuit (3 Conductors) AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 3 Cond | As per relevent standard specification | 8500 | KM | 8500
161 | SWR10703 | 0.25 | Paving of the conductor 55 Sqmm Double Circuit (6 Conductors) and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location. | Electrical work | Stringing of 55sqmm 33/11kv Line 6 Cond | As per relevent standard specification | 16000 | KM | 4000
162 | SMR11488 | 60 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 7050
163 | SWR10206 | 1.383 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 305.643
164 | SWR10524 | 1.383 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 255.855
165 | SWR10134 | 1.383 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 812.5402
166 | SWR11248 | 87 | Loading 11KV Polymer Pin Insulator with GI pins | Electrical work | Load-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 87
167 | SWR11249 | 87 | Unloading 11KV Polymer Pin Insulator with GI pins | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 87
168 | SWR11862 | 2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 20 KM and upto 30 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 7382.76
169 | SWR10191 | 2 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 404
170 | SWR10509 | 2 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 200
171 | SWR11180 | 5 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 2159.85
172 | SWR20307 | 28 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 7602.56
173 | SWR20308 | 25 | Sub Transportation of 9.1M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 10182.25
174 | SWR10228 | 11 | Loading of 11 KV V - Cross arms | Electrical work | LOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 44
175 | SWR10546 | 11 | Unloading of 11 KV V - Cross arms | Electrical work | UNLOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 44
176 | SWR12402 | 8 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 384
177 | SWR12421 | 8 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 384
178 | SWR10251 | 5 | Loading of 11 KV Top fittings | Electrical work | LOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 5
179 | SWR10569 | 5 | Unloading of 11 KV Top fittings | Electrical work | UNLOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 5
180 | SWR12416 | 10 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 20
181 | SWR10631 | 10 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 20
182 | SWR10353 | 17 | Erection of 11 kv Stay set complete including fixing of bow, fixing and binding of Eye bolt,Anchor rod,guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Assembly and erection of Stay set11kv&LT | As per relevent standard specification | 606.85 | SET | 10316.45
183 | SWR21190 | 17 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In Hard Gravel and Hard murram not requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 8840
184 | SWR10319 | 69 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 75 x 8 mm MS Flat | Electrical work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31 | EA | 2139
185 | SWR10322 | 51 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 75 x 8 mm MS Flat | Electrical work | Fab Stay clamps with 75x8 mm MM Flat | As per relevent standard specification | 42 | EA | 2142
186 | SWR10320 | 89 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 50 x 6 mm MS Flat | Electrical work | Fab Back clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 15 | EA | 1335
187 | SWR10323 | 136 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 50 x 6 mm MS Flat | Electrical work | Fab Stay clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 25 | EA | 3400
188 | SWR10378 | 58 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevent standard specification | 32 | EA | 1856
189 | SMR25236 | 5 | Supply of PSCC Pole 11Mtr 365 Kg | Electrical work | S-PSCC Pole 11Mtr 365 Kg | As per relevent standard specification | 5399 | EA | 26995
190 | SMR25233 | 25 | Supply of PSCC Pole 9.1Mtr 280kg | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 77735.25
191 | SMR25232 | 28 | Supply of PSCC Pole 8Mtr 140kg | Electrical work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 44240
192 | SMR25218 | 11 | Supply of 11KV V X-Arms with MS Angle 65x65x6 | Electrical work | S-11KV V X-Arms with MS Angle 65x65x6 | As per relevent standard specification | 743 | EA | 8173
193 | SMR25227 | 5 | Supply of 11KV Middle Phase Raiser | Electrical work | S-11KV Middle Phase Raiser | As per relevent standard specification | 519 | EA | 2595
194 | SMR22745 | 225 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KG | 12926.25
195 | SMR25205 | 360 | Supply of MS Channel 75x40 mm | Electrical work | S-MS Channel 75x40 mm | As per relevent standard specification | 58.45 | KG | 21042
196 | SMR25207 | 144 | Supply of MS Angle 65X65X6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 8244
197 | SMR25206 | 289 | Supply of MS Angle 50x50x6 | Electrical work | S-MS Angle 50x50x6 | As per relevent standard specification | 58.15 | KG | 16805.35
198 | SMR12321 | 132 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 7447.44
199 | SMR12322 | 232.5 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 13136.25
200 | SMR25225 | 24 | Supply of 11KV MS Stay Sets without BasePlate | Electrical work | S-11KV MS Stay Sets without BasePlate | As per relevent standard specification | 622 | SET | 14928
[6 empty] | Total |  |  | 4868018.6098
1 | SWR34179 | 12 | Levelling the site with the help of JCB including cost, conveyance of all materials,hire charges etc complete for finished item of work. | JCB | Hire-JCB to Level & Clear the Site | As per relevant standard specifiction | 2164.1 | H | 25969.2
2 | SWR33015 | 107.09 | Earth Work Mass Excavation (Ordinary soil) to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions, labour and material charges etc., complete as directed by the engineer-incharge. | Earth Work | Excavation in Ordinary Soil | As per relevant standard specifiction | 347 | M3 | 37160.23
3 | SWR33028 | 22.37 | PCC (1:4:8) for levelling course using 40mm size hard broken Granite stone including cost and conveyance of all materials, HBG metal for foundations and leveling course and as directed by the Engineer- in - charge etc complete for finished item of work. | Concrete | PCC with 40mm Metal (1:4:8) | As per relevant standard specifiction | 4082 | M3 | 91314.34
4 | SWR33041 | 137.72 | CRS masonry in CM (1:6) using Hard Granite Stones including cost and conveyance of all materials, seignorage charges, labour charge for construction and for dressing stones to required size and shape, dewatering, scaffolding, cutting for all leads and lifts, all incidental charges etc .complete for finished item of work as directed by the Engineer - in - charge. | Masonry | CRS Masonary CM(1:6) 2nd Sort | As per relevant standard specifiction | 4454 | M3 | 613404.88
5 | SWR33068 | 20.3 | Construction of brick masonary in CM(1:6) including cost and conveyance of all materials, labour charges etc. complete for finished item of work | Masonry | Brick Masonary in CM(1:6) GFloor | As per relevant standard specifiction | 7634 | M3 | 154970.2
6 | SWR33052 | 858.73 | Supplying and filling with borrowed gravel, watering, ramming, consolidating thoroughly complying with the standard specification including cost and conveyance of all materials, labour charges,hire charges of machnery,with all leads and incidental charges etc complete for finished item work | Earth Work | S&Filling with Borrowed Gravel | As per relevant standard specifiction | 435 | M3 | 373547.55
7 | SWR33098 | 6.53 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (a) Footings | RCC | RCC Footing: M20Gr, Steel Centering | As per relevant standard specifiction | 8221 | M3 | 53683.13
8 | SWR33100 | 4.77 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (b) Columns | RCC | RCC Column GF: M20Gr, Steel Centering | As per relevant standard specifiction | 10916 | M3 | 52069.32
9 | SWR33099 | 1.6 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (c) Plinth Beams | RCC | RCC Plinth Beam: M20Gr, Steel Centering | As per relevant standard specifiction | 10641 | M3 | 17025.6
10 | SWR33107 | 0.67 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (d) Lintels | RCC | RCC Lintel GF: M20Gr, Steel Centering | As per relevant standard specifiction | 11076 | M3 | 7420.92
11 | SWR33114 | 5.63 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (e) Sunshade | RCC | RCC Sunshade GF: M20Gr, Steel Centering | As per relevant standard specifiction | 1162 | M2 | 6542.06
12 | SWR33121 | 2.35 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (f) Roof Beams | RCC | RCC Roof Beam GF: M20Gr, Steel Centering | As per relevant standard specifiction | 10651 | M3 | 25029.85
13 | SWR33128 | 6.95 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel. (g) Slab of 130 mm thick | RCC | RCC Roof Slab GF: M20Gr, Steel Centering | As per relevant standard specifiction | 10202 | M3 | 70903.9
14 | SWR33144 | 2.2 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) / Mild steel (MS) steel bars (Fe 415/ Fe 500 grade as per IS 1786-1979) of different diameters for RCC works complete for finished item of work in all floors.( APSS No.126) | Steel | Reinforcement Steel Fe 415/500 | As per relevant standard specifiction | 76127 | TO | 167479.4
15 | SWR33163 | 320.34 | Providing plastering of 20mm thick to all uneven faces of walls and ceiling of superstructure in two coats with base coat in CM 1:6 of 16mm thick and top coat in Cm 1:4 4mm thick with dubara sponge finish | Plastering | Plastering 20mm (16mm+4mm)GFloor | As per relevant standard specifiction | 411 | M2 | 131659.74
16 | SWR33184 | 145.5 | Raised pointing in CM(1:3) including curing, cost and conveyance of all materials and labour charges for complete item of work. | Pointing | Raised Pointing to CRS Masonary CM(1:3) | As per relevant standard specifiction | 94 | M2 | 13677
17 | SWR33156 | 54.87 | Providing impervious coat over RCC roof slab surfaces to requried slopes with 20mm thick in CM 1:3 pro mixed with approvaled brand of water proffing compound as the rate of 1 kg per bag of cement inclding cost and conveyance of all materials | Roof plastering | Impervious Coat 20mm CM(1:3) GFloor | As per relevant standard specifiction | 440 | M2 | 24142.8
18 | SWR33264 | 5.7 | Supply and fixing of Flush type Doors with 35mm Thick Flush Shutters with Bondwood solied Block Board Type Faced on Both the sides with Commercial Type Plywood for finished item work as directed by the Engineer - in- charge. | Doors | S&F MT Wood Frame & Door-Laminate | As per relevant standard specifiction | 6799.02 | M2 | 38754.414
19 | SWR33278 | 5.76 | Supply and Fixing of powder coated Aluminium sliding windows with fixed glass panels using aluminium sections 62x32x1.2mm providing 5mm plain glass fixed to frame with beading gasket and glazing clips with all accessories,locking arrangements including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Windows | S&F Powder Coated Al Window | As per relevant standard specifiction | 3535.64 | M2 | 20365.2864
20 | SWR33310 | 6.25 | Supplying and fixing of MS safety grill with peripheral frame of ISA 25x25x4mm and horizontal & vertical 8mm square rods and including cost and coveyance of all mateirals with all leads and lifts, labour charges, painting charges complete for finished item of work | Window grills | S&F of MS Safety Grill | As per relevant standard specifiction | 2539 | M2 | 15868.75
21 | SWR33219 | 26.5 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and approved size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and pointing with cement, labour etc, complete for finished item of work. | Flooring | Polished Shabad Flooring 20mm CM(1:3) | As per relevant standard specifiction | 660 | M2 | 17490
22 | SWR33236 | 6.94 | Providing skirting with tandoor blue slabs including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Flooring | Polished Shabad Skirting CM(1:3) | As per relevant standard specifiction | 726 | M2 | 5038.44
23 | SWR33029 | 31.71 | Plain Cement contrete - Nominal Mix (1:3:6) using 40 mm metal with concrete mixture including cost and conveyance of all materials labour charges etc. complete for finished iitem of work and as directed by the engineer-in-charge. | Concrete | PCC with 40mm Metal (1:3:6) | As per relevant standard specifiction | 4383 | M3 | 138984.93
24 | SWR33030 | 7.2 | PCC(1:2:4) using 10 to 12 mm aggregate including cost and conveyance of all materials labour charges etc., complete for finished iitem of work and as directed by the engineer-in-charge. | Concrete | PCC with 20mm Metal (1:2:4) | As per relevant standard specifiction | 5498 | M3 | 39585.6
25 | SWR33057 | 76.92 | Supply and Spreading of 20mm machine crushed metal including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Metal | S&Spreading of 20mm HBG Metal | As per relevant standard specifiction | 1514 | M3 | 116456.88
26 | SWR33403 | 120 | Supply and fixing of fencing of welded wire mesh (1" x 2") of 3mm dia with support channels of 75x 40mm and angles around of 30x30x3 mm including cost and conveyance of all materials, fabrication charges, painting charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Welded mesh | S&F MS Security Fencing Mesh (2"X2") | As per relevant standard specifiction | 2042 | M2 | 245040
27 | SWR33404 | 10.68 | Supply and fixing of MS gates of approved design including cost and conveyance of all materials,fabrication charges etc complete for finished item of work. | Gate | S&F MS Gate | As per relevant standard specifiction | 4579.89 | M2 | 48913.2252
28 | SWR33333 | 104.6 | Painting with two coats of OBD over a coat of primer including cost and conveyance of all materials ,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Painting | Painting with OBD 2Coats+Primer | As per relevant standard specifiction | 109.9 | M2 | 11495.54
29 | SWR33336 | 153 | Painting with two coats of ACE paint over a coat of primer including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Painting | Painting SnowCem/Apex 2 Coats+Primer | As per relevant standard specifiction | 195.91 | M2 | 29974.23
30 | SWR33329 | 201.9 | Painting with lovely cem three coats including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Painting | Painting with SuryaCem of 3 Coat | As per relevant standard specifiction | 70.47 | M2 | 14227.893
31 | SWR33415 | 7.3 | Manufacture, supply ,laying and fixing of 450mm dia. NP3 class R.C.C. socket and spigot pipes (rate per meter of effective length) including transportaion ,taxes and duties etc. complete for finished item of work and as directed by the Engineer-in-charge. | Electrification | S&F RCC Hume Pipe of 450mm dia | As per relevant standard specifiction | 1344 | RMT | 9811.2
32 | SWR33442 | 25 | S&F Conceal PVC Pipe 32mm dia in Slab including cost and conveyance of all material and labour charges complete for finished item of work | Electrification | S&F Conceal PVC Pipe 25mm dia in Slab | As per relevant standard specifiction | 85 | RMT | 2125
33 | SWR33441 | 15 | S&F Conceal PVC Pipe 20mm dia in Wall including cost and conveyance of all material and labour charges complete for finished item of work | Electrification | S&F Conceal PVC Pipe 25mm dia in Wall | As per relevant standard specifiction | 89 | RMT | 1335
34 | SWR33457 | 15 | Wiring with 2X1.0 Sqm(14/.3mm) PVC insulated flexiable copper cable in the existing metalic/Non metalic conduit pipe with 6A mini modular SP switch, mounted on metalic box covereds with appropriate front plate modules etc ceiling rose including cot and conveyance of all mateials, labour charges complete for light points, bell points and fan points in non residential builsing except circuit moving finished in all types masonary as directed by department. | Electrification | S&F Modular Switch LP,FP,EFP for NRBuild | As per relevant standard specifiction | 580 | EA | 8700
35 | SWR33461 | 2 | Supply and fixing of 6A 3/2 pin flush type plug socket with 6A flush type marked switch control on a common board with earth continuity including wire leads earth connections along with all labour charges etc. complete | Electrification | S&F Modular 3/2pin 6A Sockets | As per relevant standard specifiction | 469 | EA | 938
36 | SWR33464 | 2 | Supply and fixing of 16A 3pin flush type plug socket and 16A flush type fuse unit and 16A switch control. | Electrification | S&F Modular 3pin 16/6A Sockets | As per relevant standard specifiction | 437 | EA | 874
37 | SWR33484 | 4 | Supply and fixing of slanting holders with 100W bulb with all connections and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F Batten Holder | As per relevant standard specifiction | 116 | EA | 464
38 | SWR33545 | 4 | Supply and fixing of patty type tube light fitting with 4' 0" - 40W tube light,40W copper choke,starter,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F 20W LED Retro Tube Light | As per relevant standard specifiction | 868 | EA | 3472
39 | SWR33494 | 90 | Supply and run of 2 of 14/.3mm(1.00Sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | S&R 2 of 14/0.3mm (1.0sqmm) (FR) | As per relevant standard specifiction | 48 | RMT | 4320
40 | SWR33497 | 30 | Supply and run of 2 of 36/0.3 (2.5sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | S&R 2 of 36/0.3mm (2.5sqmm) (FR) | As per relevant standard specifiction | 95 | RMT | 2850
41 | SWR33520 | 1 | SPN Distribution board with IP-20 protection suitable for single phase 40A DP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 4Nos as out going MCBs in sheet steel enclosure including connections and cost of all material labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F 8wySPNDB IP-20,10kA-6-32A SPMCB 4No | As per relevant standard specifiction | 5038 | EA | 5038
42 | SWR33596 | 1 | Providing independent earthing for main switches,IC cutouts and motors using 40mm. Dia. B-class G.I.Pipe of 2.5' length duly providing 12mm. Dia. 6No. Holes and required bolts,nuts and washers,including filling with equal preparation of salt and charcoal in layers and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | Provd-Independent Earthing | As per relevant standard specifiction | 4891 | EA | 4891
43 | SWR33597 | 15 | Supply and run of No.8 SWG Copper wire including cost of all accessories and labour charges etc., Complete | Flooring | S&R No.8 SWG Copper Wire | As per relevant standard specifiction | 140 | RMT | 2100
44 | SWR33563 | 2 | Supply and Fixing of 48" ceiling fan of bajaj make(or equivalent make) including cost material,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Sanitary | S&F 1200mm (48'') Sweep Ceiling Fan | As per relevant standard specifiction | 2215 | EA | 4430
45 | SWR33224 | 15.8 | Supply and fixing of ceramic tiles fantacy for dadoing including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | Ceramic Tile Flooring 20mm CM(1:3) | As per relevant standard specifiction | 760 | M2 | 12008
46 | SWR34311 | 1 | Supply and fixing of 580mm x 440mm long Orissa pan of Parry, Neycer or Hindhusthan, make with 'P' or 'S' trap etc complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F Orissa Pan WC 580mmx440mm | As per relevant standard specifiction | 2178 | EA | 2178
47 | SWR34386 | 2 | Supply and Fixing 4" PVC floor trap including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F Floor Trap (Bell Mouth) 110mm | As per relevant standard specifiction | 269 | EA | 538
48 | SWR34382 | 2 | Supply,fixing 90mm dia. PVC Plain Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Sanitary | S&F 90mm dia Plain Bend PVC/SWR Pipe | As per relevant standard specifiction | 84 | EA | 168
49 | SWR34385 | 1 | Supply,fixing 90mm dia. PVC Door Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F 75mm dia Door Bend PVC/SWR Pipe | As per relevant standard specifiction | 81 | EA | 81
50 | SWR34286 | 1 | S&Fixing 150mm x 100mm SWG gully traps Ist class grating & constg brick masonry in CM (1:6) prop inter mediate chamber and fitted with CI frame etc complete. | Plumbing | S&F 150mmx100mm SWG Gully Trap | As per relevant standard specifiction | 749 | EA | 749
51 | SWR34377 | 6 | Supply and Fixing 4" dia 3M Single socket PVC pipe including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Sanitary | S&F 110mm dia 3M 1Socket PVC/SWR Pipe | As per relevant standard specifiction | 422 | RMT | 2532
52 | SWR34453 | 1 | Supply and Fixing 4" dia PVC cowl including labour charges etc. complete for finished item of work. | Plumbing | S&F 4" dia PVC Cowl | As per relevant standard specifiction | 23 | EA | 23
53 | SWR34444 | 1 | Construction of soak pit with 4' dia RCM rings upto a depth of 6' including cost and conveyance of all materials as directed by the engineer-in-charge. | Plumbing | Construct- 4' dia & 5' Ht Soak Pit | As per relevant standard specifiction | 2950 | EA | 2950
54 | SWR34361 | 20 | CPVC Pipes and Fittings a) 15.90mm OD Pipe - SDR 11 | Plumbing | S&F 15.90mm OD CPVC Pipe-SDR 11 | As per relevant standard specifiction | 239 | RMT | 4780
55 | SWR34362 | 100 | CPVC Pipes and Fittings b) 22.20mm OD Pipe - SDR 11 | Plumbing | S&F 22.20mm OD CPVC Pipe-SDR 11 | As per relevant standard specifiction | 313 | RMT | 31300
56 | SWR34363 | 100 | CPVC Pipes and Fittings c) 28.60mm OD Pipe - SDR 11 | Plumbing | S&F 28.60mm OD CPVC Pipe-SDR 11 | As per relevant standard specifiction | 410 | RMT | 41000
57 | SWR34344 | 18 | Supply and fixing of 15mm dia. SS coated taps including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F-15mm GM/Bronze Ball Valve | As per relevant standard specifiction | 230 | EA | 4140
58 | SWR34345 | 1 | Supply and fixing of 20mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F-20mm GM/Bronze Ball Valve | As per relevant standard specifiction | 331 | EA | 331
59 | SWR34346 | 2 | Supply and fixing of 25mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F-25mm GM/Bronze Ball Valve | As per relevant standard specifiction | 466 | EA | 932
60 | SWR34329 | 3 | Supply and fixing of 12.7mm bib tap Indian make including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Furniture | S&F-15mm Bib Tap 400gm Full turn | As per relevant standard specifiction | 271 | EA | 813
61 | SWR34375 | 500 | Providing and placing on Terrace polyetheylene water storage tank with double layer approved brand and manufacture with cover complete for finished item of work and as directed by the engineer-in-charge. | Furniture | S&F Polyethylene Water Storage Tank | As per relevant standard specifiction | 10 | L | 5000
62 | SWR33746 | 1 | Supply of steel table of size 4'x2.5'x30" with 18 mm plywood fixed with rubber beeding with drawers on right side with automatic locking arrangements etc complete for finished item of work and as directed by the engineer-in-charge. | Furniture | Supply of Table 4'x2' with MS Frame | As per relevant standard specifiction | 4200 | EA | 4200
63 | SWR33857 | 1 | Supply of 'S' type chair with arms teakwood frame with seat back 's' type on G.I pipe including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Fencing | Supply of S-Type Chair | As per relevant standard specifiction | 3850 | EA | 3850
64 | SWR33858 | 2 | Supply of P V C chairs of Neelkamal of approved quality & make including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Fencing | Supply of PVC Chair | As per relevant standard specifiction | 1150 | EA | 2300
65 | SWR33406 | 150 | S&Fixing of R.C.C fencing poles of size 0.115mx0.115mx2.7m including cost & conveyance of all materials,labour chargesv etc complete for finished item of work. | Fencing | S&F RCC Fencing Pole 0.115mx0.115mx2.7m | As per relevant standard specifiction | 1433.9 | EA | 215085
66 | SWR33405 | 76 | Providing and fixing 1.80 metre long RCC fencing posts with 6 mm bar bibs of pole size 0.1x0.1x1.8m in pit size of 0.45x0.45x0.45 and filled with PCC (1:4:8) using 20mm metal including cost & conveyance of all materials, labour charges etc complete for finished item of work. | Name board | S&F RCC Fencing Pole 0.1mx0.1mx1.8m | As per relevant standard specifiction | 1293.04 | EA | 98271.04
67 | SWR33407 | 275 | S&Fixing of barbed wire 8 straight strands and 2 cross strands including cost & conveyance of all materials, labour charges etc complete for finished item of work. | Name board | S&F Barbed Wire 8H & 2Cross | As per relevant standard specifiction | 260.05 | M | 71513.75
68 | SWR33421 | 1.35 | Supply and Fixing of Substation name board of size 5'x3' iron sheet with angle frame and channel supports of size 75x40mm, 8' height including concreting of channel supports and painting with enamel paint complete. | Borewell | S&F MS Board | As per relevant standard specifiction | 4542.3 | Sqm | 6132.105
69 | SWR33423 | 2.21 | S&F Poly Vinyl Acrylic Board including cost and conveyance of all labour and material charges complete. | Borewell | S&F Poly Vinyl Acrylic Board | As per relevant standard specifiction | 1930.48 | Sqm | 4266.3608
70 | SWR33608 | 1 | Geophysical Investgation Charges | Borewell | Geophysical Investgation Charges | As per relevant standard specifiction | 5000 | EA | 5000
71 | SWR33609 | 90 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work. 0 to 90M | Borewell | Drilling-165mm Bore Well 0 to 90M | As per relevant standard specifiction | 336 | M | 30240
72 | SWR34830 | 30 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work. 90m to 120M | Borewell | Drill-165mm Bore Well 90M to 120M | As per relevant standard specifiction | 369 | M | 11070
73 | SWR34831 | 30 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work. 120m to 150M | Borewell | Drill-165mm Bore Well 120M to 150M | As per relevant standard specifiction | 394 | M | 11820
74 | SWR33611 | 30 | Suppy & fixing of 160 mm dia. 6 kg/cm2 PVC casing pipe including cost and conveyance of all materials labour charges etc complete for finished item of work | Borewell | S&F 160mm dia PVC Casing | As per relevant standard specifiction | 844 | M | 25320
75 | SWR33636 | 1 | Supply & fixing of 2HP Multistage submersible motor pumpset of approved make (Texmo or equivalent type) including cost and conveyance of all materials etc complete for finished item of work. | Borewell | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | As per relevant standard specifiction | 34237 | EA | 34237
76 | SWR33641 | 200 | S&R 3C 2.5sqmm Flat Copper Cable including cost of all materials and labour charges for finished item of work. | Borewell | S&R 3C 2.5sqmm Flat Copper Cable | As per relevant standard specifiction | 190 | EA | 38000
77 | SWR33644 | 1 | Supply and fixing of Panel box and starter including cost of all materials and labour charges for finished item of work. | Borewell | S&E D.O.L Starter 250V Single Phase | As per relevant standard specifiction | 1040 | EA | 1040
78 | SWR34203 | 1 | Supply & fixing of Flange Clamps including cost of all materials and labour charges for finished item of work. | Borewell | Supply & ixing of Flange Clamps | As per relevant standard specifiction | 182 | EA | 182
79 | SWR34410 | 145 | Suppy & fixing of HDPE pipe 1.5" dia. including cost & conveyance of all materials labour charges etc complete for finished item of work. | Borewell | S&F-HDPE Pipe 40mm dia 16kg/sqcm-SDR 9 | As per relevant standard specifiction | 160 | Rmt | 23200
80 | SWR34470 | 96.8 | Seigniorage Charges - Sand | Seigniorages | Seigniorage Charges - Sand | As per relevant standard specifiction | 40 | M3 | 3872
81 | SWR34471 | 107.5 | Seigniorage Charges - Metal | Seigniorages | Seigniorage Charges - Metal | As per relevant standard specifiction | 97.5 | M3 | 10481.25
82 | SWR34472 | 858.73 | Seigniorage Charges - Gravel | Seigniorages | Seigniorage Charges - Gravel | As per relevant standard specifiction | 30 | M3 | 25761.9
[7 empty] | Civil Total |  | 3394908.9144
[7 empty] | Electrical & Civil Total |  | 8262927.5242

## 9. Lakdaram SS
Lakdaram Electrical SS Schedules
Name of the work:Revised estimate for erection of new 33/11 KV SS with connected 33 KV and 11 KV lines at Lakdaram (Vg) in Patancheru (M) of Sangareddy Division of Sangareddy Circle .
S.No | SSR Code | Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR10105 | 46 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 27600
2 | SWR10343 | 38 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 91200
3 | SWR10356 | 3.27 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M with CC mix of ratio 1:3:6 Using form boxes (0.087 Cu.Mt)*38 = 3.27 cu mtr with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 21513.33
4 | SWR10356 | 33.44 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt)*38 = cu mtr with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 220001.76
5 | SWR11890 | 1.18 | ERECTION OF S.S. STRUCTURE: Coping of 0.45x0.45x0.45Mt with 1:8 slope Using form boxes (0.031Cumt.) | Civil work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | M3 | 4593.74
6 | SWR11331 | 38 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of poles with two coats of white cement (including cost of paint). | Electrical work | Paint-9.1M PSCC Poles as desc SSR | As per relevent standard specification | 485 | EA | 18430
7 | SWR11889 | 8.5 | Fabrication of 100 X 50mm MS Channel for formation of 11kV and 33kV bays: Fabrication and erection of M.S,Channel 100x50mm for forming of 33KV & 11 KV Bays as per standard specifications to facilitate stringing of bus, erection of LA sets, AB Switches bolts & Nuts etc. including painting with one coats of red oxide and two coats of Aluminium paint. GI bolts&nuts shall be used. | Electrical work | Fabr & Erect-MS Chnl 100x50mm for SS Bay | As per relevent standard specification | 6600 | TO | 56100
8 | SWR10404 | 50 | Erection of 33kV and 11kV Strung Bus with Panther (200Sqmm) ACSR Conductor: Erection of 33kV and 11kV Bus over the Substation structures with 200sqmm Panther ACSR conductor and giving Jumpers to connect the Switch gear by providing the suitable T clamps and round clamps suitable to Post type insulators & Insulators. | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 16384
9 | SWR10884 | 90 | Connectionof equipment to bus and or another equipmentwithsingle zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Electrical work | Conn. of equip/bus single zebra/panther | As per relevent standard specification | 224 | EA | 20160
10 | SWR10392 | 7 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 31500
11 | SWR10393 | 14 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 44800
12 | SWR21240 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 33kv | As per relevent standard specification | 781 | EA | 1562
13 | SWR21241 | 4 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 11kv | As per relevent standard specification | 507 | EA | 2028
14 | SWR10881 | 20 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 2840
15 | SWR23224 | 41.14 | Excavation of pit in all types of soils of size 2.2x2.2x0.85Mts.for Construction of Plinths for VCB (33KV & 11 KV ) | Earth work | Excavate-Pit for 33KV VCB | As per relevent standard specification | 331 | M3 | 13617.34
16 | SWR20685 | 55.66 | Providing of Base concreting (2.2x2.2x0.15 Mts*10=7.26 Cu Mtr) with 1:3:6 Concrete mix. Using form boxes, Providing of Concreting (2.2x2.2x1.0mts*10=48.4 Cu Mtr) with 1:3:6 Cocrete mix. Plastering of the plinth for smooth finishing with 12mm thick 1:3 cement motor and providing two coats white washing for part of the plinth above groung level. | Civil work | Cement concrete with 40MM metal VCB plin | As per relevent standard specification | 6579 | M3 | 366187.14
17 | SWR10460 | 3 | Erection of Switchgear complete for 33 kV VCB includes Assembling the VCB Structures and mounting the VCBs over the already erected foudation including wiring of Breaker Control Panel/CTs, erection of CTs and control pannel providing Jumpers. | Electrical work | Erection of 33kv VCB | As per relevent standard specification | 12500 | EA | 37500
18 | SWR10461 | 7 | Erection of Switchgear complete for 11 kV VCB includes Assembling the VCB Structures and mounting the VCBs over the already erected foudation including wiring of Breaker Control Panel/CTs, erection of CTs and control pannel providing Jumpers. | Electrical work | Erection of 11kv VCB | As per relevent standard specification | 12000 | EA | 84000
19 | SWR10396 | 2 | Erection of 33KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 1760
20 | SWR10397 | 1 | Erection of 11 KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 11kv LA stn type incl earthing | As per relevent standard specification | 559 | SET | 559
21 | SWR10398 | 5 | Erection of 11 KV Lightening Arrestors line type complete including jumpering. | Electrical work | Erect of 11kvLA line type incl earthing | As per relevent standard specification | 505 | SET | 2525
22 | SMR11482 | 32 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 111552
23 | SWR10357 | 32 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 39494.4
24 | SWR10920 | 620 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification.75x8 mm MS flat for Earth mat and connecting to electrodes | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 40300
25 | SWR10919 | 1240 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification. 50x6 mm MS flat for raisers, double flat shall be run for structure poles raisers & equipment earthing. | Electrical work | Earthing for raisers of SS Flat 50x6 mm. | As per relevent standard specification | 41 | RMT | 50840
26 | SMR40033 | 4 | Providing of double earthing for neutral with flexible copper jumpers of adequate size including arrangement by fixing M.S.Channel 100x50mm. | Electrical work | SupCU Flexi jumper for Power T/F Neutral | As per relevent standard specification | 4725 | EA | 18900
27 | SWR11771 | 10 | Erection of 24 Volts Battery along with Charger on the VCB plinth and giving DC supply to VCB's. | Electrical work | Erect-24V Batery with Chrgr incl grot-SS | As per relevent standard specification | 1050 | EA | 10500
28 | SWR11879 | 1.46 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable includes excavation of earth and back filling with sand and earth in alternate layers . The cable termination shall be made by providing proper size lugs and shall be identified with colours. | Electrical work | Laying-4 core cable | As per relevent standard specification | 27 | RMT | 39.42
29 | SWR10463 | 1 | Erection of 25 kVA Three phase Station Transformer on the Substation Structures and giving jumpers/connections on HT side to the 11kV bus. Belting angle shall be provided both sides of DTR for securing DTR firmly in position. | Electrical work | Erection of Three Phase DTRs | As per relevent standard specification | 1139.95 | EA | 1139.95
30 | SMR40045 | 1 | Supply of AC Panel Board includes: Fixing of 1 No.100A, MCCB, 10kA capacity of any standard make including material cost. Fixing of suitable panel box 3x3x1 with M.S.Sheet of 16 SWG with front door compartments inclusive of material cost & powder coating (with C Channel ). Fabrication of panel Fixing of 96x96mm analog voltmeter with VSS switch Fixing of 20A HRC fuse Fixing of 3 phase supply indicator kwith HRC fuses Supply and fixing of 6 Sqmm copper flexible wire (PVC) Fixing of Stud type TBs for outgoing feeder Fixing of Epoxy bus supports | Electrical work | Supply of AC Supply panel complete | As per relevent standard specification | 42000 | EA | 42000
31 | SMR40044 | 1 | Supply of DC Panel Board Fixing of suitable panel box of size 6'x6'x1' with M S sheet of 16 SWG with back doors (4'x6') and on front side with provision to fix up bakelite hylam sheet size of 4'x6' including cost of the panel with powder coating. Fixing of best quality of angles for panel. Fixing of C Channelfor panel. Fabrication of control panel including making suitable holes and board Fixing of Stud type TBs for outgoing feeder Fixing of 24V DC pilot lamps of standard make Fixing of healthy trip push buttons with LED lamp Fixing of plain switches for alarm acceptance and for PTR signal Fixing of ON/OFF push buttons Fixing of digital volt meter for 11kV Fixing of VSS of standard make, Fixing of Engraved AL plates for Alarm panel of various VCB Laying of 2.5Sqmm copper flexible wire for internal wiring . Fixing of digital frequency meter Fixing of Copper lugs and ferrules for internal wiring. Fixing of 4" Gang bells 24V DC Fixing of flow diagram with rading strip Fixing of HRC fuse units | Electrical work | Supply of DC Anunc.relay panel 8 feeders | As per relevent standard specification | 42500 | EA | 42500
32 | SWR20025 | 1 | fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supplied by tenderer. | Electrical work | 33/11kv S.S Erection of AC&DC Panel | As per relevent standard specification | 7871.85 | SET | 7871.85
33 | SWR10342 | 8 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 12000
34 | SWR10956 | 8 | Fixing of Metal halide/LED lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5M GI pipe complete. | Electrical work | Fixing of LED/Metal halide complete. | As per relevent standard specification | 1268 | EA | 10144
35 | SWR20028 | 8 | Supply and Fixing of junction box and Providing with proper Fuse protection and required glauds suitable for Cable Terminations. The box shall be fixed on the pole. | Electrical work | 33/11kv S.S Yard lighting junction box | As per relevent standard specification | 351.9 | EA | 2815.2
36 | SWR20526 | 4 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply & fixing of marshall box | As per relevent standard specification | 1139.85 | EA | 4559.4
37 | SMR40088 | 1 | Supply and fixing of filled sand bucket set complete (4 Nos. Buckets) with stand to mount fire buckets. | Electrical work | Sup Fire Buckets Stand with Buckets | As per relevent standard specification | 1386 | SET | 1386
38 | SMR40087 | 2 | Supply and fixing of CO2 Cylinder set as per IS2878 Specifications. | Electrical work | Sup TrollyMounted Co2 Cylinders(IS-2878) | As per relevent standard specification | 9240 | EA | 18480
39 | SWR11895 | 1 | Supplying and fixing of feeder indicator board to each of the 3Nos feeder breakers and LV breaker, danger boards made of 1'x1' and properly mounted on the structures. The letters written on the borad shall be 1.5"size with blue colour and background shall be of white colour | Electrical work | S&F-33/11KV SS Feeder Indicator Board | As per relevent standard specification | 551 | SET | 551
40 | SWR20032 | 1 | Supply and fixing of wooden board of size 3'x2'.5'indicating the layout of the Switch yard. | Electrical work | Sup &fix of board ind Switchyard layout | As per relevent standard specification | 1654 | EA | 1654
41 | SMR40086 | 1 | Supply and Erection of Permanent Name Board of on 3'x4' steel sheetmounted on steel frame as described in Specification. | Electrical work | Sup 33/11kv S.S Permanent name board | As per relevent standard specification | 10238 | EA | 10238
42 | SMR40076 | 1 | Supply of Digital clamp meter. | Electrical work | Supply of Digital clamp meter. | As per relevent standard specification | 2888 | EA | 2888
43 | SMR40064 | 1 | Supply of Rechargeable LED torch light of Standard make | Electrical work | Sup Rechargeable LED torch light. | As per relevent standard specification | 1733 | EA | 1733
44 | SMR40063 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box containing ‘D’Spanners from size 6 to 54, Hammer small and big size, Ring spanners from 6 to 28, Adjustable spanner, Pipe wrench, Cutting Plier, Nose plier, Tester, insulated Screw drive. | Electrical work | SupTaparia Tool kit complete as per Spec | As per relevent standard specification | 4925 | SET | 4925
45 | SWR22090 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Electrical work | Sup& fix safety inst/SS Op. inst board | As per relevent standard specification | 2205 | EA | 2205
46 | SMR11598 | 8 | Supply of 25 W LED lamp with fitting of philips make | Electrical work | S-25W LED fixture set | As per relevent standard specification | 3200 | EA | 25600
47 | SMR12378 | 1 | Supply of Alluminum Ladder(20 feet) | Electrical work | S-10ft Aluminium Ladder | As per relevent standard specification | 1654 | EA | 1654
48 | SMR40075 | 1 | Supply of Megger (2000 ohms, 0-2.5kv) | Electrical work | Supply of Earth megger (1000v) | As per relevent standard specification | 8085 | EA | 8085
49 | SMR11599 | 4 | Supply of Earth Discharging Rod 10' length. | Electrical work | S-Earth Rod 8ft Long 3mm Thick | As per relevent standard specification | 1000 | EA | 4000
50 | SMR11488 | 230 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 27025
51 | SMR11591 | 72 | Supply of PG clamps for panther 2 bolted 800 A | Electrical work | S-Al. alloy three bolted PG clamps 800A | As per relevent standard specification | 130 | EA | 9360
52 | SWR20029 | 350 | Supply and Laying of 2 core/4 core cable includes excavation earth and back filling with sand and earth in alternate layers as shown in the sketch. The cable termination shall be made by providing proper size of lugs at both ends of the cable termination. | Electrical work | 33/11kv S.S laying of 2/4core for light | As per relevent standard specification | 50 | M | 17500
53 | SWR20308 | 38 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 15477.02
54 | SWR20307 | 8 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 2172.16
55 | SWR11860 | 10 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 27203.4
56 | SWR10150 | 14.7 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 9071.37
57 | SWR10206 | 14.7 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 3248.7
58 | SWR10524 | 14.7 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 2719.5
59 | SWR11220 | 580 | Loading and unwinding of Panther conductor | Electrical work | Load-Unwinding Panther conductor | As per relevent standard specification | 3 | M | 1740
60 | SWR11221 | 580 | Unloading of Panther conductor | Electrical work | Unload-Unwinding Panther conductor | As per relevent standard specification | 2 | M | 1160
61 | SWR12416 | 3 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 6
62 | SWR10631 | 3 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 6
63 | SWR10618 | 3 | Loading of 33KV Metal parts bag of 25 nos | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 195
64 | SWR10632 | 3 | Unloading of 33 KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 195
65 | SWR10212 | 3 | Loading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators | Electrical work | LOADING of 11kv Pin/Post/Solid Core Insu | As per relevent standard specification | 1 | CRT | 3
66 | SWR10530 | 3 | Unloading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators | Electrical work | UNLOADING of 11kv Pin/Post/Solid Core In | As per relevent standard specification | 1 | CRT | 3
67 | SWR11701 | 1460 | Loading of PVC Copper Control Cable 4 core and 10 core | Electrical work | Load-PVC Control Cable 10C | As per relevent standard specification | 1 | M | 1460
68 | SWR11712 | 1460 | Unloading of PVC Copper Control Cable 4 core and 10 core | Electrical work | UnLoad-PVC Control Cable 10C | As per relevent standard specification | 1.02 | M | 1489.2
69 | SWR11691 | 1 | Loading of 3Ph 25KVA Distribution Transformer | Electrical work | Load-3Ph 25KVA DTR | As per relevent standard specification | 252 | EA | 252
70 | SWR11692 | 1 | UnLoading of 3Ph 25KVA Distribution Transformer | Electrical work | UnLoad-3Ph 25KVA DTR | As per relevent standard specification | 202 | EA | 202
71 | SWR10200 | 2 | Loading of 33/11 KV Current Transformers/ Potential Transformers | Electrical work | LOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 165 | EA | 330
72 | SWR10266 | 6 | Loading of 33 KV10 KA LAs Station type | Electrical work | LOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 41 | EA | 246
73 | SWR10584 | 6 | Unloading of 33 KV10 KA LAs Station type | Electrical work | UNLOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 35 | EA | 210
74 | SWR10265 | 15 | Loading of 11 KV10 KA LAs Line type | Electrical work | LOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 480
75 | SWR10583 | 15 | Unloading of 11 KV10 KA LAs Line type | Electrical work | UNLOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 480
76 | SWR10264 | 3 | Loading of 11 KV10 KA LAs Station type | Electrical work | LOADING of 11 KV,10 KA LAs Station type | As per relevent standard specification | 32 | EA | 96
77 | SWR10582 | 3 | Unloading of 11 KV10 KA LAs Station type | Electrical work | UNLOADING of 11 KV,10 KA LAs Station typ | As per relevent standard specification | 32 | EA | 96
78 | SWR10239 | 7 | Loading of 33 KV AB Switch Conventional 400/800 Amp | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 882
79 | SWR10557 | 7 | Unloading of 33 KV AB Switch Conventional 400/800 Amp | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 553
80 | SWR10238 | 10 | loading of 11 KV AB Switch Conventional 200/400 Amp | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 800
81 | SWR10556 | 10 | Unloading of 11 KV AB Switch Conventional 200/400 Amp | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 800
82 | SWR11224 | 10 | Loading and Unloading of 12V/24V Battery Set | Electrical work | Load/Unload-12V/24V Battery Set | As per relevent standard specification | 23 | EA | 230
83 | SWR10402 | 1 | Erection of 11kv Potential Transformer sets complete including jumpering. The LV side of the PT shall be provided with proper fuse protection mounted in separate marshalling boxwith proper size cable glands etc. The box shall be mounted on the Substation structure. | Electrical work | Erection of 11kv three phase PT s | As per relevent standard specification | 800 | SET | 800
84 | SWR10518 | 2 | Unloading of 33/11 KV Current Transformers/ Potential Transformers | Electrical work | UNLOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 128 | EA | 256
85 | SWR10674 | 1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
86 | SMR11608 | 1 | Supply of 11kv HG fuse set including providing of jumpers | Electrical work | S-11KV HG Fuse Set | As per relevent standard specification | 1733.75 | SET | 1733.75
87 | SWR10395 | 1 | Erection of 11kv HG fuse set including providing of jumpers | Electrical work | Erect. of 11kv HG Fuseset incl earthing | As per relevent standard specification | 740.52 | SET | 740.52
88 | SMR40067 | 2 | Supply of Hand Gloves | Electrical work | Supply of Hand Gloves | As per relevent standard specification | 289 | SET | 578
89 | SMR40071 | 2 | Supply of Safety Helmet of standard make | Electrical work | Supply of Safety Helmet of standard make | As per relevent standard specification | 231 | EA | 462
90 | SWR10401 | 1 | Erection of 33kv Potential Transformer sets complete including jumpering. The LV side of the PT shall be provided with proper fuse protection mounted in separate marshalling boxwith proper size cable glands etc. The box shall be mounted on the Substation structure. | Electrical work | Erection of 33kv single phase PT s | As per relevent standard specification | 1079 | SET | 1079
91 | SMR25233 | 38 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 118157.58
92 | SMR22745 | 8500 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 488325
93 | SMR12321 | 3100 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 174902
94 | SMR12322 | 3100 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 175150
95 | SMR25232 | 8 | Supply of 8.0Mtr PSCC 140 Kg Pole | Electrical work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 12640
96 | SMR12315 | 7 | Supply of 33KV 800A DB Break AB Switch | Electrical work | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 284611.46
97 | SMR12316 | 3 | Supply of 11KV 800A DB Break AB Switch | Electrical work | S-11KV 800A DB Break AB Switch | As per relevent standard specification | 30847.46 | EA | 92542.38
98 | SMR12317 | 11 | Supply of 11KV 400A DB Break AB Switch | Electrical work | S-11KV 400A DB Break AB Switch | As per relevent standard specification | 18150 | EA | 199650
99 | SMR25200 | 1 | Supply of LT Distribution Box (SMC) | Electrical work | S-LT Distribution Box (SMC) | As per relevent standard specification | 7797 | EA | 7797
100 | SWR10674 | 1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
101 | SMR40009 | 8.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for First coat of 1st GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 18538.5
102 | SWR10877 | 8.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 1st coat of Aluminium | Electrical work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 7233.5
103 | SMR40010 | 8.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for second coat of 2nd GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 10990.5
104 | SWR10879 | 8.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 2nd coat of Aluminium | Electrical work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 4097
105 | SWR22092 | 2.99 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 2287.35
106 | swr12087 | 8 | Excavation of Pole pits of size 0.76x0.76x2.5 Mts' for 15 mts/12.5mtr spun Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT exc of hard blast 0.75mx 0.75mx2.5m | As per relevent standard specification | 990 | EA | 7920
107 | SWR10107 | 40 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11.0 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 28000
108 | SWR10112 | 11 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | As per relevent standard specification | 1680 | EA | 18480
109 | SWR10105 | 22 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 13200
110 | SWR25138 | 6 | Erection of spun pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Spun poles 15 Mtrs | Electrical work | Erection of Spun pole 15Mt | As per relevent standard specification | 5600 | EA | 33600
111 | SWR10350 | 2 | Erection of spun pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Spun poles 12.5 Mtrs / 12.9Mtrs PSCC | Electrical work | Erection of Spun pole 12.5Mt | As per relevent standard specification | 4115.7 | EA | 8231.4
112 | SWR10978 | 51 | Erection of 11 M long PSCC pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 212429.28
113 | SWR10343 | 22 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 52800
114 | SWR10981 | 12 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Horizontal Cut point for 33 KV line | As per relevent standard specification | 1759.5 | EA | 21114
115 | SWR10356 | 42.689 | Concreting the location after erection of 15mtr/ 12.5mtr mt spun pole and 11.0 mt /9.1mtr PSCC pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.75X0.9X1.9 Mts)* 8 = 11.552 Cu.Mt for spun pole, (0.75X0.75X2 Mts)*23 = 25.875 Cu.Mt for 11.0mtr PSCC pole and (0.76X0.76X1.52 Mts)* 6 = 5.262 Cu.Mt for 9.1mtr PSCC pole, | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 280850.931
116 | SWR10366 | 2.99 | Paving of the 100 sqmm AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 12600.06 | KM | 37674.1794
117 | swr11310 | 0.3 | Paving of the 100 sqmm AAA conductor and Re stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Re Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 9600 | KM | 2880
118 | swr11309 | 0.3 | Paving of the 55sqmm AAA conductor and Restringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Re Stringing 55sqmm 33/11kv Line 6 Cond SC | As per relevent standard specification | 6501.23 | KM | 1950.369
119 | SMR11488 | 162 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 19035
120 | SWR11185 | 8 | Sub Transportation of Spun Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt any Spun Pole incl. L&UL<10KM | As per relevent standard specification | 771.38 | EA | 6171.04
121 | SWR11180 | 55 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 23758.35
122 | SWR20308 | 18 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 7331.22
123 | SWR10191 | 2 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 404
124 | SWR10509 | 2 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 200
125 | SWR11860 | 2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 5440.68
126 | SWR10150 | 2.25 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 1388.475
127 | SWR10206 | 2.25 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 497.25
128 | SWR10524 | 2.25 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 416.25
129 | SWR10211 | 20 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 60
130 | SWR10529 | 20 | Unloading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 60
131 | SWR11248 | 36 | Loading 11KV Polymer Pin Insulator- with GI pins | Electrical work | Load-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 36
132 | SWR11249 | 36 | Unloading 11KV Polymer Pin Insulator with GI pins | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 36
133 | SWR12416 | 8 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 16
134 | SWR10631 | 8 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 16
135 | SWR10618 | 3 | Loading of 33KV Metal parts bag of 25 nos | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 195
136 | SWR10632 | 3 | Unloading of 33 KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 195
137 | SWR10227 | 42 | Loading of 33 KV V - Cross arms | Electrical work | LOADING of 33 KV V - Cross arms | As per relevent standard specification | 6 | EA | 252
138 | SWR10545 | 42 | Unloading of 33 KV V - Cross arms | Electrical work | UNLOADING of 33 KV V - Cross arms | As per relevent standard specification | 6 | EA | 252
139 | SWR10252 | 42 | Loading of 33 KV Top fittings | Electrical work | LOADING of 33 KV Top fittings | As per relevent standard specification | 1 | EA | 42
140 | SWR10570 | 42 | Unloading of 33 KV Top fittings | Electrical work | UNLOADING of 33 KV Top fittings | As per relevent standard specification | 1 | EA | 42
141 | SWR10319 | 152 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 75 x 8 mm MS Flat | Electrical work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31 | EA | 4712
142 | SWR10322 | 88 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 75 x 8 mm MS Flat | Electrical work | Fab Stay clamps with 75x8 mm MM Flat | As per relevent standard specification | 42 | EA | 3696
143 | SWR10378 | 56 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevent standard specification | 32 | EA | 1792
144 | SWR10354 | 11 | Erection of 33 kv Stay set complete including fixing of bow ,fixing and binding of Eye bolt, Anchor rod, guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. | Electrical work | Assembly and erection of Stay set 33kv | As per relevent standard specification | 684.53 | SET | 7529.83
145 | SWR21190 | 11 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In Hard Gravel and Hard murram not requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 5720
146 | SWR10356 | 2.981 | Concreting the stay location with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.45X0.45X1.34 Mts)*11 = 2.981 Cu.Mt | Electrical work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 19611.999
147 | SMR25239 | 6 | Supply of 15Mtr spun Pole | Electrical work | S-PSCC Spun Pole 15Mtr | As per relevent standard specification | 42372.88 | EA | 254237.28
148 | SMR25238 | 2 | Supply of 12.5Mtr spun Pole | Electrical work | S-PSCC Spun Pole 12.5Mtr | As per relevent standard specification | 15635.59 | EA | 31271.18
149 | SMR25236 | 55 | Supply of 11Mtr PSCC 365 Kg Pole | Electrical work | S-PSCC Pole 11Mtr 365 Kg | As per relevent standard specification | 5399 | EA | 296945
150 | SMR25233 | 18 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 55969.38
151 | SMR25229 | 42 | Supply of 33KV V-Cross Arm without Clamps | Electrical work | S-33KV V-Cross Arm without Clamps | As per relevent standard specification | 1678 | EA | 70476
152 | SMR25207 | 580 | Supply of MS Angle 65X65X6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 33205
153 | SMR22745 | 920 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 52854
154 | SMR12321 | 750 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 42315
155 | SMR25231 | 11 | Supply of 33KV MS Stay Set with BasePlate | Electrical work | S-33KV MS Stay Set with BasePlate | As per relevent standard specification | 1035 | SET | 11385
156 | SWR22092 | 8.22 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 11 kv line. | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 6288.3
157 | SWR10107 | 60 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11.0 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 42000
158 | SWR10112 | 15 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | As per relevent standard specification | 1680 | EA | 25200
159 | SWR10105 | 84 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 50400
160 | SWR10978 | 75 | Erection of 11 M long PSCC pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 312396
161 | SWR10343 | 41 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 98400
162 | SWR11083 | 21 | Erection of 9.1Mtr stud pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M studPole | As per relevent standard specification | 2400 | EA | 50400
163 | SWR10342 | 22 | Erection of 8.0 Mts PSCC Poles including fixing of 11 KV X arm and top cleats and fixing of Pin insulators complete with necessary hard ware for tangential locations excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 33000
164 | SWR10653 | 31 | Formation of 11 kv cut points (Vertical/Horizantal) including fixing of 11 KV Cross arms,clamps, strain insulators sets complete with hardware and stays (Bows and Eye-bolts), Excluding the cost of pit Excavation and pole erection. The contractor has to supply GI Bolts and Nuts. | Electrical work | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1350 | EA | 41850
165 | SWR10356 | 55.524 | Concreting the location after erection of 9.1mtr / 11.0 mt PSCC pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes(0.76X0.76X1.52Mts)*12 = 10.524 Cu.Mt and (0.75X0.75X2Mts)*40 = 45 | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 365292.396
166 | SWR10365 | 5.82 | Paving of the conductor 55 Sqmm AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 3 Cond | As per relevent standard specification | 8500 | KM | 49470
167 | SWR10703 | 2.4 | Paving of the conductor 55 Sqmm AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 6 Cond | As per relevent standard specification | 16000 | KM | 38400
168 | SMR11488 | 240 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 28200
169 | SWR10206 | 2.32 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 512.72
170 | SWR10524 | 2.32 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 429.2
171 | SWR11248 | 501 | Loading 11KV Polymer Pin Insulator- with GI pins | Electrical work | Load-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 501
172 | SWR11249 | 501 | Unloading 11KV Polymer Pin Insulator with GI pins | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 501
173 | SWR10134 | 2.32 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 1363.0464
174 | SWR11862 | 4 | Transport of VCB , Control pannels, current transformater, bosster etc, above 20 KM and upto 30 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 14765.52
175 | SWR10191 | 4 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 808
176 | SWR10509 | 4 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 400
177 | SWR11180 | 75 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 32397.75
178 | SWR20307 | 22 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 5973.44
179 | SWR20308 | 62 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 25251.98
180 | SWR10228 | 182 | Loading of 11 KV V - Cross arms | Electrical work | LOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 728
181 | SWR10546 | 182 | Unloading of 11 KV V - Cross arms | Electrical work | UNLOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 728
182 | SWR12402 | 8 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 384
183 | SWR12421 | 8 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 384
184 | SWR10251 | 53 | Loading of 11 KV Top fittings | Electrical work | LOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 53
185 | SWR10569 | 53 | Unloading of 11 KV Top fittings | Electrical work | UNLOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 53
186 | SWR12416 | 10 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 20
187 | SWR10631 | 10 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 20
188 | SWR10353 | 21 | Erection of 11 kv Stay set complete including fixing of bow, fixing and binding of Eye bolt,Anchor rod,guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Assembly and erection of Stay set11kv&LT | As per relevent standard specification | 606.85 | SET | 12743.85
189 | SWR21190 | 21 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In Hard Gravel and Hard murram not requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 10920
190 | SWR10356 | 5.691 | Concreting the stay location with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.45X0.45X1.265 Mts)* 21 = 5.691Cu.Mt | Electrical work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 37441.089
191 | SWR10319 | 195 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 75 x 8 mm MS Flat | Electrical work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31 | EA | 6045
192 | SWR10322 | 86 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 75 x 8 mm MS Flat | Electrical work | Fab Stay clamps with 75x8 mm MM Flat | As per relevent standard specification | 42 | EA | 3612
193 | SWR10320 | 59 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 50 x 6 mm MS Flat | Electrical work | Fab Back clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 15 | EA | 885
194 | SWR10323 | 80 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 50 x 6 mm MS Flat | Electrical work | Fab Stay clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 25 | EA | 2000
195 | SWR10378 | 116 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevent standard specification | 32 | EA | 3712
196 | SMR25236 | 75 | Supply of 11Mtr PSCC 365 Kg Pole | Electrical work | S-PSCC Pole 11Mtr 365 Kg | As per relevent standard specification | 5399 | EA | 404925
197 | SMR25233 | 62 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 192783.42
198 | SMR25232 | 62 | Supply of 8.0Mtr PSCC 140 Kg Pole | Electrical work | S-PSCC Pole 8.0Mtr 280kg | As per relevent standard specification | 1580 | EA | 97960
199 | SMR25218 | 182 | Supply of 11KV V X-Arms with MS Angle 65x65x6 | Electrical work | S-11KV V X-Arms with MS Angle 65x65x6 | As per relevent standard specification | 743 | EA | 135226
200 | SMR22745 | 420 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 24129
201 | SMR25205 | 450 | Supply of MS Channel 75x40 mm | Electrical work | S-MS Channel 75x40 mm | As per relevent standard specification | 58.45 | KG | 26302.5
202 | SMR25207 | 260 | Supply of MS Angle 65X65X6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 14885
203 | SMR25206 | 350 | Supply of MS Angle 50x50x6 | Electrical work | S-MS Angle 50x50x6 | As per relevent standard specification | 58.15 | KG | 20352.5
204 | SMR12321 | 760 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 42879.2
205 | SMR12322 | 250 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 14125
206 | SMR25214 | 21 | Supply of LT/11KV MS Stay Sets with Base Plate | Electrical work | S-LT/11KV MS Stay Sets with Base Plate | As per relevent standard specification | 1168 | SET | 24528
207 | SWR10392 | 1 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 4500
208 | SWR10105 | 2 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 1200
209 | SWR10343 | 2 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 4800
210 | SWR10356 | 1.08 | Concreting the location after erection of 9.1mtr PSCC pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.76X0.76X1.52 Mts)* 2 = 1.08 Cu.Mt for 9.1mtr PSCC pole, | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 7105.32
211 | SMR11488 | 20 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 2350
212 | SWR10206 | 0.56 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 123.76
213 | SWR10524 | 0.56 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 103.6
214 | SWR10134 | 0.56 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 329.0112
215 | SWR20308 | 2 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 814.58
216 | SWR12416 | 6 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 12
217 | SWR10631 | 6 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 12
218 | SMR11482 | 1 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 3486
219 | SWR10357 | 1 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 1234.2
220 | SWR10239 | 1 | Loading of 33 KV AB Switch Conventional 400/800 Amp | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 126
221 | SWR10557 | 1 | Unloading of 33 KV AB Switch Conventional 400/800 Amp | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 79
222 | SWR10404 | 5 | Erection of 33kV and 11kV Strung Bus with Panther (200Sqmm) ACSR Conductor: Erection of 33kV and 11kV Bus over the Substation structures with 200sqmm Panther ACSR conductor and giving Jumpers to connect the Switch gear by providing the suitable T clamps and round clamps suitable to Post type insulators & Insulators. | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 1638.4
223 | SWR10884 | 6 | Connectionof equipment to bus and or another equipmentwithsingle zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Electrical work | Conn. of equip/bus single zebra/panther | As per relevent standard specification | 224 | EA | 1344
224 | SWR10421 | 9 | Supply of T-Clamps | Electrical work | Fixing of T- clamp | As per relevent standard specification | 116 | EA | 1044
225 | swr10424 | 6 | Supply of pad clamps for AB switch | Electrical work | Fixing of pad clamps for AB switch | As per relevent standard specification | 116 | EA | 696
226 | SWR10881 | 1 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 142
227 | SWR20976 | 1 | Erection of 33KV Lightening Arrestors line type complete including jumpering. | Electrical work | Erect of 33kvLA line type incl earthing | As per relevent standard specification | 880 | SET | 880
228 | SWR10920 | 30 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification.75x8 mm MS flat for Earth mat and connecting to electrodes. | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 1950
229 | SWR10919 | 12 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification. 50x6 mm MS flat for raisers, double flat shall be run for structure poles raisers & equipment earthing. | Electrical work | Earthing for raisers of SS Flat 50x6 mm. | As per relevent standard specification | 41 | RMT | 492
230 | SMR12315 | 1 | Supply of 33KV 800A DB Break AB Switch | Electrical work | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 40658.78
231 | SMR25233 | 2 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 6218.82
232 | SMR25207 | 20 | Supply of MS Angle 65X65X6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 1145
233 | SMR22745 | 360 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 20682
234 | SMR12321 | 150 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 8463
235 | SMR12322 | 50 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 2825
[6 empty] | Total |  |  | 7367542.236
1 | SWR34179 | 5 | Levelling the site with the help of JCB including cost, conveyance of all materials,hire charges etc complete for finished item of work. | Site Levelling | Hire-JCB to Level & Clear the Site | As per relevant standard specifiction | 2164.1 | H | 10820.5
2 | SWR33015 | 102.59 | Earth Work Mass Excavation (Ordinary rock not requiring blasting) to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions, labour and material charges etc., complete as directed by the engineer-incharge. | Earth work | Earth Work Mass Excavation | As per relevant standard specifiction | 347 | M3 | 35598.73
3 | SWR33028 | 25.75 | PCC (1:4:8) for levelling course using 40mm size hard broken Granite stone including cost and conveyance of all materials, HBG metal for foundations and leveling course and as directed by the Engineer- in - charge etc complete for finished item of work. | Cement Concrete | PCC (1:4:8) for levelling course using 40mm metal | As per relevant standard specifiction | 4064 | M3 | 104648
4 | SWR33041 | 128.72 | CRS masonry in CM (1:6) using Hard Granite Stones including cost and conveyance of all materials, seignorage charges, labour charge for construction and for dressing stones to required size and shape, dewatering, scaffolding, cutting for all leads and lifts, all incidental charges etc .complete for finished item of work as directed by the Engineer - in - charge. | CRS Masonry | CRS masonry in CM (1:6) using Hard Granite Stones | As per relevant standard specifiction | 4437 | M3 | 571130.64
5 | SWR33068 | 20.3 | Construction of brick masonary in CM(1:6) including cost and conveyance of all materials, labour charges etc. complete for finished item of work | Brick Masonry | Construction of brick masonary in CM(1:6) | As per relevant standard specifiction | 7624 | M3 | 154767.2
6 | SWR33052 | 760.2 | Supplying and filling with borrowed gravel, watering, ramming, consolidating thoroughly complying with the standard specification including cost and conveyance of all materials, labour charges,hire charges of machnery,with all leads and incidental charges etc complete for finished item work | Earth work | Supplying and filling with borrowed gravel, | As per relevant standard specifiction | 435 | M3 | 330687
7 | SWR33098 | 6.53 | RCC M20 GRADE Nominal Mix (a) Footings | RCC | RCC M20 GRADE Nominal Mix (a) Footings | As per relevant standard specifiction | 8227 | M3 | 53722.31
8 | SWR33100 | 4.77 | RCC M20 GRADE Nominal Mix (b) Columns | RCC | RCC M20 GRADE Nominal Mix (b) Columns | As per relevant standard specifiction | 10922 | M3 | 52097.94
9 | SWR33099 | 1.6 | RCC M20 GRADE Nominal Mix (c) Plinth Beams | RCC | RCC M20 GRADE Nominal Mix (c) Plinth Beams | As per relevant standard specifiction | 10647 | M3 | 17035.2
10 | SWR33107 | 0.67 | RCC M20 GRADE Nominal Mix (d) Lintels | RCC | RCC M20 GRADE Nominal Mix (d) Lintels | As per relevant standard specifiction | 11082 | M3 | 7424.94
11 | SWR33114 | 5.63 | RCC M20 GRADE Nominal Mix (e) Sunshade | RCC | RCC M20 GRADE Nominal Mix (e) Sunshade | As per relevant standard specifiction | 1162 | M2 | 6542.06
12 | SWR33121 | 2.35 | RCC M20 GRADE Nominal Mix (f) Roof Beams | RCC | RCC M20 GRADE Nominal Mix (f) Roof Beams | As per relevant standard specifiction | 10657 | M3 | 25043.95
13 | SWR33128 | 6.95 | RCC M20 GRADE Nominal Mix (g) Slab of 130 mm thick | RCC | RCC M20 GRADE Nominal Mix (g) Slab of 130 mm thick | As per relevant standard specifiction | 10208 | M3 | 70945.6
14 | SWR33144 | 2.2 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) / Mild steel (MS) steel bars (Fe 415/ Fe 500 grade as per IS 1786-1979) of different diameters for RCC works complete for finished item of work in all floors.( APSS No.126) | Steel | Reinforcement Steel bars FE415/500 gr. | As per relevant standard specifiction | 75077 | TO | 165169.4
15 | SWR33163 | 314.34 | Providing plastering of 20mm thick to all uneven faces of walls and ceiling of superstructure in two coats with base coat in CM 1:6 of 16mm thick and top coat in Cm 1:4 4mm thick with dubara sponge finish | Plastering | Providing plastering of 20mm thick in 2coats | As per relevant standard specifiction | 410 | M2 | 128879.4
16 | SWR33184 | 136.5 | Raised pointing in CM(1:3) including curing, cost and conveyance of all materials and labour charges for complete item of work. | Plastering | Raised pointing in CM(1:3) including curing | As per relevant standard specifiction | 94 | M2 | 12831
17 | SWR33156 | 54.87 | Providing impervious coat over RCC roof slab surfaces to requried slopes with 20mm thick in CM 1:3 pro mixed with approvaled brand of water proffing compound as the rate of 1 kg per bag of cement inclding cost and conveyance of all materials | Plastering | Providing impervious coat over RCC roof slab | As per relevant standard specifiction | 440 | M2 | 24142.8
18 | SWR33264 | 5.7 | Supply and fixing of Flush type Doors with 35mm Thick Flush Shutters with Bondwood solied Block Board Type Faced on Both the sides with Commercial Type Plywood for finished item work as directed by the Engineer - in- charge. | Doors | Supply and fixing of Flush type Doors | As per relevant standard specifiction | 6799.02 | M2 | 38754.414
19 | SWR33278 | 5.76 | Supply and Fixing of powder coated Aluminium sliding windows with fixed glass panels using aluminium sections 62x32x1.2mm providing 5mm plain glass fixed to frame with beading gasket and glazing clips with all accessories,locking arrangements including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Windows | S&F of powder coated Aluminium sliding windows | As per relevant standard specifiction | 3535.64 | M2 | 20365.2864
20 | SWR33310 | 6.25 | Supplying and fixing of MS safety grill with peripheral frame of ISA 25x25x4mm and horizontal & vertical 8mm square rods and including cost and coveyance of all mateirals with all leads and lifts, labour charges, painting charges complete for finished item of work | Grills | Supplying and fixing of MS safety grill | As per relevant standard specifiction | 2539 | M2 | 15868.75
21 | SWR33219 | 26.5 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and approved size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and pointing with cement, labour etc, complete for finished item of work. | Flooring | Flooring with double machine polished and hand cut Tandur blue stone | As per relevant standard specifiction | 659 | M2 | 17463.5
22 | SWR33236 | 6.94 | Providing skirting with tandoor blue slabs including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Flooring | Providing skirting with tandoor blue slabs | As per relevant standard specifiction | 726 | M2 | 5038.44
23 | SWR33029 | 31.71 | Plain Cement contrete - Nominal Mix (1:3:6) using 40 mm metal with concrete mixture including cost and conveyance of all materials labour charges etc. complete for finished iitem of work and as directed by the engineer-in-charge. | Concrete | Plain Cement contrete - Nominal Mix (1:3:6) using 40 mm metal | As per relevant standard specifiction | 4371 | M3 | 138604.41
24 | SWR33030 | 6.75 | PCC(1:2:4) using 10 to 12 mm aggregate including cost and conveyance of all materials labour charges etc., complete for finished iitem of work and as directed by the engineer-in-charge. | Concrete | PCC(1:2:4) using 10 to 12 mm aggregate | As per relevant standard specifiction | 5504 | M3 | 37152
25 | SWR33057 | 65.92 | Supply and Spreading of 20mm machine crushed metal including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Metal | Supply and Spreading of 20mm machine crushed metal | As per relevant standard specifiction | 1514 | M3 | 99802.88
26 | SWR33403 | 110 | Supply and fixing of fencing of welded wire mesh (1" x 2") of 3mm dia with support channels of 75x 40mm and angles around of 30x30x3 mm including cost and conveyance of all materials, fabrication charges, painting charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Welded Mesh | Supply and fixing of fencing of welded wire mesh | As per relevant standard specifiction | 2042 | M2 | 224620
27 | SWR33404 | 10.68 | Supply and fixing of MS gates of approved design including cost and conveyance of all materials,fabrication charges etc complete for finished item of work. | Gate | Supply and fixing of MS gates | As per relevant standard specifiction | 4579.89 | M2 | 48913.2252
28 | SWR33333 | 104.6 | Painting with two coats of OBD over a coat of primer including cost and conveyance of all materials ,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Paint | Painting with two coats of OBD over a coat of primer | As per relevant standard specifiction | 109.9 | M2 | 11495.54
29 | SWR33336 | 153 | Painting with two coats of ACE paint over a coat of primer including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Paint | Painting with two coats of ACE paint | As per relevant standard specifiction | 195.91 | M2 | 29974.23
30 | SWR33329 | 196.5 | Painting with lovely cem three coats including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Paint | Painting with lovely cem three coats | As per relevant standard specifiction | 70.47 | M2 | 13847.355
31 | SWR33415 | 7.3 | Manufacture, supply ,laying and fixing of 450mm dia. NP3 class R.C.C. socket and spigot pipes (rate per meter of effective length) including transportaion ,taxes and duties etc. complete for finished item of work and as directed by the Engineer-in-charge. | Culvert Pipe | Hume pipe of 450mm dia | As per relevant standard specifiction | 1344 | RMT | 9811.2
32 | SWR33442 | 25 | S&F Conceal PVC Pipe 32mm dia in Slab | Electrification | S&F Conceal PVC Pipe 32mm dia in Slab | As per relevant standard specifiction | 85 | RMT | 2125
33 | SWR33441 | 15 | S&F Conceal PVC Pipe 20mm dia in Wall | Electrification | S&F Conceal PVC Pipe 20mm dia in Wall | As per relevant standard specifiction | 89 | RMT | 1335
34 | SWR33457 | 15 | Wiring with 2X1.0 Sqm(14/.3mm) PVC insulated flexiable copper cable in the existing metalic/Non metalic conduit pipe with 6A mini modular SP switch, mounted on metalic box covereds with appropriate front plate modules etc ceiling rose including cot and conveyance of all mateials, labour charges complete for light points, bell points and fan points in non residential builsing except circuit moving finished in all types masonary as directed by department. | Electrification | Wiring with 2X1.0 Sqm(14/.3mm) PVC insulated flexiable copper cable | As per relevant standard specifiction | 580 | EA | 8700
35 | SWR33461 | 2 | Supply and fixing of 6A 3/2 pin flush type plug socket with 6A flush type marked switch control on a common board with earth continuity including wire leads earth connections along with all labour charges etc. complete | Electrification | Supply and fixing of 6A 3/2 pin flush type plug socket | As per relevant standard specifiction | 469 | EA | 938
36 | SWR33464 | 2 | Supply and fixing of 16A 3pin flush type plug socket and 16A flush type fuse unit and 16A switch control. | Electrification | Supply and fixing of 16A 3pin flush type plug socket | As per relevant standard specifiction | 437 | EA | 874
37 | SWR33484 | 4 | Supply and fixing of slanting holders with 100W bulb with all connections and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | Supply and fixing of slanting holders with 100W bulb | As per relevant standard specifiction | 116 | EA | 464
38 | SWR33545 | 4 | Supply and fixing of patty type tube light fitting with 4' 0" - 40W tube light,40W copper choke,starter,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | Supply and fixing of patty type tube light fitting | As per relevant standard specifiction | 868 | EA | 3472
39 | SWR33494 | 90 | Supply and run of 2 of 14/.3mm(1.00Sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | Supply and run of 2 of 14/.3mm(1.00Sqmm) | As per relevant standard specifiction | 48 | RMT | 4320
40 | SWR33497 | 30 | Supply and run of 2 of 36/0.3 (2.5sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | Supply and run of 2 of 36/0.3 (2.5sqmm) | As per relevant standard specifiction | 95 | RMT | 2850
41 | SWR33520 | 1 | SPN Distribution board with IP-20 protection suitable for single phase 40A DP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 4Nos as out going MCBs in sheet steel enclosure including connections and cost of all material labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | SPN Distribution board with IP-20 protection | As per relevant standard specifiction | 5038 | EA | 5038
42 | SWR33596 | 1 | Providing independent earthing for main switches,IC cutouts and motors using 40mm. Dia. B-class G.I.Pipe of 2.5' length duly providing 12mm. Dia. 6No. Holes and required bolts,nuts and washers,including filling with equal preparation of salt and charcoal in layers and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | Providing independent earthing | As per relevant standard specifiction | 4891 | EA | 4891
43 | SWR33597 | 15 | Supply and run of No.8 SWG Copper wire including cost of all accessories and labour charges etc., Complete | Electrification | Supply and run of No.8 SWG Copper wire | As per relevant standard specifiction | 140 | RMT | 2100
44 | SWR33563 | 2 | Supply and Fixing of 48" ceiling fan of bajaj make(or equivalent make) including cost material,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | Supply and Fixing of 48" ceiling fan | As per relevant standard specifiction | 2215 | EA | 4430
45 | SWR33224 | 15.8 | Supply and fixing of ceramic tiles fantacy for dadoing including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Tiles | Supply and fixing of ceramic tiles | As per relevant standard specifiction | 759 | M2 | 11992.2
46 | SWR34311 | 1 | Supply and fixing of 580mm x 440mm long Orissa pan of Parry, Neycer or Hindhusthan, make with 'P' or 'S' trap etc complete for finished item of work and as directed by the engineer-in-charge. | Sanitary | S&F of 580mm x 440mm long Orissa pan | As per relevant standard specifiction | 2178 | EA | 2178
47 | SWR34386 | 2 | Supply and Fixing 4" PVC floor trap including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Sanitary | Supply and Fixing 4" PVC floor trap | As per relevant standard specifiction | 269 | EA | 538
48 | SWR34382 | 2 | Supply,fixing 90mm dia. PVC Plain Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Sanitary | Supply,fixing 90mm dia. PVC Plain Bend | As per relevant standard specifiction | 84 | EA | 168
49 | SWR34385 | 1 | Supply,fixing 90mm dia. PVC Door Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Sanitary | Supply,fixing 90mm dia. PVC Door Bend | As per relevant standard specifiction | 81 | EA | 81
50 | SWR34286 | 1 | S&Fixing 150mm x 100mm SWG gully traps Ist class grating & constg brick masonry in CM (1:6) prop inter mediate chamber and fitted with CI frame etc complete. | Sanitary | S&Fixing 150mm x 100mm SWG gully traps | As per relevant standard specifiction | 749 | EA | 749
51 | SWR34377 | 6 | Supply and Fixing 4" dia 3M Single socket PVC pipe including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Sanitary | S&F 4" dia 3M Single socket PVC pipe | As per relevant standard specifiction | 422 | RMT | 2532
52 | SWR34453 | 1 | Supply and Fixing 4" dia PVC cowl including labour charges etc. complete for finished item of work. | Sanitary | Supply and Fixing 4" dia PVC cowl | As per relevant standard specifiction | 23 | EA | 23
53 | SWR34444 | 1 | Construction of soak pit with 4' dia RCM rings upto a depth of 6' including cost and conveyance of all materials as directed by the engineer-in-charge. | Sanitary | Construction of soak pit with 4' dia RCM rings | As per relevant standard specifiction | 2950 | EA | 2950
54 | SWR34361 | 20 | CPVC Pipes and Fittings a) 15.90mm OD Pipe - SDR 11 | Plumbing | CPVC Pipes and Fittings a) 15.90mm OD Pipe - SDR 11 | As per relevant standard specifiction | 239 | RMT | 4780
55 | SWR34362 | 100 | CPVC Pipes and Fittings b) 22.20mm OD Pipe - SDR 11 | Plumbing | CPVC Pipes and Fittings b) 22.20mm OD Pipe - SDR 11 | As per relevant standard specifiction | 313 | RMT | 31300
56 | SWR34363 | 100 | CPVC Pipes and Fittings c) 28.60mm OD Pipe - SDR 11 | Plumbing | CPVC Pipes and Fittings c) 28.60mm OD Pipe - SDR 11 | As per relevant standard specifiction | 410 | RMT | 41000
57 | SWR34344 | 18 | Supply and fixing of 15mm dia. SS coated taps including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | Supply and fixing of 15mm dia. SS coated taps | As per relevant standard specifiction | 230 | EA | 4140
58 | SWR34345 | 1 | Supply and fixing of 20mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | Supply and fixing of 20mm dia. GM Ball | As per relevant standard specifiction | 331 | EA | 331
59 | SWR34346 | 2 | Supply and fixing of 25mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | Supply and fixing of 25mm dia. GM Ball | As per relevant standard specifiction | 466 | EA | 932
60 | SWR34329 | 3 | Supply and fixing of 12.7mm bib tap Indian make including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | Supply and fixing of 12.7mm bib tap | As per relevant standard specifiction | 271 | EA | 813
61 | SWR34375 | 500 | Providing and placing on Terrace polyetheylene water storage tank with double layer approved brand and manufacture with cover complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | Providing and placing on Terrace polyetheylene water storage tank | As per relevant standard specifiction | 10 | L | 5000
62 | SWR33746 | 1 | Supply of steel table of size 4'x2.5'x30" with 18 mm plywood fixed with rubber beeding with drawers on right side with automatic locking arrangements etc complete for finished item of work and as directed by the engineer-in-charge. | Furnitre | Supply of steel table of size 4'x2.5'x30" | As per relevant standard specifiction | 4200 | EA | 4200
63 | SWR33857 | 1 | Supply of 'S' type chair with arms teakwood frame with seat back 's' type on G.I pipe including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Furnitre | Supply of 'S' type chair with arms teakwood frame | As per relevant standard specifiction | 3850 | EA | 3850
64 | SWR33858 | 2 | Supply of P V C chairs of Neelkamal of approved quality & make including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Furnitre | Supply of P V C chairs of Neelkamal | As per relevant standard specifiction | 1150 | EA | 2300
65 | SWR33406 | 150 | S&Fixing of R.C.C fencing poles of size 0.115mx0.115mx2.7m including cost & conveyance of all materials,labour chargesv etc complete for finished item of work. | Fencing | S&Fixing of R.C.C fencing pole 0.115x0.115x2.7m | As per relevant standard specifiction | 1433.9 | EA | 215085
66 | SWR33405 | 76 | Providing and fixing 1.80 metre long RCC fencing posts with 6 mm bar bibs of pole size 0.1x0.1x1.8m in pit size of 0.45x0.45x0.45 and filled with PCC (1:4:8) using 20mm metal including cost & conveyance of all materials, labour charges etc complete for finished item of work. | Fencing | S&Fixing of R.C.C fencing pole 0.1x0.1x1.8m | As per relevant standard specifiction | 1293.04 | EA | 98271.04
67 | SWR33407 | 275 | S&Fixing of barbed wire 8 straight strands and 2 cross strands including cost & conveyance of all materials, labour charges etc complete for finished item of work. | Fencing | S&Fixing of barbed wire | As per relevant standard specifiction | 260.05 | M | 71513.75
68 | SWR33421 | 1.35 | S&F MS Board | Name board | S&F MS Board | As per relevant standard specifiction | 4542.3 | M2 | 6132.105
69 | SWR33423 | 2.21 | S&F Poly Vinyl Acrylic Board | Name board | S&F Poly Vinyl Acrylic Board | As per relevant standard specifiction | 1930.48 | M2 | 4266.3608
70 | SWR33608 | 1 | Geophysical Investgation Charges | Borewell | Geophysical Investgation Charges | As per relevant standard specifiction | 5000 | EA | 5000
71 | SWR33609 | 90 | Drilling-165mm Bore Well 0 to 90M | Borewell | Drilling-165mm Bore Well 0 to 90M | As per relevant standard specifiction | 336 | M | 30240
72 | SWR34830 | 30 | Drilling-165mm Bore Well 90m to 120M | Borewell | Drilling-165mm Bore Well 90m to 120M | As per relevant standard specifiction | 369 | M | 11070
73 | SWR34831 | 30 | Drilling-165mm Bore Well 120m to 150M | Borewell | Drilling-165mm Bore Well 120m to 150M | As per relevant standard specifiction | 394 | M | 11820
74 | SWR33611 | 30 | S&F 160mm dia PVC Casing | Borewell | S&F 160mm dia PVC Casing | As per relevant standard specifiction | 844 | M | 25320
75 | SWR33636 | 1 | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | Borewell | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | As per relevant standard specifiction | 34237 | EA | 34237
76 | SWR33641 | 200 | S&R 3C 2.5sqmm Flat Copper Cable | Borewell | S&R 3C 2.5sqmm Flat Copper Cable | As per relevant standard specifiction | 190 | EA | 38000
77 | SWR33644 | 1 | S&E D.O.L Starter 250V Single Phase | Borewell | S&E D.O.L Starter 250V Single Phase | As per relevant standard specifiction | 1040 | EA | 1040
78 | SWR34203 | 1 | Supply & fixing of Flange Clamps | Borewell | Supply & fixing of Flange Clamps | As per relevant standard specifiction | 182 | EA | 182
79 | SWR34410 | 145 | S&F HDPE Pipe 40mm dia 6kg/sqcm | Borewell | S&F HDPE Pipe 40mm dia 6kg/sqcm | As per relevant standard specifiction | 160 | Rmt | 23200
80 | SWR34470 | 95 | Seigniorage Charges - Sand | Seignorages | Seigniorage Charges - Sand | As per relevant standard specifiction | 40 | M3 | 3800
81 | SWR34471 | 96.5 | Seigniorage Charges - Metal | Seignorages | Seigniorage Charges - Metal | As per relevant standard specifiction | 97.5 | M3 | 9408.75
82 | SWR34472 | 760.2 | Seigniorage Charges - Gravel | Seignorages | Seigniorage Charges - Gravel | As per relevant standard specifiction | 30 | M3 | 22806
[7 empty] | Civil total |  | 3255984.1064
[6 empty] | Electrical & civil total |  |  | 10623526.3424

## 10. Rajampet SS
Rajampet SS Schedules(WBS No: S-1380-90-06-01-01-002)
Name of the work: Estimate for erection of new 33/11 KV SS with connected 33 KV and 11 KV lines at Rajampet (Vg) in Sangareddy (M)of Sangareddy Division of Sangareddy Circle .
S.No | SSR Code | Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR10105 | 39 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 23400
2 | SWR10343 | 31 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 74400
3 | SWR10356 | 27.28 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt)*31 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 179475.12
4 | SWR11890 | 0.96 | ERECTION OF S.S. STRUCTURE: Coping of 0.45x0.45x0.45Mt with 1:8 slope Using form boxes (0.031Cumt.) | Civil work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | M3 | 3737.28
5 | SWR11331 | 31 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of poles with two coats of white cement (including cost of paint). | Electrical work | Paint-9.1M PSCC Poles as desc SSR | As per relevent standard specification | 485 | EA | 15035
6 | SWR11889 | 5.5 | Fabrication of 100 X 50mm MS Channel for formation of 11kV and 33kV bays: Fabrication and erection of M.S,Channel 100x50mm for forming of 33KV & 11 KV Bays as per standard specifications to facilitate stringing of bus, erection of LA sets, AB Switches bolts & Nuts etc. including painting with one coats of red oxide and two coats of Aluminium paint. GI bolts&nuts shall be used. | Electrical work | Fabr & Erect-MS Chnl 100x50mm for SS Bay | As per relevent standard specification | 6600 | TO | 36300
7 | SWR10404 | 116 | Erection of 33kV and 11kV Strung Bus with Panther (200Sqmm) ACSR Conductor: Erection of 33kV and 11kV Bus over the Substation structures with 200sqmm Panther ACSR conductor and giving Jumpers to connect the Switch gear by providing the suitable T clamps and round clamps suitable to Post type insulators & Insulators. | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 38010.88
8 | SWR10392 | 2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 9000
9 | SWR10393 | 10 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 32000
10 | SWR11742 | 3 | Supply & erection of 11 kV 400 A convential single(1/3) phasing AB switches.includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | S&E-400A 11KV ABSwth Conv 1ph(1/3) in SS | As per relevent standard specification | 4232 | EA | 12696
11 | SWR21240 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt). | Electrical work | Hoisting post ins&hrd wr 1panther 33kv | As per relevent standard specification | 781 | EA | 1562
12 | SWR21241 | 4 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 11kv | As per relevent standard specification | 507 | EA | 2028
13 | SWR10881 | 11 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 1562
14 | SWR23224 | 20.57 | Excavation of pit in all types of soils of size 2.2x2.2x0.85Mts.for Construction of Plinths for VCB (33KV & 11 KV ) | Earth work | Excavate-Pit for 33KV VCB | As per relevent standard specification | 331 | M3 | 6808.67
15 | SWR20685 | 27.8 | Providing of Base concreting (2.2x2.2x0.15 Mts) with 1:3:6 Concrete mix. Using form boxes, Providing of Concreting (2x2x1.0mts) with 1:3:6 Cocrete mix. Plastering of the plinth for smooth finishing with 12mm thick 1:3 cement motor and providing two coats white washing for part of the plinth above groung level. | Civil work | Cement concrete with 40MM metal VCB plin | As per relevent standard specification | 5160 | M3 | 143448
16 | SWR10461 | 5 | Erection of Switchgear complete for 11 kV VCB includes Assembling the VCB Structures and mounting the VCBs over the already erected foudation including wiring of Breaker Control Panel/CTs, erection of CTs and control pannel providing Jumpers. | Electrical work | Erection of 11kv VCB | As per relevent standard specification | 12000 | EA | 60000
17 | SWR10396 | 2 | Erection of 33KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 1760
18 | SWR10397 | 1 | Erection of 11 KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 11kv LA stn type incl earthing | As per relevent standard specification | 559 | SET | 559
19 | SWR10398 | 4 | Erection of 11 KV Lightening Arrestors line type complete including jumpering. | Electrical work | Erect of 11kvLA line type incl earthing | As per relevent standard specification | 505 | SET | 2020
20 | SMR11607 | 1 | Supply of 33kv HG fuse set including providing of jumpers | Electrical work | S-33KV HG Fuse Set excl Ins & Chnl | As per relevent standard specification | 6431 | SET | 6431
21 | SWR10394 | 1 | Erection of 33kv HG fuse set including providing of jumpers | Electrical work | Erect. of 33kv HG Fuseset incl earthing | As per relevent standard specification | 1331.81 | SET | 1331.81
22 | SMR11608 | 1 | Supply of 11kv HG fuse set including providing of jumpers | Electrical work | S-11KV HG Fuse Set | As per relevent standard specification | 1733.75 | SET | 1733.75
23 | SWR10395 | 1 | Erection of 11kv HG fuse set including providing of jumpers | Electrical work | Erect. of 11kv HG Fuseset incl earthing | As per relevent standard specification | 740.52 | SET | 740.52
24 | SMR11482 | 22 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 76692
25 | SWR10357 | 22 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 27152.4
26 | SWR10920 | 500 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification.75x8 mm MS flat for Earth mat and connecting to electrodes. | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 32500
27 | SWR10919 | 950 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification. 50x6 mm MS flat for raisers, double flat shall be run for structure poles raisers & equipment earthing. | Electrical work | Earthing for raisers of SS Flat 50x6 mm. | As per relevent standard specification | 41 | RMT | 38950
28 | SMR40033 | 2 | Providing of double earthing for neutral with flexible copper jumpers of adequate size including arrangement by fixing M.S.Channel 100x50mm. | Electrical work | SupCU Flexi jumper for Power T/F Neutral | As per relevent standard specification | 4725 | EA | 9450
29 | SWR11771 | 5 | Erection of 24 Volts Battery along with Charger on the VCB plinth and giving DC supply to VCB's. | Electrical work | Erect-24V Batery with Chrgr incl grot-SS | As per relevent standard specification | 1050 | EA | 5250
30 | SWR11474 | 750 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable includes excavation of earth and back filling with sand and earth in alternate layers . The cable termination shall be made by providing proper size lugs and shall be identified with colours. | Electrical work | Laying-4 core cable | As per relevent standard specification | 15 | RMT | 11250
31 | SWR10463 | 1 | Erection of 25 kVA Three phase Station Transformer on the Substation Structures and giving jumpers/connections on HT side to the 11kV bus. Belting angle shall be provided both sides of DTR for securing DTR firmly in position. | Electrical work | Erection of Three Phase DTRs | As per relevent standard specification | 1139.95 | EA | 1139.95
32 | SMR40045 | 1 | Supply of AC Panel Board includes: Fixing of 1 No.100A, MCCB, 10kA capacity of any standard make including material cost. Fixing of suitable panel box 3x3x1 with M.S.Sheet of 16 SWG with front door compartments inclusive of material cost & powder coating (with C Channel ). Fabrication of panel Fixing of 96x96mm analog voltmeter with VSS switch Fixing of 20A HRC fuse Fixing of 3 phase supply indicator kwith HRC fuses Supply and fixing of 6 Sqmm copper flexible wire (PVC) Fixing of Stud type TBs for outgoing feeder Fixing of Epoxy bus supports. | Electrical work | Supply of AC Supply panel complete | As per relevent standard specification | 42000 | EA | 42000
33 | SMR40044 | 1 | Supply of DC Panel Board Fixing of suitable panel box of size 6'x6'x1' with M S sheet of 16 SWG with back doors (4'x6') and on front side with provision to fix up bakelite hylam sheet size of 4'x6' including cost of the panel with powder coating. Fixing of best quality of angles for panel. Fixing of C Channelfor panel. Fabrication of control panel including making suitable holes and board Fixing of Stud type TBs for outgoing feeder Fixing of 24V DC pilot lamps of standard make Fixing of healthy trip push buttons with LED lamp Fixing of plain switches for alarm acceptance and for PTR signal Fixing of ON/OFF push buttons Fixing of digital volt meter for 11kV Fixing of VSS of standard make, Fixing of Engraved AL plates for Alarm panel of various VCB Laying of 2.5Sqmm copper flexible wire for internal wiring . Fixing of digital frequency meter Fixing of Copper lugs and ferrules for internal wiring. Fixing of 4" Gang bells 24V DC Fixing of flow diagram with rading strip Fixing of HRC fuse units | Electrical work | Supply of DC Anunc.relay panel 8 feeders | As per relevent standard specification | 42500 | EA | 42500
34 | SWR11893 | 2 | fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supplied by tenderer. | Electrical work | Erect-Contrl/Relay, AC, Announ. Panels | As per relevent standard specification | 1930 | EA | 3860
35 | SWR10342 | 8 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 12000
36 | SWR10956 | 8 | Fixing of Metal halide/LED lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5M GI pipe complete. | Electrical work | Fixing of LED/Metal halide complete. | As per relevent standard specification | 1268 | EA | 10144
37 | SWR20028 | 8 | Supply and Fixing of junction box and Providing with proper Fuse protection and required glauds suitable for Cable Terminations. The box shall be fixed on the pole. | Electrical work | 33/11kv S.S Yard lighting junction box | As per relevent standard specification | 351.9 | EA | 2815.2
38 | SWR20526 | 1 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply & fixing of marshall box | As per relevent standard specification | 3085.5 | EA | 3085.5
39 | SMR40088 | 1 | Supply and fixing of filled sand bucket set complete (4 Nos. Buckets) with stand to mount fire buckets. | Electrical work | Sup Fire Buckets Stand with Buckets | As per relevent standard specification | 1386 | SET | 1386
40 | SMR40087 | 2 | Supply and fixing of CO2 Cylinder set as per IS2878 Specifications. | Electrical work | Sup TrollyMounted Co2 Cylinders(IS-2878) | As per relevent standard specification | 9240 | EA | 18480
41 | SWR11895 | 1 | Supplying and fixing of feeder indicator board to each of the 3Nos feeder breakers and LV breaker, danger boards made of 1'x1' and properly mounted on the structures. The letters written on the borad shall be 1.5"size with blue colour and background shall be of white colour | Electrical work | S&F-33/11KV SS Feeder Indicator Board | As per relevent standard specification | 551 | SET | 551
42 | SWR20032 | 1 | Supply and fixing of wooden board of size 3'x2'.5'indicating the layout of the Switch yard. | Electrical work | Sup &fix of board ind Switchyard layout | As per relevent standard specification | 1654 | EA | 1654
43 | SMR40086 | 1 | Supply and Erection of Permanent Name Board of on 3'x4' steel sheetmounted on steel frame as described in Specification. | Electrical work | Sup 33/11kv S.S Permanent name board | As per relevent standard specification | 10238 | EA | 10238
44 | SMR40076 | 1 | Supply of Digital clamp meter. | Electrical work | Supply of Digital clamp meter. | As per relevent standard specification | 2888 | EA | 2888
45 | SMR40064 | 1 | Supply of Rechargeable LED torch light of Standard make. | Electrical work | Sup Rechargeable LED torch light. | As per relevent standard specification | 1733 | EA | 1733
46 | SMR40063 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box containing ‘D’Spanners from size 6 to 54, Hammer small and big size, Ring spanners from 6 to 28, Adjustable spanner, Pipe wrench, Cutting Plier, Nose plier, Tester, insulated Screw drive. | Electrical work | SupTaparia Tool kit complete as per Spec | As per relevent standard specification | 4925 | SET | 4925
47 | SWR22090 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Electrical work | Sup& fix safety inst/SS Op. inst board | As per relevent standard specification | 2205 | EA | 2205
48 | SMR11598 | 8 | Supply of 25 W LED lamp with fitting of philips make | Electrical work | S-25W LED fixture set | As per relevent standard specification | 3200 | EA | 25600
49 | SMR12378 | 1 | Supply of Alluminum Ladder(20 feet) | Electrical work | S-10ft Aluminium Ladder | As per relevent standard specification | 1654 | EA | 1654
50 | SMR40075 | 1 | Supply of Megger (2000 ohms, 0-2.5kv) | Electrical work | Supply of Earth megger (1000v) | As per relevent standard specification | 8085 | EA | 8085
51 | SMR40067 | 2 | Supply of Hand Gloves | Electrical work | Supply of Hand Gloves | As per relevent standard specification | 289 | SET | 578
52 | SMR40071 | 2 | Supply of Safety Helmets of standard make | Electrical work | Supply of Safety Helmet of standard make | As per relevent standard specification | 231 | EA | 462
53 | SMR11599 | 4 | Supply of Earth Discharging Rod 10' length. | Electrical work | S-Earth Rod 8ft Long 3mm Thick | As per relevent standard specification | 1000 | EA | 4000
54 | SMR11488 | 200 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 23500
55 | SMR11591 | 66 | Supply of PG clamps for panther 2 bolted 800 A. | Electrical work | S-Al. alloy three bolted PG clamps 800A | As per relevent standard specification | 130 | EA | 8580
56 | SWR20029 | 350 | Supply and Laying of 2 core/4 core cable includes excavation earth and back filling with sand and earth in alternate layers as shown in the sketch. The cable termination shall be made by providing proper size of lugs at both ends of the cable termination. | Electrical work | 33/11kv S.S laying of 2/4core for light | As per relevent standard specification | 50 | M | 17500
57 | SWR20308 | 31 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 12625.99
58 | SWR20307 | 8 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 2172.16
59 | SWR11860 | 2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 5440.68
60 | SWR10150 | 10.5 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 6479.55
61 | SWR10206 | 10.5 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 2320.5
62 | SWR10524 | 10.5 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 1942.5
63 | SWR11220 | 350 | Loading and unwinding of Panther conductor. | Electrical work | Load-Unwinding Panther conductor | As per relevent standard specification | 3 | M | 1050
64 | SWR11221 | 350 | Unloading of Panther conductor. | Electrical work | Unload-Unwinding Panther conductor | As per relevent standard specification | 2 | M | 700
65 | SWR12416 | 2 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 4
66 | SWR10631 | 2 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 4
67 | SWR10618 | 2 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 130
68 | SWR10632 | 2 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 130
69 | SWR10212 | 2 | Loading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | LOADING of 11kv Pin/Post/Solid Core Insu | As per relevent standard specification | 1 | CRT | 2
70 | SWR10530 | 2 | Unloading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | UNLOADING of 11kv Pin/Post/Solid Core In | As per relevent standard specification | 1 | CRT | 2
71 | SWR11701 | 750 | Loading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | Load-PVC Control Cable 10C | As per relevent standard specification | 1 | M | 750
72 | SWR11712 | 750 | Unloading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | UnLoad-PVC Control Cable 10C | As per relevent standard specification | 1.02 | M | 765
73 | SWR11691 | 1 | Loading of 3Ph 25KVA Distribution Transformer. | Electrical work | Load-3Ph 25KVA DTR | As per relevent standard specification | 252 | EA | 252
74 | SWR11692 | 1 | UnLoading of 3Ph 25KVA Distribution Transformer. | Electrical work | UnLoad-3Ph 25KVA DTR | As per relevent standard specification | 202 | EA | 202
75 | SWR10200 | 1 | Loading of 33/11 KV Current Transformers/ Potential Transformers. | Electrical work | LOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 165 | EA | 165
76 | SWR10266 | 6 | Loading of 33 KV10 KA LAs Station type. | Electrical work | LOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 41 | EA | 246
77 | SWR10584 | 6 | Unloading of 33 KV10 KA LAs Station type. | Electrical work | UNLOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 35 | EA | 210
78 | SWR10265 | 9 | Loading of 11 KV10 KA LAs Line type. | Electrical work | LOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 288
79 | SWR10583 | 9 | Unloading of 11 KV10 KA LAs Line type. | Electrical work | UNLOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 288
80 | SWR10264 | 3 | Loading of 11 KV10 KA LAs Station type. | Electrical work | LOADING of 11 KV,10 KA LAs Station type | As per relevent standard specification | 32 | EA | 96
81 | SWR10582 | 3 | Unloading of 11 KV10 KA LAs Station type. | Electrical work | UNLOADING of 11 KV,10 KA LAs Station typ | As per relevent standard specification | 32 | EA | 96
82 | SWR10239 | 2 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 252
83 | SWR10557 | 2 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 158
84 | SWR10238 | 9 | loading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 720
85 | SWR10556 | 9 | Unloading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 720
86 | SWR11224 | 4 | Loading and Unloading of 12V/24V Battery Set. | Electrical work | Load/Unload-12V/24V Battery Set | As per relevent standard specification | 23 | EA | 92
87 | SWR10356 | 2.66 | ERECTION OF S.S. STRUCTURE: Providing of base concreting of size 0.76x0.76x0.15M with CC mix of ratio 1:3:6 Using form boxes(0.087Cu.Mt)x31 with 20mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 17500.14
88 | SWR10402 | 1 | Erection of 11kv Potential Transformer sets complete including jumpering. The LV side of the PT shall be provided with proper fuse protection mounted in separate marshalling boxwith proper size cable glands etc. The box shall be mounted on the Substation structure. | Electrical work | Erection of 11kv three phase PT s | As per relevent standard specification | 800 | SET | 800
89 | SWR10518 | 1 | Unloading of 33/11 KV Current Transformers/ Potential Transformers | Electrical work | UNLOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 128 | EA | 128
90 | SWR10674 | 1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
91 | SWR10356 | 4.32 | Concreting the location after erection of 8.0 Mtrs pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) ( 0.6x0.6x1.5)mtrs x 8 . | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 28421.28
92 | SWR21750 | 2 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply and fixing of PT Marshalling box | As per relevent standard specification | 1139.85 | EA | 2279.7
93 | SWR10884 | 50 | Connectionof equipment to bus and or another equipmentwithsingle zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Electrical work | Conn. of equip/bus single zebra/panther | As per relevent standard specification | 224 | EA | 11200
94 | swr20102 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Electrical work | Erection of 11kv TT type AB Switch | As per relevent standard specification | 1813.49 | EA | 1813.49
95 | SWR20905 | 1 | Erection of 3 Phase DTR including loading and Unloading DTR on the Structure/Plinth etc | Electrical work | E/r 3ph DTR inclu L&Un-T&C on plinth | As per relevent standard specification | 1650 | EA | 1650
96 | SWR10612 | 1 | Loading of 5 MVA Power Transformer | Electrical work | LOADING of 5 MVA PTR | As per relevent standard specification | 5079.6 | EA | 5079.6
97 | swr10626 | 1 | Unloading of 5 MVA Power Transformer | Electrical work | UNLOADING of 5 MVA PTR | As per relevent standard specification | 5079.6 | EA | 5079.6
98 | SMR40009 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for First coat of 1st GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 11995.5
99 | SWR10877 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 1st coat of Aluminium | Electrical work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 4680.5
100 | SMR40010 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for second coat of 2nd GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 7111.5
101 | SWR10879 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 2nd coat of Aluminium | Electrical work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 2651
102 | SMR25233 | 31 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 96391.71
103 | SMR22745 | 5500 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 315975
104 | SMR12321 | 2350 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 132587
105 | SMR12322 | 2280 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 128820
106 | SMR25232 | 8 | Supply of 8.0Mtr PSCC 140 Kg Pole | Electrical work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 12640
107 | SMR12315 | 2 | Supply of 33KV 800A DB Break AB Switch | Electrical work | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 81317.56
108 | SMR12316 | 2 | Supply of 11KV 800A DB Break AB Switch | Electrical work | S-11KV 800A DB Break AB Switch | As per relevent standard specification | 30847.46 | EA | 61694.92
109 | SMR12317 | 9 | Supply of 11KV 400A DB Break AB Switch | Electrical work | S-11KV 400A DB Break AB Switch | As per relevent standard specification | 18150 | EA | 163350
110 | SMR25200 | 1 | Supply of LT Distribution Box (SMC) | Electrical work | S-LT Distribution Box (SMC) | As per relevent standard specification | 7797 | EA | 7797
111 | SWR22092 | 0.44 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 336.6
112 | SWR10107 | 6 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 4200
113 | SWR10112 | 3 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | As per relevent standard specification | 1680 | EA | 5040
114 | SWR10105 | 8 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/ excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 4800
115 | SWR10978 | 9 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 37487.52
116 | SWR11083 | 8 | Erection of 9.1 Mts Sturt pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. | Electrical work | Erec of 9.1 Mts PSCC poles for stuts | As per relevent standard specification | 2400 | EA | 19200
117 | SWR10981 | 5 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Horizontal Cut point for 33 KV line | As per relevent standard specification | 1759.5 | EA | 8797.5
118 | SWR10356 | 7.399 | Concreting the location after erection of 11 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.6X0.6X1.5 Mts)* 7 = 7.399 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 48678.021
119 | SWR10366 | 0.44 | Paving of the 100 sqmm AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 12600.06 | KM | 5544.0264
120 | SMR11488 | 50 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 5875
121 | SWR11180 | 9 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 3887.73
122 | SWR20308 | 8 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 3258.32
123 | SWR10191 | 1 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 202
124 | SWR10509 | 1 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 100
125 | SWR11860 | 1 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 2720.34
126 | SWR10150 | 0.488 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 301.1448
127 | SWR10206 | 0.488 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 107.848
128 | SWR10524 | 0.488 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 90.28
129 | SWR10211 | 6 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 18
130 | SWR10529 | 6 | Unloading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 18
131 | SWR12416 | 5 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 10
132 | SWR10631 | 5 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 10
133 | SWR10618 | 2 | Loading of 33KV Metal parts bag of 25 nos | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 130
134 | SWR10632 | 2 | Unloading of 33 KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 130
135 | SWR10252 | 9 | Loading of 33KV Top fittings | Electrical work | LOADING of 33 KV Top fittings | As per relevent standard specification | 1 | EA | 9
136 | SWR10570 | 9 | Unloading of 33 KV Top fittings | Electrical work | UNLOADING of 33 KV Top fittings | As per relevent standard specification | 1 | EA | 9
137 | SWR10319 | 26 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 75 x 8 mm MS Flat | Electrical work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31 | EA | 806
138 | SWR10322 | 32 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 75 x 8 mm MS Flat | Electrical work | Fab Stay clamps with 75x8 mm MM Flat | As per relevent standard specification | 42 | EA | 1344
139 | SWR10378 | 9 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevent standard specification | 32 | EA | 288
140 | SWR10354 | 4 | Erection of 33 kv Stay set complete including fixing of bow ,fixing and binding of Eye bolt, Anchor rod, guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. | Electrical work | Assembly and erection of Stay set 33kv | As per relevent standard specification | 684.53 | SET | 2738.12
141 | SWR21190 | 4 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock,Hard rock Requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 2080
142 | SMR25236 | 9 | Supply of 11Mtr PSCC 365 Kg Pole | Electrical work | S-PSCC Pole 11Mtr 365 Kg | As per relevent standard specification | 5399 | EA | 48591
143 | SMR25233 | 8 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 24875.28
144 | SMR25229 | 5 | Supply of 33KV V-Cross Arm without Clamps | Electrical work | S-33KV V-Cross Arm without Clamps | As per relevent standard specification | 1678 | EA | 8390
145 | SMR25207 | 130 | Supply of MS Angle 65X65X6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 7442.5
146 | SMR22745 | 250 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 14362.5
147 | SMR12321 | 200 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 11284
148 | SMR25231 | 4 | Supply of 33KV MS Stay Set with BasePlate | Electrical work | S-33KV MS Stay Set with BasePlate | As per relevent standard specification | 1035 | SET | 4140
149 | SWR22092 | 0.89 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 11 kv line. | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 680.85
150 | SWR10107 | 2 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 1400
151 | SWR10105 | 12 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 7200
152 | SWR10110 | 5 | Excavation of Pole pits of size (2.6" x 2.6" x 5.0') 0.88 cum 0.76 M x 0.76M x 1.52M for 9.1 mtrs PSCC Poles including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD(2.6" x 2.6" x 5.0") | As per relevent standard specification | 1440 | EA | 7200
153 | SWR10978 | 2 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 8330.56
154 | SWR10343 | 17 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 40800
155 | SWR10342 | 20 | Erection of 8.0 Mts PSCC Poles including fixing of 11 KV X arm and top cleats and fixing of Pin insulators complete with necessary hard ware for tangential locations excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 30000
156 | SWR10653 | 14 | Formation of 11 kv cut points (Vertical/Horizantal) including fixing of 11 KV Cross arms,clamps, strain insulators sets complete with hardware and stays (Bows and Eye-bolts), Excluding the cost of pit Excavation and pole erection. The contractor has to supply GI Bolts and Nuts. | Electrical work | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1350 | EA | 18900
157 | SWR10356 | 10.214 | Concreting the location after erection of 11 mtrs/ 9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes for 2 no's 11 Mtrs poles (0.76X0.76X1.83 Mts)*2 = 2.114 Cu.Mt and 9 no's 9 Mtrs poles (0.76X0.76X1.52 Mts)*9 = 7.892 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 67197.906
158 | SWR10365 | 0.89 | Paving of the conductor 55 Sqmm AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 3 Cond | As per relevent standard specification | 8500 | KM | 7565
159 | SMR11488 | 60 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 7050
160 | SWR10206 | 0.699 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 154.479
161 | SWR10524 | 0.699 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 129.315
162 | SWR11248 | 54 | Loading 11KV Polymer Pin Insulator- with GI pins | Electrical work | Load-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 54
163 | SWR11249 | 54 | Unloading 11KV Polymer Pin Insulator with GI pins | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 54
164 | SWR10134 | 0.699 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 410.6765
165 | SWR11862 | 1 | Transport of VCB , Control pannels, current transformater, bosster etc, above 20 KM and upto 30 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 3691.38
166 | SWR10191 | 1 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 202
167 | SWR10509 | 1 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 100
168 | SWR11180 | 2 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 863.94
169 | SWR20307 | 20 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 5430.4
170 | SWR20308 | 17 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 6923.93
171 | SWR10228 | 9 | Loading of 11 KV V - Cross arms | Electrical work | LOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 36
172 | SWR10546 | 9 | Unloading of 11 KV V - Cross arms | Electrical work | UNLOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 36
173 | SWR12402 | 4 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 192
174 | SWR12421 | 4 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 192
175 | SWR10251 | 9 | Loading of 11 KV Top fittings | Electrical work | LOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 9
176 | SWR10569 | 9 | Unloading of 11 KV Top fittings | Electrical work | UNLOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 9
177 | SWR12416 | 84 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 168
178 | SWR10631 | 84 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 168
179 | SWR10353 | 10 | Erection of 11 kv Stay set complete including fixing of bow, fixing and binding of Eye bolt,Anchor rod,guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Assembly and erection of Stay set11kv&LT | As per relevent standard specification | 606.85 | SET | 6068.5
180 | SWR21190 | 20 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In Hard Gravel and Hard murram not requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 10400
181 | SWR10319 | 10 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 75 x 8 mm MS Flat | Electrical work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31 | EA | 310
182 | SWR10322 | 4 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 75 x 8 mm MS Flat | Electrical work | Fab Stay clamps with 75x8 mm MM Flat | As per relevent standard specification | 42 | EA | 168
183 | SWR10320 | 40 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 50 x 6 mm MS Flat | Electrical work | Fab Back clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 15 | EA | 600
184 | SWR10323 | 40 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 50 x 6 mm MS Flat | Electrical work | Fab Stay clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 25 | EA | 1000
185 | SWR10378 | 19 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevent standard specification | 32 | EA | 608
186 | SMR25236 | 2 | Supply of 11Mtr PSCC 365 Kg Pole | Electrical work | S-PSCC Pole 11Mtr 365 Kg | As per relevent standard specification | 5399 | EA | 10798
187 | SMR25233 | 17 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 52859.97
188 | SMR25232 | 20 | Supply of 8.0Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 31600
189 | SMR25218 | 9 | Supply of 11KV V X-Arms with MS Angle 65x65x6 | Electrical work | S-11KV V X-Arms with MS Angle 65x65x6 | As per relevent standard specification | 743 | EA | 6687
190 | SMR25205 | 260 | Supply of MS Channel 75x40 mm | Electrical work | S-MS Channel 75x40 mm | As per relevent standard specification | 58.45 | KG | 15197
191 | SMR25206 | 210 | Supply of MS Angle 50x50x6 | Electrical work | S-MS Angle 50x50x6 | As per relevent standard specification | 58.15 | KG | 12211.5
192 | SMR12321 | 30 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 1692.6
193 | SMR12322 | 170 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 9605
194 | SMR25214 | 10 | Supply of LT/11KV MS Stay Sets with Base Plate | Electrical work | S-LT/11KV MS Stay Sets with Base Plate | As per relevent standard specification | 1168 | SET | 11680
[6 empty] | Electrical Total |  |  | 2911644.3667
1 | SWR34179 | 4 | Levelling the site with the help of JCB including cost, conveyance of all materials,hire charges etc complete for finished item of work. | JCB | Hire-JCB to Level & Clear the Site | As per relevant standard specifiction | 2164.1 | H | 8656.4
2 | SWR33015 | 203.32 | Earth Work Mass Excavation (Ordinary rock not requiring blasting) to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions, labour and material charges etc., complete as directed by the engineer-incharge. | Earth Work | Excavation in Ordinary Soil | As per relevant standard specifiction | 347 | M3 | 70552.04
3 | SWR33028 | 42.25 | PCC (1:4:8) for levelling course using 40mm size hard broken Granite stone including cost and conveyance of all materials, HBG metal for foundations and leveling course and as directed by the Engineer- in - charge etc complete for finished item of work. | Concrete | PCC with 40mm Metal (1:4:8) | As per relevant standard specifiction | 4064 | M3 | 171704
4 | SWR33041 | 258.66 | CRS masonry in CM (1:6) using Hard Granite Stones including cost and conveyance of all materials, seignorage charges, labour charge for construction and for dressing stones to required size and shape, dewatering, scaffolding, cutting for all leads and lifts, all incidental charges etc .complete for finished item of work as directed by the Engineer - in - charge. | Masonry | CRS Masonary CM(1:6) 2nd Sort | As per relevant standard specifiction | 4437 | M3 | 1147674.42
5 | SWR33068 | 20.3 | Construction of brick masonary in CM(1:6) including cost and conveyance of all materials, labour charges etc. complete for finished item of work | Masonry | Brick Masonary in CM(1:6) GFloor | As per relevant standard specifiction | 7624 | M3 | 154767.2
6 | SWR33052 | 626.35 | Supplying and filling with borrowed gravel, watering, ramming, consolidating thoroughly complying with the standard specification including cost and conveyance of all materials, labour charges,hire charges of machnery,with all leads and incidental charges etc complete for finished item work | Earth Work | S&Filling with Borrowed Gravel | As per relevant standard specifiction | 435 | M3 | 272462.25
7 | SWR33098 | 6.53 | RCC M20 GRADE Nominal Mix (a) Footings | RCC | RCC Footing: M20Gr, Steel Centering | As per relevant standard specifiction | 8227 | M3 | 53722.31
8 | SWR33100 | 4.77 | RCC M20 GRADE Nominal Mix (b) Columns | RCC | RCC Column GF: M20Gr, Steel Centering | As per relevant standard specifiction | 10922 | M3 | 52097.94
9 | SWR33099 | 1.6 | RCC M20 GRADE Nominal Mix (c) Plinth Beams | RCC | RCC Plinth Beam: M20Gr, Steel Centering | As per relevant standard specifiction | 10647 | M3 | 17035.2
10 | SWR33107 | 0.67 | RCC M20 GRADE Nominal Mix (d) Lintels | RCC | RCC Lintel GF: M20Gr, Steel Centering | As per relevant standard specifiction | 11082 | M3 | 7424.94
11 | SWR33114 | 5.63 | RCC M20 GRADE Nominal Mix (e) Sunshade | RCC | RCC Sunshade GF: M20Gr, Steel Centering | As per relevant standard specifiction | 1162 | M2 | 6542.06
12 | SWR33121 | 2.35 | RCC M20 GRADE Nominal Mix (f) Roof Beams | RCC | RCC Roof Beam GF: M20Gr, Steel Centering | As per relevant standard specifiction | 10657 | M3 | 25043.95
13 | SWR33128 | 6.95 | RCC M20 GRADE Nominal Mix (g) Slab of 130 mm thick | RCC | RCC Roof Slab GF: M20Gr, Steel Centering | As per relevant standard specifiction | 10208 | M3 | 70945.6
14 | SWR33144 | 2.2 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) / Mild steel (MS) steel bars (Fe 415/ Fe 500 grade as per IS 1786-1979) of different diameters for RCC works complete for finished item of work in all floors.( APSS No.126) | Steel | Reinforcement Steel Fe 415/500 | As per relevant standard specifiction | 75077 | TO | 165169.4
15 | SWR33163 | 314.34 | Providing plastering of 20mm thick to all uneven faces of walls and ceiling of superstructure in two coats with base coat in CM 1:6 of 16mm thick and top coat in Cm 1:4 4mm thick with dubara sponge finish | Plastering | Plastering 20mm (16mm+4mm)GFloor | As per relevant standard specifiction | 410 | M2 | 128879.4
16 | SWR33184 | 136.5 | Raised pointing in CM(1:3) including curing, cost and conveyance of all materials and labour charges for complete item of work. | Pointing | Raised Pointing to CRS Masonary CM(1:3) | As per relevant standard specifiction | 94 | M2 | 12831
17 | SWR33156 | 54.87 | Providing impervious coat over RCC roof slab surfaces to requried slopes with 20mm thick in CM 1:3 pro mixed with approvaled brand of water proffing compound as the rate of 1 kg per bag of cement inclding cost and conveyance of all materials | Roof plastering | Impervious Coat 20mm CM(1:3) GFloor | As per relevant standard specifiction | 440 | M2 | 24142.8
18 | SWR33264 | 5.7 | Supply and fixing of Flush type Doors with 35mm Thick Flush Shutters with Bondwood solied Block Board Type Faced on Both the sides with Commercial Type Plywood for finished item work as directed by the Engineer - in- charge. | Doors | S&F MT Wood Frame & Door-Laminate | As per relevant standard specifiction | 6799.02 | M2 | 38754.414
19 | SWR33278 | 5.76 | Supply and Fixing of powder coated Aluminium sliding windows with fixed glass panels using aluminium sections 62x32x1.2mm providing 5mm plain glass fixed to frame with beading gasket and glazing clips with all accessories,locking arrangements including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Windows | S&F Powder Coated Al Window | As per relevant standard specifiction | 3535.64 | M2 | 20365.2864
20 | SWR33310 | 6.25 | Supplying and fixing of MS safety grill with peripheral frame of ISA 25x25x4mm and horizontal & vertical 8mm square rods and including cost and coveyance of all mateirals with all leads and lifts, labour charges, painting charges complete for finished item of work | Window grills | S&F of MS Safety Grill | As per relevant standard specifiction | 2539 | M2 | 15868.75
21 | SWR33219 | 26.5 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and approved size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and pointing with cement, labour etc, complete for finished item of work. | Flooring | Polished Shabad Flooring 20mm CM(1:3) | As per relevant standard specifiction | 659 | M2 | 17463.5
22 | SWR33236 | 6.94 | Providing skirting with tandoor blue slabs including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Flooring | Polished Shabad Skirting CM(1:3) | As per relevant standard specifiction | 726 | M2 | 5038.44
23 | SWR33029 | 31.71 | Plain Cement contrete - Nominal Mix (1:3:6) using 40 mm metal with concrete mixture including cost and conveyance of all materials labour charges etc. complete for finished iitem of work and as directed by the engineer-in-charge. | Concrete | PCC with 40mm Metal (1:3:6) | As per relevant standard specifiction | 4371 | M3 | 138604.41
24 | SWR33030 | 6.75 | PCC(1:2:4) using 10 to 12 mm aggregate including cost and conveyance of all materials labour charges etc., complete for finished iitem of work and as directed by the engineer-in-charge. | Concrete | PCC with 20mm Metal (1:2:4) | As per relevant standard specifiction | 5504 | M3 | 37152
25 | SWR33057 | 65.92 | Supply and Spreading of 20mm machine crushed metal including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Metal | S&Spreading of 20mm HBG Metal | As per relevant standard specifiction | 1514 | M3 | 99802.88
26 | SWR33403 | 110 | Supply and fixing of fencing of welded wire mesh (1" x 2") of 3mm dia with support channels of 75x 40mm and angles around of 30x30x3 mm including cost and conveyance of all materials, fabrication charges, painting charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Welded mesh | S&F MS Security Fencing Mesh (2"X2") | As per relevant standard specifiction | 2042 | M2 | 224620
27 | SWR33404 | 10.68 | Supply and fixing of MS gates of approved design including cost and conveyance of all materials,fabrication charges etc complete for finished item of work. | Gate | S&F MS Gate | As per relevant standard specifiction | 4579.89 | M2 | 48913.2252
28 | SWR33333 | 104.6 | Painting with two coats of OBD over a coat of primer including cost and conveyance of all materials ,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Painting | Painting with OBD 2Coats+Primer | As per relevant standard specifiction | 109.9 | M2 | 11495.54
29 | SWR33336 | 153 | Painting with two coats of ACE paint over a coat of primer including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Painting | Painting SnowCem/Apex 2 Coats+Primer | As per relevant standard specifiction | 195.91 | M2 | 29974.23
30 | SWR33329 | 196.5 | Painting with lovely cem three coats including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Painting | Painting with SuryaCem of 3 Coat | As per relevant standard specifiction | 70.47 | M2 | 13847.355
31 | SWR33415 | 7.3 | Manufacture, supply ,laying and fixing of 450mm dia. NP3 class R.C.C. socket and spigot pipes (rate per meter of effective length) including transportaion ,taxes and duties etc. complete for finished item of work and as directed by the Engineer-in-charge. | Electrification | S&F RCC Hume Pipe of 450mm dia | As per relevant standard specifiction | 1344 | RMT | 9811.2
32 | SWR33442 | 25 | S&F Conceal PVC Pipe 32mm dia in Slab | Electrification | S&F Conceal PVC Pipe 32mm dia in Slab | As per relevant standard specifiction | 85 | RMT | 2125
33 | SWR33441 | 15 | S&F Conceal PVC Pipe 20mm dia in Wall | Electrification | S&F Conceal PVC Pipe 25mm dia in Wall | As per relevant standard specifiction | 89 | RMT | 1335
34 | SWR33457 | 15 | Wiring with 2X1.0 Sqm(14/.3mm) PVC insulated flexiable copper cable in the existing metalic/Non metalic conduit pipe with 6A mini modular SP switch, mounted on metalic box covereds with appropriate front plate modules etc ceiling rose including cot and conveyance of all mateials, labour charges complete for light points, bell points and fan points in non residential builsing except circuit moving finished in all types masonary as directed by department. | Electrification | S&F Modular Switch LP,FP,EFP for NRBuild | As per relevant standard specifiction | 580 | EA | 8700
35 | SWR33461 | 2 | Supply and fixing of 6A 3/2 pin flush type plug socket with 6A flush type marked switch control on a common board with earth continuity including wire leads earth connections along with all labour charges etc. complete | Electrification | S&F Modular 3/2pin 6A Sockets | As per relevant standard specifiction | 469 | EA | 938
36 | SWR33464 | 2 | Supply and fixing of 16A 3pin flush type plug socket and 16A flush type fuse unit and 16A switch control. | Electrification | S&F Modular 3pin 16/6A Sockets | As per relevant standard specifiction | 437 | EA | 874
37 | SWR33484 | 4 | Supply and fixing of slanting holders with 100W bulb with all connections and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F Batten Holder | As per relevant standard specifiction | 116 | EA | 464
38 | SWR33545 | 4 | Supply and fixing of patty type tube light fitting with 4' 0" - 40W tube light,40W copper choke,starter,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F 20W LED Retro Tube Light | As per relevant standard specifiction | 868 | EA | 3472
39 | SWR33494 | 90 | Supply and run of 2 of 14/.3mm(1.00Sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | S&R 2 of 14/0.3mm (1.0M2m) (FR) | As per relevant standard specifiction | 48 | RMT | 4320
40 | SWR33497 | 30 | Supply and run of 2 of 36/0.3 (2.5sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | S&R 2 of 36/0.3mm (2.5M2m) (FR) | As per relevant standard specifiction | 95 | RMT | 2850
41 | SWR33520 | 1 | SPN Distribution board with IP-20 protection suitable for single phase 40A DP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 4Nos as out going MCBs in sheet steel enclosure including connections and cost of all material labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | S&F 8wySPNDB IP-20,10kA-6-32A SPMCB 4No | As per relevant standard specifiction | 5038 | EA | 5038
42 | SWR33596 | 1 | Providing independent earthing for main switches,IC cutouts and motors using 40mm. Dia. B-class G.I.Pipe of 2.5' length duly providing 12mm. Dia. 6No. Holes and required bolts,nuts and washers,including filling with equal preparation of salt and charcoal in layers and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | Provd-Independent Earthing | As per relevant standard specifiction | 4891 | EA | 4891
43 | SWR33597 | 15 | Supply and run of No.8 SWG Copper wire including cost of all accessories and labour charges etc., Complete | Flooring | S&R No.8 SWG Copper Wire | As per relevant standard specifiction | 140 | RMT | 2100
44 | SWR33563 | 2 | Supply and Fixing of 48" ceiling fan of bajaj make(or equivalent make) including cost material,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Sanitary | S&F 1200mm (48'') Sweep Ceiling Fan | As per relevant standard specifiction | 2215 | EA | 4430
45 | SWR33224 | 15.8 | Supply and fixing of ceramic tiles fantacy for dadoing including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | Ceramic Tile Flooring 20mm CM(1:3) | As per relevant standard specifiction | 759 | M2 | 11992.2
46 | SWR34311 | 1 | Supply and fixing of 580mm x 440mm long Orissa pan of Parry, Neycer or Hindhusthan, make with 'P' or 'S' trap etc complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F Orissa Pan WC 580mmx440mm | As per relevant standard specifiction | 2178 | EA | 2178
47 | SWR34386 | 2 | Supply and Fixing 4" PVC floor trap including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F Floor Trap (Bell Mouth) 110mm | As per relevant standard specifiction | 269 | EA | 538
48 | SWR34382 | 2 | Supply,fixing 90mm dia. PVC Plain Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Sanitary | S&F 90mm dia Plain Bend PVC/SWR Pipe | As per relevant standard specifiction | 84 | EA | 168
49 | SWR34385 | 1 | Supply,fixing 90mm dia. PVC Door Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F 75mm dia Door Bend PVC/SWR Pipe | As per relevant standard specifiction | 81 | EA | 81
50 | SWR34286 | 1 | S&Fixing 150mm x 100mm SWG gully traps Ist class grating & constg brick masonry in CM (1:6) prop inter mediate chamber and fitted with CI frame etc complete. | Plumbing | S&F 150mmx100mm SWG Gully Trap | As per relevant standard specifiction | 749 | EA | 749
51 | SWR34377 | 6 | Supply and Fixing 4" dia 3M Single socket PVC pipe including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Sanitary | S&F 110mm dia 3M 1Socket PVC/SWR Pipe | As per relevant standard specifiction | 422 | RMT | 2532
52 | SWR34453 | 1 | Supply and Fixing 4" dia PVC cowl including labour charges etc. complete for finished item of work. | Plumbing | S&F 4" dia PVC Cowl | As per relevant standard specifiction | 23 | EA | 23
53 | SWR34444 | 1 | Construction of soak pit with 4' dia RCM rings upto a depth of 6' including cost and conveyance of all materials as directed by the engineer-in-charge. | Plumbing | Construct- 4' dia & 5' Ht Soak Pit | As per relevant standard specifiction | 2950 | EA | 2950
54 | SWR34361 | 20 | CPVC Pipes and Fittings a) 15.90mm OD Pipe - SDR 11 | Plumbing | S&F 15.90mm OD CPVC Pipe-SDR 11 | As per relevant standard specifiction | 239 | RMT | 4780
55 | SWR34362 | 100 | CPVC Pipes and Fittings b) 22.20mm OD Pipe - SDR 11 | Plumbing | S&F 22.20mm OD CPVC Pipe-SDR 11 | As per relevant standard specifiction | 313 | RMT | 31300
56 | SWR34363 | 100 | CPVC Pipes and Fittings c) 28.60mm OD Pipe - SDR 11 | Plumbing | S&F 28.60mm OD CPVC Pipe-SDR 11 | As per relevant standard specifiction | 410 | RMT | 41000
57 | SWR34344 | 18 | Supply and fixing of 15mm dia. SS coated taps including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F 15mm GM Ball Valve | As per relevant standard specifiction | 230 | EA | 4140
58 | SWR34345 | 1 | Supply and fixing of 20mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F 20mm GM Ball Valve | As per relevant standard specifiction | 331 | EA | 331
59 | SWR34346 | 2 | Supply and fixing of 25mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | S&F 25mm GM Ball Valve | As per relevant standard specifiction | 466 | EA | 932
60 | SWR34329 | 3 | Supply and fixing of 12.7mm bib tap Indian make including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Furniture | S&F 12.7mm Bib Tap 400grams | As per relevant standard specifiction | 271 | EA | 813
61 | SWR34375 | 500 | Providing and placing on Terrace polyetheylene water storage tank with double layer approved brand and manufacture with cover complete for finished item of work and as directed by the engineer-in-charge. | Furniture | S&F Polyethylene Water Storage Tank | As per relevant standard specifiction | 10 | L | 5000
62 | SWR33746 | 1 | Supply of steel table of size 4'x2.5'x30" with 18 mm plywood fixed with rubber beeding with drawers on right side with automatic locking arrangements etc complete for finished item of work and as directed by the engineer-in-charge. | Furniture | Supply of Table 4'x2' with MS Frame | As per relevant standard specifiction | 4200 | EA | 4200
63 | SWR33857 | 1 | Supply of 'S' type chair with arms teakwood frame with seat back 's' type on G.I pipe including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Fencing | Supply of S-Type Chair | As per relevant standard specifiction | 3850 | EA | 3850
64 | SWR33858 | 2 | Supply of P V C chairs of Neelkamal of approved quality & make including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Fencing | Supply of PVC Chair | As per relevant standard specifiction | 1150 | EA | 2300
65 | SWR33405 | 150 | Providing and fixing 1.80 metre long RCC fencing posts with 6 mm bar bibs of pole size 0.1x0.1x1.8m in pit size of 0.45x0.45x0.45 and filled with PCC (1:4:8) using 20mm metal including cost & conveyance of all materials, labour charges etc complete for finished item of work. | Fencing | S&F RCC Fencing Pole 0.1mx0.1mx1.8m | As per relevant standard specifiction | 1293.04 | EA | 193956
66 | SWR33407 | 275 | S&Fixing of barbed wire 8 straight strands and 2 cross strands including cost & conveyance of all materials, labour charges etc complete for finished item of work. | Name board | S&F Barbed Wire 8H & 2Cross | As per relevant standard specifiction | 260.05 | M | 71513.75
67 | SWR33421 | 1.35 | S&F MS Board | Name board | S&F MS Board | As per relevant standard specifiction | 4542.3 | Sqm | 6132.105
68 | SWR33423 | 2.21 | S&F Poly Vinyl Acrylic Board | Borewell | S&F Poly Vinyl Acrylic Board | As per relevant standard specifiction | 1930.48 | Sqm | 4266.3608
69 | SWR33608 | 1 | Geophysical Investgation Charges | Borewell | Geophysical Investgation Charges | As per relevant standard specifiction | 5000 | EA | 5000
70 | SWR33609 | 90 | Drilling-165mm Bore Well 0 to 90M | Borewell | Drilling-165mm Bore Well 0 to 90M | As per relevant standard specifiction | 336 | M | 30240
71 | SWR34830 | 30 | Drilling-165mm Bore Well 90m to 120M | Borewell | Drilling-165mm Bore Well 90m to 120m | As per relevant standard specifiction | 369 | M | 11070
72 | SWR34831 | 30 | Drilling-165mm Bore Well 120m to 150M | Borewell | Drill-165mm Bore Well 120M to 150M | As per relevant standard specifiction | 394 | M | 11820
73 | SWR33611 | 30 | S&F 160mm dia PVC Casing | Borewell | S&F 160mm dia PVC Casing | As per relevant standard specifiction | 844 | M | 25320
74 | SWR33636 | 1 | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | Borewell | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | As per relevant standard specifiction | 34237 | EA | 34237
75 | SWR33641 | 200 | S&R 3C 2.5sqmm Flat Copper Cable | Borewell | S&R 3C 2.5sqmm Flat Copper Cable | As per relevant standard specifiction | 190 | EA | 38000
76 | SWR33644 | 1 | S&E D.O.L Starter 250V Single Phase | Borewell | S&E D.O.L Starter 250V Single Phase | As per relevant standard specifiction | 1040 | EA | 1040
77 | SWR34203 | 1 | Supply & fixing of Flange Clamps | Borewell | Supply & fixing of Flange Clamps | As per relevant standard specifiction | 182 | EA | 182
78 | SWR34410 | 145 | S&F HDPE Pipe 40mm dia 6kg/sqcm | Borewell | S&F HDPE Pipe 40mm dia 6kg/sqcm | As per relevant standard specifiction | 160 | Rmt | 23200
79 | SWR34470 | 144.2 | Seigniorage Charges - Sand | Borewell | Seigniorage Charges - Sand | As per relevant standard specifiction | 40 | M3 | 5768
80 | SWR34471 | 96.5 | Seigniorage Charges - Metal | Seigniorages | Seigniorage Charges - Metal | As per relevant standard specifiction | 97.5 | M3 | 9408.75
81 | SWR34472 | 626.35 | Seigniorage Charges - Gravel | Seigniorages | Seigniorage Charges - Gravel | As per relevant standard specifiction | 30 | M3 | 18790.5
[7 empty] | Civill total |  | 3752700.8064
[7 empty] | Electrical & Civil total |  | 6664345.1731

## 11. Andole SS
Andole SS Schedules
Name of the work: Estimate for erection of new 33/11 KV SS with connected 33 KV and 11 KV lines at Andole (V) in Andole(M) of Jogipet Division of Sangareddy Circle .
S.No | SSR Code | Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR10105 | 39 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 23400
2 | SWR10343 | 31 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 74400
3 | SWR10356 | 27.28 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt)*31 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 179475.12
4 | SWR11890 | 0.961 | ERECTION OF S.S. STRUCTURE: Coping of 0.45x0.45x0.45Mt with 1:8 slope Using form boxes (0.031Cumt.) | Civil work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | M3 | 3741.173
5 | SWR11331 | 31 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of poles with two coats of white cement (including cost of paint). | Electrical work | Paint-9.1M PSCC Poles as desc SSR | As per relevent standard specification | 485 | EA | 15035
6 | SWR11889 | 5.5 | Fabrication of 100 X 50mm MS Channel for formation of 11kV and 33kV bays: Fabrication and erection of M.S,Channel 100x50mm for forming of 33KV & 11 KV Bays as per standard specifications to facilitate stringing of bus, erection of LA sets, AB Switches bolts & Nuts etc. including painting with one coats of red oxide and two coats of Aluminium paint. GI bolts&nuts shall be used. | Electrical work | Fabr & Erect-MS Chnl 100x50mm for SS Bay | As per relevent standard specification | 6600 | TO | 36300
7 | SWR10404 | 40 | Erection of 33kV and 11kV Strung Bus with Panther (200Sqmm) ACSR Conductor: Erection of 33kV and 11kV Bus over the Substation structures with 200sqmm Panther ACSR conductor and giving Jumpers to connect the Switch gear by providing the suitable T clamps and round clamps suitable to Post type insulators & Insulators. | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 13107.2
8 | SWR10884 | 50 | Connectionof equipment to bus and or another equipmentwithsingle zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Electrical work | Conn. of equip/bus single zebra/panther | As per relevent standard specification | 224 | EA | 11200
9 | SWR10392 | 2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 9000
10 | SWR10393 | 9 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 28800
11 | SWR11742 | 3 | Supply & erection of 11 kV 400 A convential single(1/3) phasing AB switches.includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | S&E-400A 11KV ABSwth Conv 1ph(1/3) in SS | As per relevent standard specification | 4232 | EA | 12696
12 | SWR21240 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt). | Electrical work | Hoisting post ins&hrd wr 1panther 33kv | As per relevent standard specification | 781 | EA | 1562
13 | SWR21241 | 4 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 11kv | As per relevent standard specification | 507 | EA | 2028
14 | SWR10881 | 11 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 1562
15 | SWR23224 | 16.46 | Excavation of pit in all types of soils of size 2.2x2.2x0.85Mts.for Construction of Plinths for VCB (33KV & 11 KV ) | Earth work | Excavate-Pit for 33KV VCB | As per relevent standard specification | 331 | M3 | 5448.26
16 | SWR20685 | 22.24 | Providing of Base concreting (2.2x2.2x0.15 Mts) with 1:3:6 Concrete mix. Using form boxes, Providing of Concreting (2x2x1.0mts) with 1:3:6 Cocrete mix. Plastering of the plinth for smooth finishing with 12mm thick 1:3 cement motor and providing two coats white washing for part of the plinth above groung level. | Civil work | Cement concrete with 40MM metal VCB plin | As per relevent standard specification | 5160 | M3 | 114758.4
17 | SWR10461 | 4 | Erection of Switchgear complete for 11 kV VCB includes Assembling the VCB Structures and mounting the VCBs over the already erected foudation including wiring of Breaker Control Panel/CTs, erection of CTs and control pannel providing Jumpers. | Electrical work | Erection of 11kv VCB | As per relevent standard specification | 12000 | EA | 48000
18 | SWR10396 | 2 | Erection of 33KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 1760
19 | SWR10397 | 1 | Erection of 11 KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 11kv LA stn type incl earthing | As per relevent standard specification | 559 | SET | 559
20 | SWR10398 | 3 | Erection of 11 KV Lightening Arrestors line type complete including jumpering. | Electrical work | Erect of 11kvLA line type incl earthing | As per relevent standard specification | 505 | SET | 1515
21 | SMR11607 | 1 | Supply of 33kv HG fuse set including providing of jumpers | Electrical work | S-33KV HG Fuse Set excl Ins & Chnl | As per relevent standard specification | 6431 | SET | 6431
22 | SWR10394 | 1 | Erection of 33kv HG fuse set including providing of jumpers | Electrical work | Erect. of 33kv HG Fuseset incl earthing | As per relevent standard specification | 1331.81 | SET | 1331.81
23 | SMR11608 | 1 | Supply of 11kv HG fuse set including providing of jumpers | Electrical work | S-11KV HG Fuse Set | As per relevent standard specification | 1733.75 | SET | 1733.75
24 | SWR10395 | 1 | Erection of 11kv HG fuse set including providing of jumpers | Electrical work | Erect. of 11kv HG Fuseset incl earthing | As per relevent standard specification | 740.52 | SET | 740.52
25 | SMR11482 | 22 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 76692
26 | SWR10357 | 22 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 27152.4
27 | SWR10920 | 500 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification.75x8 mm MS flat for Earth mat and connecting to electrodes. | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 32500
28 | SWR10919 | 950 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification. 50x6 mm MS flat for raisers, double flat shall be run for structure poles raisers & equipment earthing. | Electrical work | Earthing for raisers of SS Flat 50x6 mm. | As per relevent standard specification | 41 | RMT | 38950
29 | SMR40033 | 2 | Providing of double earthing for neutral with flexible copper jumpers of adequate size including arrangement by fixing M.S.Channel 100x50mm. | Electrical work | SupCU Flexi jumper for Power T/F Neutral | As per relevent standard specification | 4725 | EA | 9450
30 | SWR11771 | 4 | Erection of 24 Volts Battery along with Charger on the VCB plinth and giving DC supply to VCB's. | Electrical work | Erect-24V Batery with Chrgr incl grot-SS | As per relevent standard specification | 1050 | EA | 4200
31 | SWR11474 | 600 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable includes excavation of earth and back filling with sand and earth in alternate layers . The cable termination shall be made by providing proper size lugs and shall be identified with colours. | Electrical work | Laying-4 core cable | As per relevent standard specification | 15 | RMT | 9000
32 | SWR10463 | 1 | Erection of 25 KVA Three phase Station Transformer on the Substation Structures and giving jumpers/connections on HT side to the 11kV bus. Belting angle shall be provided both sides of DTR for securing DTR firmly in position. | Electrical work | Erection of Three Phase DTRs | As per relevent standard specification | 1139.95 | EA | 1139.95
33 | SMR40045 | 1 | Supply of AC Panel Board includes: Fixing of 1 No.100A, MCCB, 10kA capacity of any standard make including material cost. Fixing of suitable panel box 3x3x1 with M.S.Sheet of 16 SWG with front door compartments inclusive of material cost & powder coating (with C Channel ). Fabrication of panel Fixing of 96x96mm analog voltmeter with VSS switch Fixing of 20A HRC fuse Fixing of 3 phase supply indicator kwith HRC fuses Supply and fixing of 6 Sqmm copper flexible wire (PVC) Fixing of Stud type TBs for outgoing feeder Fixing of Epoxy bus supports. | Electrical work | Supply of AC Supply panel complete | As per relevent standard specification | 42000 | EA | 42000
34 | SMR40044 | 1 | Supply of DC Panel Board Fixing of suitable panel box of size 6'x6'x1' with M S sheet of 16 SWG with back doors (4'x6') and on front side with provision to fix up bakelite hylam sheet size of 4'x6' including cost of the panel with powder coating. Fixing of best quality of angles for panel. Fixing of C Channelfor panel. Fabrication of control panel including making suitable holes and board Fixing of Stud type TBs for outgoing feeder Fixing of 24V DC pilot lamps of standard make Fixing of healthy trip push buttons with LED lamp Fixing of plain switches for alarm acceptance and for PTR signal Fixing of ON/OFF push buttons Fixing of digital volt meter for 11kV Fixing of VSS of standard make, Fixing of Engraved AL plates for Alarm panel of various VCB Laying of 2.5Sqmm copper flexible wire for internal wiring . Fixing of digital frequency meter Fixing of Copper lugs and ferrules for internal wiring. Fixing of 4" Gang bells 24V DC Fixing of flow diagram with rading strip Fixing of HRC fuse units | Electrical work | Supply of DC Anunc.relay panel 8 feeders | As per relevent standard specification | 42500 | EA | 42500
35 | SWR20025 | 1 | fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supplied by tenderer. | Electrical work | Erect-Contrl/Relay, AC, Announ. Panels | As per relevent standard specification | 7871.85 | EA | 7871.85
36 | SWR10342 | 8 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 12000
37 | SWR10956 | 8 | Fixing of Metal halide/LED lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5M GI pipe complete. | Electrical work | Fixing of LED/Metal halide complete. | As per relevent standard specification | 1268 | EA | 10144
38 | SWR20028 | 8 | Supply and Fixing of junction box and Providing with proper Fuse protection and required glauds suitable for Cable Terminations. The box shall be fixed on the pole. | Electrical work | 33/11kv S.S Yard lighting junction box | As per relevent standard specification | 351.9 | EA | 2815.2
39 | SWR20526 | 1 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply & fixing of marshall box | As per relevent standard specification | 3085.5 | EA | 3085.5
40 | SMR40088 | 1 | Supply and fixing of filled sand bucket set complete (4 Nos. Buckets) with stand to mount fire buckets. | Electrical work | Sup Fire Buckets Stand with Buckets | As per relevent standard specification | 1386 | SET | 1386
41 | SMR40087 | 2 | Supply and fixing of CO2 Cylinder set as per IS2878 Specifications. | Electrical work | Sup TrollyMounted Co2 Cylinders(IS-2878) | As per relevent standard specification | 9240 | EA | 18480
42 | SWR11895 | 1 | Supplying and fixing of feeder indicator board to each of the 3Nos feeder breakers and LV breaker, danger boards made of 1'x1' and properly mounted on the structures. The letters written on the borad shall be 1.5"size with blue colour and background shall be of white colour | Electrical work | S&F-33/11KV SS Feeder Indicator Board | As per relevent standard specification | 551 | SET | 551
43 | SWR20032 | 1 | Supply and fixing of wooden board of size 3'x2'.5'indicating the layout of the Switch yard. | Electrical work | Sup &fix of board ind Switchyard layout | As per relevent standard specification | 1654 | EA | 1654
44 | SMR40086 | 1 | Supply and Erection of Permanent Name Board of on 3'x4' steel sheetmounted on steel frame as described in Specification. | Electrical work | Sup 33/11kv S.S Permanent name board | As per relevent standard specification | 10238 | EA | 10238
45 | SMR40076 | 1 | Supply of Digital clamp meter. | Electrical work | Supply of Digital clamp meter. | As per relevent standard specification | 2888 | EA | 2888
46 | SMR40064 | 1 | Supply of Rechargeable LED torch light of Standard make. | Electrical work | Sup Rechargeable LED torch light. | As per relevent standard specification | 1733 | EA | 1733
47 | SMR40063 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box containing ‘D’Spanners from size 6 to 54, Hammer small and big size, Ring spanners from 6 to 28, Adjustable spanner, Pipe wrench, Cutting Plier, Nose plier, Tester, insulated Screw drive. | Electrical work | SupTaparia Tool kit complete as per Spec | As per relevent standard specification | 4925 | SET | 4925
48 | SWR22090 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Electrical work | Sup& fix safety inst/SS Op. inst board | As per relevent standard specification | 2205 | EA | 2205
49 | SMR11598 | 8 | Supply of 25 W LED lamp with fitting of philips make | Electrical work | S-25W LED fixture set | As per relevent standard specification | 3200 | EA | 25600
50 | SMR12378 | 1 | Supply of Alluminum Ladder(20 feet) | Electrical work | S-10ft Aluminium Ladder | As per relevent standard specification | 1654 | EA | 1654
51 | SMR40075 | 1 | Supply of Megger (2000 ohms, 0-2.5kv) | Electrical work | Supply of Earth megger (1000v) | As per relevent standard specification | 8085 | EA | 8085
52 | SMR40067 | 2 | Supply of Hand Gloves | Electrical work | Supply of Hand Gloves | As per relevent standard specification | 289 | SET | 578
53 | SMR40071 | 2 | Supply of Safety Helmets of standard make | Electrical work | Supply of Safety Helmet of standard make | As per relevent standard specification | 231 | EA | 462
54 | SMR11599 | 4 | Supply of Earth Discharging Rod 10' length. | Electrical work | S-Earth Rod 8ft Long 3mm Thick | As per relevent standard specification | 1000 | EA | 4000
55 | SMR11488 | 200 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 23500
56 | SMR11591 | 66 | Supply of PG clamps for panther 2 bolted 800 A. | Electrical work | S-Al. alloy three bolted PG clamps 800A | As per relevent standard specification | 130 | EA | 8580
57 | SWR20029 | 300 | Supply and Laying of 2 core/4 core cable includes excavation earth and back filling with sand and earth in alternate layers as shown in the sketch. The cable termination shall be made by providing proper size of lugs at both ends of the cable termination. | Electrical work | 33/11kv S.S laying of 2/4core for light | As per relevent standard specification | 50 | M | 15000
58 | SWR20308 | 31 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 12625.99
59 | SWR20307 | 8 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 2172.16
60 | SWR11860 | 2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 5440.68
61 | SWR10150 | 10.5 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 6479.55
62 | SWR10206 | 10.5 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 2320.5
63 | SWR10524 | 10.5 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 1942.5
64 | SWR11220 | 350 | Loading and unwinding of Panther conductor. | Electrical work | Load-Unwinding Panther conductor | As per relevent standard specification | 3 | M | 1050
65 | SWR11221 | 350 | Unloading of Panther conductor. | Electrical work | Unload-Unwinding Panther conductor | As per relevent standard specification | 2 | M | 700
66 | SWR12416 | 2 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 4
67 | SWR10631 | 2 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 4
68 | SWR10618 | 2 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 130
69 | SWR10632 | 2 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 130
70 | SWR10212 | 2 | Loading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | LOADING of 11kv Pin/Post/Solid Core Insu | As per relevent standard specification | 1 | CRT | 2
71 | SWR10530 | 2 | Unloading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | UNLOADING of 11kv Pin/Post/Solid Core In | As per relevent standard specification | 1 | CRT | 2
72 | SWR11701 | 600 | Loading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | Load-PVC Control Cable 10C | As per relevent standard specification | 1 | M | 600
73 | SWR11712 | 600 | Unloading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | UnLoad-PVC Control Cable 10C | As per relevent standard specification | 1.02 | M | 612
74 | SWR11691 | 1 | Loading of 3Ph 25KVA Distribution Transformer. | Electrical work | Load-3Ph 25KVA DTR | As per relevent standard specification | 252 | EA | 252
75 | SWR11692 | 1 | UnLoading of 3Ph 25KVA Distribution Transformer. | Electrical work | UnLoad-3Ph 25KVA DTR | As per relevent standard specification | 202 | EA | 202
76 | SWR10200 | 1 | Loading of 33/11 KV Current Transformers/ Potential Transformers. | Electrical work | LOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 165 | EA | 165
77 | SWR10266 | 6 | Loading of 33 KV10 KA LAs Station type. | Electrical work | LOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 41 | EA | 246
78 | SWR10584 | 6 | Unloading of 33 KV10 KA LAs Station type. | Electrical work | UNLOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 35 | EA | 210
79 | SWR10265 | 9 | Loading of 11 KV10 KA LAs Line type. | Electrical work | LOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 288
80 | SWR10583 | 9 | Unloading of 11 KV10 KA LAs Line type. | Electrical work | UNLOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 288
81 | SWR10264 | 3 | Loading of 11 KV10 KA LAs Station type. | Electrical work | LOADING of 11 KV,10 KA LAs Station type | As per relevent standard specification | 32 | EA | 96
82 | SWR10582 | 3 | Unloading of 11 KV10 KA LAs Station type. | Electrical work | UNLOADING of 11 KV,10 KA LAs Station typ | As per relevent standard specification | 32 | EA | 96
83 | SWR10239 | 2 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 252
84 | SWR10557 | 2 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 158
85 | SWR10238 | 9 | loading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 720
86 | SWR10556 | 9 | Unloading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 720
87 | SWR11224 | 4 | Loading and Unloading of 12V/24V Battery Set. | Electrical work | Load/Unload-12V/24V Battery Set | As per relevent standard specification | 23 | EA | 92
88 | SWR10356 | 2.66 | ERECTION OF S.S. STRUCTURE: Providing of base concreting of size 0.76x0.76x0.15M with CC mix of ratio 1:3:6 Using form boxes(0.087Cu.Mt)x31 with 20mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 17500.14
89 | SWR10402 | 1 | Erection of 11kv Potential Transformer sets complete including jumpering. The LV side of the PT shall be provided with proper fuse protection mounted in separate marshalling boxwith proper size cable glands etc. The box shall be mounted on the Substation structure. | Electrical work | Erection of 11kv three phase PT s | As per relevent standard specification | 800 | SET | 800
90 | SWR10518 | 1 | Unloading of 33/11 KV Current Transformers/ Potential Transformers | Electrical work | UNLOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 128 | EA | 128
91 | SWR10674 | 1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
92 | SWR10356 | 4.32 | Concreting the location after erection of 8.0 Mtrs pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) ( 0.6x0.6x1.5)mtrs x 8 . | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 28421.28
93 | SWR21750 | 2 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply and fixing of PT Marshalling box | As per relevent standard specification | 1139.85 | EA | 2279.7
94 | SMR25233 | 31 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 96391.71
95 | SMR22745 | 5500 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 315975
96 | SMR12321 | 2350 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 132587
97 | SMR12322 | 2280 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 128820
98 | SMR25232 | 8 | Supply of 8.0Mtr PSCC 140 Kg Pole | Electrical work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 12640
99 | SMR12315 | 2 | Supply of 33KV 800A DB Break AB Switch | Electrical work | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 81317.56
100 | SMR12316 | 2 | Supply of 11KV 800A DB Break AB Switch | Electrical work | S-11KV 800A DB Break AB Switch | As per relevent standard specification | 30847.46 | EA | 61694.92
101 | SMR12317 | 7 | Supply of 11KV 400A DB Break AB Switch | Electrical work | S-11KV 400A DB Break AB Switch | As per relevent standard specification | 18150 | EA | 127050
102 | SMR25200 | 1 | Supply of LT Distribution Box (SMC) | Electrical work | S-LT Distribution Box (SMC) | As per relevent standard specification | 7797 | EA | 7797
103 | SWR10674 | 1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
104 | SMR40009 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for First coat of 1st GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 11995.5
105 | SWR10877 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 1st coat of Aluminium | Electrical work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 4680.5
106 | SMR40010 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for second coat of 2nd GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 7111.5
107 | SWR10879 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 2nd coat of Aluminium | Electrical work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 2651
108 | SWR22092 | 3.32 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 2539.8
109 | SWR10107 | 45 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 31500
110 | SWR10112 | 16 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | As per relevent standard specification | 1680 | EA | 26880
111 | SWR10105 | 18 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 10800
112 | SWR10978 | 61 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 254082.08
113 | SWR10343 | 18 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | Erec of 9.1 Mts PSCC poles for stuts | As per relevent standard specification | 2400 | EA | 43200
114 | SWR10981 | 11 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Horizontal Cut point for 33 KV line | As per relevent standard specification | 1759.5 | EA | 19354.5
115 | SWR10356 | 27.482 | Concreting the location after erection of 11 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.76X0.76X1.83 Mts)* 18 = 19.026 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 180804.078
116 | SWR10366 | 3.32 | Paving of the 100 sqmm AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 12600.06 | KM | 41832.1992
117 | SMR11488 | 61 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 7167.5
118 | SWR11180 | 61 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 26350.17
119 | SWR20308 | 18 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 7331.22
120 | SWR10191 | 2 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 404
121 | SWR10509 | 2 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 200
122 | SWR11860 | 2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 5440.68
123 | SWR10150 | 1.08 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 666.468
124 | SWR10206 | 1.08 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 238.68
125 | SWR10524 | 1.08 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 199.8
126 | SWR10211 | 22 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 66
127 | SWR10529 | 22 | Unloading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 66
128 | SWR12416 | 7 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 14
129 | SWR10631 | 7 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 14
130 | SWR10618 | 3 | Loading of 33KV Metal parts bag of 25 nos | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 195
131 | SWR10632 | 3 | Unloading of 33 KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 195
132 | SWR10319 | 88 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 75 x 8 mm MS Flat | Electrical work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31 | EA | 2728
133 | SWR10322 | 72 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 75 x 8 mm MS Flat | Electrical work | Fab Stay clamps with 75x8 mm MM Flat | As per relevent standard specification | 42 | EA | 3024
134 | SWR10378 | 61 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevent standard specification | 32 | EA | 1952
135 | SWR10354 | 9 | Erection of 33 kv Stay set complete including fixing of bow ,fixing and binding of Eye bolt, Anchor rod, guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. | Electrical work | Assembly and erection of Stay set 33kv | As per relevent standard specification | 684.53 | SET | 6160.77
136 | SWR21190 | 9 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock,Hard rock Requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 4680
137 | SMR25236 | 61 | Supply of 11Mtr PSCC 365 Kg Pole | Electrical work | S-PSCC Pole 11Mtr 365 Kg | As per relevent standard specification | 5399 | EA | 329339
138 | SMR25233 | 18 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 55969.38
139 | SMR25229 | 52 | Supply of 33KV V-Cross Arm without Clamps | Electrical work | S-33KV V-Cross Arm without Clamps | As per relevent standard specification | 1678 | EA | 87256
140 | SMR25207 | 250 | Supply of MS Angle 65X65X6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 14312.5
141 | SMR22745 | 370 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 21256.5
142 | SMR12321 | 460 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 25953.2
143 | SMR25231 | 9 | Supply of 33KV MS Stay Set with BasePlate | Electrical work | S-33KV MS Stay Set with BasePlate | As per relevent standard specification | 1035 | SET | 9315
144 | SWR22092 | 6.14 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 11 kv line. | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 4697.1
145 | SWR10107 | 4 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 2800
146 | SWR10110 | 40 | Excavation of Pole pits of size (2.6" x 2.6" x 5.0') 0.88 cum 0.76 M x 0.76M x 1.52M for 9.1 mtrs PSCC Poles including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD(2.6" x 2.6" x 5.0") | As per relevent standard specification | 1440 | EA | 57600
147 | SWR10105 | 160 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 96000
148 | SWR10978 | 4 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 16661.12
149 | SWR10343 | 160 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 384000
150 | SWR10342 | 40 | Erection of 8.0 Mts PSCC Poles including fixing of 11 KV X arm and top cleats and fixing of Pin insulators complete with necessary hard ware for tangential locations excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 60000
151 | SWR10653 | 27 | Formation of 11 kv cut points (Vertical/Horizantal) including fixing of 11 KV Cross arms,clamps, strain insulators sets complete with hardware and stays (Bows and Eye-bolts), Excluding the cost of pit Excavation and pole erection. The contractor has to supply GI Bolts and Nuts. | Electrical work | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1350 | EA | 36450
152 | SWR10356 | 38.788 | Concreting the location after erection of 11/9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.76X0.76X1.83 Mts)* 35 = 36.995 Cu.Mt & (0.76X0.76X1.52 Mts)*6 = 5.262 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 255186.252
153 | SWR10365 | 6.14 | Paving of the conductor 55 Sqmm Single Circuit (3 Conductors) AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 3 Cond | As per relevent standard specification | 8500 | KM | 52190
154 | SMR11488 | 160 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 18800
155 | SWR10206 | 1.6 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 353.6
156 | SWR10524 | 1.6 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 296
157 | SWR10134 | 1.6 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 940.032
158 | SWR11248 | 459 | Loading 11KV Polymer Pin Insulator with GI pins | Electrical work | Load-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 459
159 | SWR11249 | 459 | Unloading 11KV Polymer Pin Insulator with GI pins | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 459
160 | SWR11862 | 3 | Transport of VCB , Control pannels, current transformater, bosster etc, above 20 KM and upto 30 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 11074.14
161 | SWR10191 | 3 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 606
162 | SWR10509 | 3 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 300
163 | SWR11180 | 4 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 1727.88
164 | SWR20308 | 160 | Sub Transportation of 9.1M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 65166.4
165 | SWR20307 | 40 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 10860.8
166 | SWR10228 | 129 | Loading of 11 KV V - Cross arms | Electrical work | LOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 516
167 | SWR10546 | 129 | Unloading of 11 KV V - Cross arms | Electrical work | UNLOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 516
168 | SWR12402 | 7 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 336
169 | SWR12421 | 7 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 336
170 | SWR10251 | 129 | Loading of 11 KV Top fittings | Electrical work | LOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 129
171 | SWR10569 | 129 | Unloading of 11 KV Top fittings | Electrical work | UNLOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 129
172 | SWR12416 | 9 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 18
173 | SWR10631 | 9 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 18
174 | SWR10353 | 24 | Erection of 11 kv Stay set complete including fixing of bow, fixing and binding of Eye bolt,Anchor rod,guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Assembly and erection of Stay set11kv&LT | As per relevent standard specification | 606.85 | SET | 14564.4
175 | SWR21190 | 24 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In Hard Gravel and Hard murram not requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 12480
176 | SWR10319 | 8 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 75 x 8 mm MS Flat | Electrical work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31 | EA | 248
177 | SWR10322 | 32 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 75 x 8 mm MS Flat | Electrical work | Fab Stay clamps with 75x8 mm MM Flat | As per relevent standard specification | 42 | EA | 1344
178 | SWR10320 | 172 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 50 x 6 mm MS Flat | Electrical work | Fab Back clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 15 | EA | 2580
179 | SWR10323 | 160 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 50 x 6 mm MS Flat | Electrical work | Fab Stay clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 25 | EA | 4000
180 | SWR10378 | 156 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevent standard specification | 32 | EA | 4992
181 | SMR25236 | 4 | Supply of 11Mtr PSCC 365 Kg Pole | Electrical work | S-PSCC Pole 11Mtr 365 Kg | As per relevent standard specification | 5399 | EA | 21596
182 | SMR25233 | 160 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 497505.6
183 | SMR25232 | 40 | Supply of 8.0Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 63200
184 | SMR25218 | 129 | Supply of 11KV V X-Arms with MS Angle 65x65x6 | Electrical work | S-11KV V X-Arms with MS Angle 65x65x6 | As per relevent standard specification | 743 | EA | 95847
185 | SMR25205 | 550 | Supply of MS Channel 75x40mm | Electrical work | S-MS Channel 75x40 mm | As per relevent standard specification | 58.45 | KG | 32147.5
186 | SMR25206 | 440 | Supply of MS Angle 50x50x6 | Electrical work | S-MS Angle 50x50x6 | As per relevent standard specification | 58.15 | KG | 25586
187 | SMR12321 | 110 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 6206.2
188 | SMR12322 | 500 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 28250
189 | SMR25214 | 24 | Supply of LT/11KV MS Stay Sets with Base Plate | Electrical work | S-LT/11KV MS Stay Sets with Base Plate | As per relevent standard specification | 1168 | SET | 28032
190 | SWR10392 | 1 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 4500
191 | SWR10107 | 2 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 1400
192 | swr10978 | 2 | Erection of 11 M long PSCC pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 8330.56
193 | SWR10343 | 4 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 9600
194 | SWR10356 | 4.27 | Concreting the location after erection of 9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes(0.6X0.6X1.5 Mts)*4 = 2.16 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 28092.33
195 | SMR11488 | 5 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 587.5
196 | SWR10206 | 0.34 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 75.14
197 | SWR10524 | 0.34 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 62.9
198 | SWR10134 | 0.34 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 199.7568
199 | SWR11180 | 2 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 863.94
200 | SWR20308 | 4 | Sub Transportation of 9.1M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 1629.16
201 | SWR12402 | 1 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 48
202 | SWR12421 | 1 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 48
203 | SWR12416 | 1 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 2
204 | SWR10631 | 1 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 2
205 | SMR11482 | 2 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 6972
206 | SWR10357 | 2 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 2468.4
207 | SWR34671 | 2 | Providing of collar rings of 450mm dia at 4 pole structure | Electrical work | Collar/ Rings of 450mm dia | As per relevent standard specification | 250 | EA | 500
208 | SMR11485 | 30 | Supply of earthing GI Flat 25X3 mm including material | Electrical work | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 3150
209 | SWR10239 | 1 | Loading of 33 KV AB Switch Conventional 400/800 Amp | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 126
210 | SWR10557 | 1 | Unloading of 33 KV AB Switch Conventional 400/800 Amp | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 79
211 | SMR12315 | 1 | Supply of 33KV 800A DB Break AB Switch | Electrical work | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 40658.78
212 | SMR25236 | 2 | Supply of 11Mtr PSCC 365 Kg Pole | Electrical work | S-PSCC Pole 11Mtr 365 Kg | As per relevent standard specification | 5399 | EA | 10798
213 | SMR25233 | 4 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 12437.64
214 | SMR25207 | 60 | Supply of MS Angle 65X65X6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 3435
215 | SMR22745 | 240 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 13788
216 | SMR12321 | 36 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 2031.12
217 | SWR10393 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 9600
218 | SMR11488 | 6 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 705
219 | SWR10206 | 0.26 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 57.46
220 | SWR10524 | 0.26 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 48.1
221 | SWR10134 | 0.26 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 152.7552
222 | SMR11484 | 3 | Supply of C I earth pipe of size 50mm dia, 2 mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 50mm dia 2m long | As per relevent standard specification | 2441 | EA | 7323
223 | SWR11222 | 6 | Loading/Unloading of C I earth pipe of size 80/50mm dia, 2 mtrs long for earth electrode | Electrical work | Load/Unload-CI pipe 80/50 mm dia 2mt L | As per relevent standard specification | 18 | EA | 108
224 | SWR34671 | 3 | Providing of collar rings of 450mm dia at 4 pole structure | Electrical work | Collar/ Rings of 450mm dia | As per relevent standard specification | 250 | EA | 750
225 | SMR11485 | 30 | Supply of earthing GI Flat 25X3 mm including material | Electrical work | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 3150
226 | SWR10238 | 3 | Loading of 11 KV AB Switch Conventional 200/400 Amp | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 240
227 | SWR10556 | 3 | Unloading of 11 KV AB Switch Conventional 200/400 Amp | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 240
228 | SMR12317 | 3 | Supply of 11KV 400A DB Break AB Switch | Electrical work | S-11KV 400A DB Break AB Switch | As per relevent standard specification | 18150 | EA | 54450
229 | SMR25206 | 36 | Supply of MS Angle 50x50x6 | Electrical work | S-MS Angle 50x50x6 | As per relevent standard specification | 58.15 | KG | 2093.4
230 | SMR25205 | 120 | Supply of MS Channel 75x40 mm | Electrical work | S-MS Channel 75x40 mm | As per relevent standard specification | 58.45 | KG | 7014
231 | SMR12322 | 50 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 2825
[6 empty] | Total |  |  | 5505968.1542
1 | SWR34179 | 12 | Cutting and Levelling the site with the help of JCB including cost,conveyance of all materials,hire charges etc complete for finished item of work. | JCB | NA | As per relevant standard specification | 2164.1 | H | 25969.2
2 | SWR33015 | 105.22 | Earth Work Mass Excavation (Ordinary rock not requiring blasting) to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions, labour and material charges etc., complete as directed by the engineer-incharge. | Earth Work | NA | As per relevant standard specification | 347 | M3 | 36511.34
3 | SWR33028 | 20.97 | PCC (1:4:8) for levelling course using 40mm size hard broken Granite stone including cost and conveyance of all materials, HBG metal for foundations and leveling course and as directed by the Engineer- in - charge etc complete for finished item of work. | PCC | NA | As per relevant standard specification | 4064 | M3 | 85222.08
4 | SWR33041 | 128.92 | CRS masonry in CM (1:6) using Hard Granite Stones including cost and conveyance of all materials, seignorage charges, labour charge for construction and for dressing stones to required size and shape, dewatering,scaffolding,cutting for all leads and lifts, all incidental charges etc .complete for finished item of work as directed by the Engineer - in - charge. | Masonry | NA | As per relevant standard specification | 4437 | M3 | 572018.04
5 | SWR33068 | 20.6 | Construction of brick masonary in CM(1:6) including cost and conveyance of all materials, labour charges etc. complete for finished item of work | Masonry | NA | As per relevant standard specification | 7624 | M3 | 157054.4
6 | SWR33052 | 3912.82 | Supplying and filling with borrowed gravel, watering, ramming, consolidating thoroughly complying with the standard specification including cost and conveyance of all materials, labour charges, hire charges of machinery, with all leads and incidental charges etc complete for finished item work | Gravel | NA | As per relevant standard specification | 435 | M3 | 1702076.7
7 | SWR33098 | 6.53 | RCC M20 GRADE Nominal Mix (a) Footings | RCC | NA | As per relevant standard specification | 8227 | M3 | 53722.31
8 | SWR33100 | 4.68 | RCC M20 GRADE Nominal Mix (b) Columns | RCC | NA | As per relevant standard specification | 10922 | M3 | 51114.96
9 | SWR33099 | 1.61 | RCC M20 GRADE Nominal Mix (c) Plinth Beams | RCC | NA | As per relevant standard specification | 10647 | M3 | 17141.67
10 | SWR33107 | 0.55 | RCC M20 GRADE Nominal Mix (d) Lintels | RCC | NA | As per relevant standard specification | 11082 | M3 | 6095.1
11 | SWR33114 | 11.7 | RCC M20 GRADE Nominal Mix (e) Sunshade | RCC | NA | As per relevant standard specification | 1162 | M2 | 13595.4
12 | SWR33121 | 2.35 | RCC M20 GRADE Nominal Mix (f) Roof Beams | RCC | NA | As per relevant standard specification | 10657 | M3 | 25043.95
13 | SWR33128 | 6.94 | RCC M20 GRADE Nominal Mix (g) Slab | RCC | NA | As per relevant standard specification | 10208 | M3 | 70843.52
14 | SWR33144 | 2.3 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) / Mild steel (MS) steel bars (Fe 415/ Fe 500 grade as per IS 1786-1979) of different diameters for RCC works complete for finished item of work in all floors.( APSS No.126) | Steel | NA | As per relevant standard specification | 75077 | TO | 172677.1
15 | SWR33163 | 353.86 | Providing plastering of 20mm thick to all uneven faces of walls and ceiling of superstructure in two coats with base coat in CM 1:6 of 16mm thick and top coat in Cm 1:4 4mm thick with dubara sponge finish | Plastering | NA | As per relevant standard specification | 410 | M2 | 145082.6
16 | SWR33184 | 155.64 | Raised pointing in CM(1:3) including curing, cost and conveyance of all materials and labour charges for complete item of work. | Plastering | NA | As per relevant standard specification | 94 | M2 | 14630.16
17 | SWR33156 | 54.87 | Providing impervious coat over RCC roof slab surfaces to requried slopes with 20mm thick in CM 1:3 pro mixed with approvaled brand of water proffing compound as the raet of 1 kg per bag of cement inclding cost and conveyance of all materials | Plastering | NA | As per relevant standard specification | 440 | M2 | 24142.8
18 | SWR33264 | 5.7 | Supply and fixing of Flush type Doors with 35mm Thick Flush Shutters with Bondwood solied Block Board Type Faced on Both the sides with Commercial Type Plywood for finished item work as directed by the Engineer - in- charge. | Doors | NA | As per relevant standard specification | 6799 | M2 | 38754.3
19 | SWR33278 | 5.76 | Supply and Fixing of Aluminium sliding windows with fixed glass panels using aluminium sections 62x32x1.2mm providing 5mm plain glass fixed to frame with beading gasket and glazing clips with all accessories,locking arrangements including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Windows | NA | As per relevant standard specification | 3535.64 | M2 | 20365.2864
20 | SWR33310 | 6.25 | Supplying and fixing of MS safety grill with peripheral frame of ISA 25x25x4mm and horizontal & vertical 8mm square rods and including cost and coveyance of all mateirals with all leads and lifts, labour charges, painting charges complete for finished item of work | Windows | NA | As per relevant standard specification | 2539 | M2 | 15868.75
21 | SWR33219 | 29 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and approved size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and pointing with cement, labour etc, complete for finished item of work. | Flooring | NA | As per relevant standard specification | 659 | M2 | 19111
22 | SWR33236 | 10.67 | Providing skirting with tandoor blue slabs including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Flooring | NA | As per relevant standard specification | 726 | M2 | 7746.42
23 | SWR33029 | 34.11 | Plain Cement contrete - Nominal Mix (1:3:6) using 40 mm metal with concrete mixture including cost and conveyance of all materials labour charges etc. complete for finished iitem of work and as directed by the engineer-in-charge. | PCC | NA | As per relevant standard specification | 4371 | M3 | 149094.81
24 | SWR33030 | 14.73 | PCC(1:2:4) using 10 to 12 mm aggregate including cost and conveyance of all materials labour charges etc., complete for finished iitem of work and as directed by the engineer-in-charge. | PCC | NA | As per relevant standard specification | 5504 | M3 | 81073.92
25 | SWR33057 | 49.44 | Supply and Spreading of 20mm machine crushed metal including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | HBG metal | NA | As per relevant standard specification | 1514 | M3 | 74852.16
26 | SWR33403 | 110 | Supply and fixing of fencing of welded wire mesh (2"x2") of 3mm dia with support channels of 75x 40mm and angles around of 30x30x3 mm including cost and conveyance of all materials, fabrication charges, painting charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Welded mesh | NA | As per relevant standard specification | 2042 | M2 | 224620
27 | SWR33333 | 73.7 | Painting with two coats of OBD over a coat of primer including cost and conveyance of all materials ,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Paint | NA | As per relevant standard specification | 109.9 | M2 | 8099.63
28 | SWR33336 | 177.8 | Painting with two coats of ACE paint over a coat of primer including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Paint | NA | As per relevant standard specification | 195.91 | M2 | 34832.798
29 | SWR33329 | 194.6 | Painting with lovely cem three coats including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Paint | NA | As per relevant standard specification | 70.47 | M2 | 13713.462
30 | SWR33404 | 10.07 | Supply and fixing of MS gates of approved design including cost and conveyance of all materials,fabrication charges etc complete for finished item of work. | Gate | NA | As per relevant standard specification | 4579.89 | M2 | 46119.4923
31 | SWR33442 | 30 | S&F Conceal PVC Pipe 32mm dia in Slab | Electrification | NA | As per relevant standard specification | 85 | RMT | 2550
32 | SWR33440 | 20 | S&F Conceal PVC Pipe 20mm dia in Wall | Electrification | NA | As per relevant standard specification | 89 | RMT | 1780
33 | SWR33457 | 15 | Wiring with 2X1.0 Sqm(14/.3mm) PVC insulated flexiable copper cable in the existing metalic/Non metalic conduit pipe with 6A mini modular SP switch, mounted on metalic box covereds with appropriate front plate modules etc ceiling rose including cot and conveyance of all mateials, labour charges complete for light points, bell points and fan points in non residential builsing except circuit moving finished in all types masonary as directed by department. | Electrification | NA | As per relevant standard specification | 580 | EA | 8700
34 | SWR33461 | 2 | Supply and fixing of 6A 3/2 pin flush type plug socket with 6A flush type marked switch control on a common board with earth continuity including wire leads earth connections along with all labour charges etc. complete | Electrification | NA | As per relevant standard specification | 469 | EA | 938
35 | SWR33464 | 2 | Supply and fixing of 16A 3pin flush type plug socket and 16A flush type fuse unit and 16A switch control. | Electrification | NA | As per relevant standard specification | 437 | EA | 874
36 | SWR33484 | 4 | Supply and fixing of slanting holders with 100W bulb with all connections and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | NA | As per relevant standard specification | 116 | EA | 464
37 | SWR33545 | 3 | Supply and fixing of patty type tube light fitting with 4' 0" - 40W tube light,40W copper choke,starter,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | NA | As per relevant standard specification | 868 | EA | 2604
38 | SWR33494 | 90 | Supply and run of 2 of 14/.3mm(1.00Sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | NA | As per relevant standard specification | 48 | RMT | 4320
39 | SWR33497 | 30 | Supply and run of 2 of 36/0.3 (2.5sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | NA | As per relevant standard specification | 95 | RMT | 2850
40 | SWR33520 | 1 | SPN Distribution board with IP-20 protection suitable for single phase 40A DP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 4Nos as out going MCBs in sheet steel enclosure including connections and cost of all material labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | NA | As per relevant standard specification | 5038 | EA | 5038
41 | SWR33596 | 1 | Providing independent earthing for main switches,IC cutouts and motors using 40mm. Dia. B-class G.I.Pipe of 2.5' length duly providing 12mm. Dia. 6No. Holes and required bolts,nuts and washers,including filling with equal preparation of salt and charcoal in layers and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | NA | As per relevant standard specification | 4891 | EA | 4891
42 | SWR33597 | 15 | Supply and run of No.8 SWG Copper wire including cost of all accessories and labour charges etc., Complete | Electrification | NA | As per relevant standard specification | 140 | RMT | 2100
43 | SWR33563 | 2 | Supply and Fixing of 48" ceiling fan of bajaj make(or equivalent make) including cost material,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Flooring | NA | As per relevant standard specification | 2215 | EA | 4430
44 | SWR33224 | 13.7 | Supply and fixing of ceramic tiles fantacy for dadoing including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 734 | M2 | 10055.8
45 | SWR34311 | 1 | Supply and fixing of 580mm x 440mm long Orissa pan of Parry, Neycer or Hindhusthan, make with 'P' or 'S' trap etc complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 2178 | EA | 2178
46 | SWR34386 | 2 | Supply and Fixing 4" PVC floor trap including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 269 | EA | 538
47 | SWR34382 | 2 | Supply,fixing 90mm dia. PVC Plain Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 84 | EA | 168
48 | SWR34385 | 2 | Supply,fixing 90mm dia. PVC Door Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 81 | EA | 162
49 | SWR34286 | 1 | S&Fixing 150mm x 100mm SWG gully traps Ist class grating & const. brick masonry in CM (1:6) prop inter mediate chamber and fitted with CI frame etc complete. | Plumbing | NA | As per relevant standard specification | 749 | EA | 749
50 | SWR34377 | 6 | Supply and Fixing 4" dia 3M Single socket PVC pipe including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 422 | RMT | 2532
51 | SWR34453 | 1 | Supply and Fixing 4" dia PVC cowl including labour charges etc. complete for finished item of work. | Plumbing | NA | As per relevant standard specification | 23 | EA | 23
52 | SWR34444 | 1 | Construction of soak pit with 4' dia RCM rings upto a depth of 6' including cost and conveyance of all materials as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 2950 | EA | 2950
53 | SWR34362 | 150 | CPVC Pipes and Fittings b) 22.20mm OD Pipe - SDR 11 | Plumbing | NA | As per relevant standard specification | 313 | RMT | 46950
54 | SWR34363 | 100 | CPVC Pipes and Fittings c) 28.60mm OD Pipe - SDR 11 | Plumbing | NA | As per relevant standard specification | 410 | RMT | 41000
55 | SWR34344 | 24 | Supply and fixing of 15mm dia. SS coated taps including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 230 | EA | 5520
56 | SWR34345 | 1 | Supply and fixing of 20mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 331 | EA | 331
57 | SWR34346 | 2 | Supply and fixing of 25mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 466 | EA | 932
58 | SWR34329 | 4 | Supply and fixing of 12.7mm bib tap Indian make including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 271 | EA | 1084
59 | SWR34375 | 1000 | Providing and placing on Terrace polyetheylene water storage tank with double layer approved brand and manufacture with cover complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 10 | L | 10000
60 | SWR33744 | 1 | Supply of steel table of size 4'x2.5'x30" with 18 mm plywood fixed with rubber beeding with drawers on right side with automatic locking arrangements etc complete for finished item of work and as directed by the engineer-in-charge. | Furniture | NA | As per relevant standard specification | 8190 | EA | 8190
61 | SWR33857 | 1 | Supply of 'S' type chair with arms teakwood frame with seat back 's' type on G.I pipe including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Furniture | NA | As per relevant standard specification | 3850 | EA | 3850
62 | SWR33858 | 2 | Supply of P V C chairs of Neelkamal of approved quality & make including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Furniture | NA | As per relevant standard specification | 1150 | EA | 2300
63 | SWR34656 | 759 | S-LDPE Sheet 500Micron | Board | NA | As per relevant standard specification | 95 | M2 | 72105
64 | SWR33054 | 71.42 | S&Filling with Borrowed Stone Dust | LDPE sheet | NA | As per relevant standard specification | 1000 | M3 | 71420
65 | SWR33415 | 7.3 | Manufacture, supply ,laying and fixing of 450mm dia. NP3 class R.C.C. socket and spigot pipes (rate per meter of effective length) including transportaion ,taxes and duties etc. complete for finished item of work and as directed by the Engineer-in-charge. | Stone Dust | NA | As per relevant standard specification | 1344 | M | 9811.2
66 | SWR33425 | 1 | Prov supply of electricity to the site | Hume pipe | NA | As per relevant standard specification | 5677.88 | EA | 5677.88
67 | SWR33608 | 1 | Geophysical Investgation Charges | Fencing poles | NA | As per relevant standard specification | 5000 | EA | 5000
68 | SWR33609 | 90 | Drilling-165mm Bore Well 0 to 90M | Fencing poles | NA | As per relevant standard specification | 336 | RMT | 30240
69 | SWR34830 | 30 | Drilling-165mm Bore Well 90 to 120M | Barbed wire | NA | As per relevant standard specification | 369 | RMT | 11070
70 | SWR34831 | 30 | Drilling-165mm Bore Well 120 to 150M | Power Supply | NA | As per relevant standard specification | 369 | RMT | 11070
71 | SWR33611 | 30 | S&F 160mm dia PVC Casing | Borewell | NA | As per relevant standard specification | 844 | RMT | 25320
72 | SWR33636 | 1 | S&E SP SubMrsbl Pumpset 2.0HP 30 Stages | Borewell | NA | As per relevant standard specification | 34237 | EA | 34237
73 | SWR33641 | 60 | S&R 3C 2.5sqmm Flat Copper Cable | Borewell | NA | As per relevant standard specification | 190 | RMT | 11400
74 | SWR33644 | 1 | S&E D.O.L Starter 250V Single Phase | Borewell | NA | As per relevant standard specification | 1040 | EA | 1040
75 | SWR34203 | 1 | Supply & fixing of Flange Clamps | Borewell | NA | As per relevant standard specification | 182 | EA | 182
76 | SWR34410 | 178 | S&F HDPE Pipe 40mm dia 6kg/sqcm | Borewell | NA | As per relevant standard specification | 160 | RMT | 28480
77 | SWR33422 | 2.5 | S&F Glow Sign Board | Borewell | NA | As per relevant standard specification | 3730.36 | M2 | 9325.9
78 | SWR33405 | 40 | S&F RCC Fencing Pole 0.1mx0.1mx1.8m | Borewell | NA | As per relevant standard specification | 1293.04 | EA | 51721.6
79 | SWR33406 | 120 | S&F RCC Fencing Pole 0.115mx0.115mx2.7m | Borewell | NA | As per relevant standard specification | 1433.9 | EA | 172068
80 | SWR33407 | 265 | S&F Barbed Wire 8H & 2Cross | Seignorages | NA | As per relevant standard specification | 260.05 | RMT | 68913.25
81 | SWR33421 | 1.5 | S&F MS Board | Seignorages | NA | As per relevant standard specification | 4542.3 | M2 | 6813.45
82 | #REF! | 80.0076 | Seigniorage Charges - Sand | Seignorages | NA | As per relevant standard specification | 40 | M3 | 3200.3058
83 | #REF! | 169.1657 | Seigniorage Charges - Metal | Seignorages | NA | As per relevant standard specification | 97.5 | M3 | 16493.6548
84 | #REF! | 3912.82 | Seigniorage Charges - Gravel | Seignorages | NA | As per relevant standard specification | 30 | M3 | 117384.6
[7 empty] | Civil total |  | 4851218.9992
[6 empty] | Electrical & civil total |  |  | 10357187.1534

## 12. Peddapur SS
Peddapur SS Schedules(WBS No: S-1384-90-06-01-01-001)
Name of the work: Estimate for erection of new 33/11 KV SS with connected 33 KV and 11 KV lines at Peddapur (Vg) in Ssdashivapet (M) of Sangareddy Division of Sangareddy Circle .
S.No | SSR Code | Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR10105 | 39 | ERECTION OF S.S. STRUCTURE: Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 23400
2 | SWR10343 | 31 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 74400
3 | SWR10356 | 27.28 | ERECTION OF S.S. STRUCTURE: Providing of mass concreting of size 0.76x0.76x1.52M with CC mix of ratio 1:3:6 Using form boxes (0.88 Cu.Mt)*31 with 40mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 179475.12
4 | SWR11890 | 0.96 | ERECTION OF S.S. STRUCTURE: Coping of 0.45x0.45x0.45Mt with 1:8 slope Using form boxes (0.031Cumt.) | Civil work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | M3 | 3737.28
5 | SWR11331 | 31 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of poles with two coats of white cement (including cost of paint). | Electrical work | Paint-9.1M PSCC Poles as desc SSR | As per relevent standard specification | 485 | EA | 15035
6 | SWR11889 | 5.5 | Fabrication of 100 X 50mm MS Channel for formation of 11kV and 33kV bays: Fabrication and erection of M.S,Channel 100x50mm for forming of 33KV & 11 KV Bays as per standard specifications to facilitate stringing of bus, erection of LA sets, AB Switches bolts & Nuts etc. including painting with one coats of red oxide and two coats of Aluminium paint. GI bolts&nuts shall be used. | Electrical work | Fabr & Erect-MS Chnl 100x50mm for SS Bay | As per relevent standard specification | 6600 | TO | 36300
7 | SWR10404 | 115 | Erection of 33kV and 11kV Strung Bus with Panther (200Sqmm) ACSR Conductor: Erection of 33kV and 11kV Bus over the Substation structures with 200sqmm Panther ACSR conductor and giving Jumpers to connect the Switch gear by providing the suitable T clamps and round clamps suitable to Post type insulators & Insulators. | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 37683.2
8 | SWR10392 | 2 | Erection of 33 kv AB Switches includesAssembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 9000
9 | SWR10393 | 10 | Erection of 11kV AB Switches 800/400 Amps includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 32000
10 | SWR11742 | 3 | Supply & erection of 11 kV 400 A convential single(1/3) phasing AB switches.includes Assembling, Erection and alignment for normal Operation for perfect closing and opening and providing Jumpers on either side of AB Switch with Panther ACSR.The AB switch operating rod shall be provided with proper locking arrangement with locks of reputed Company. | Electrical work | S&E-400A 11KV ABSwth Conv 1ph(1/3) in SS | As per relevent standard specification | 4232 | EA | 12696
11 | SWR21240 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt). | Electrical work | Hoisting post ins&hrd wr 1panther 33kv | As per relevent standard specification | 781 | EA | 1562
12 | SWR21241 | 4 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 11kv | As per relevent standard specification | 507 | EA | 2028
13 | SWR10881 | 12 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 1704
14 | SWR23224 | 16.46 | Excavation of pit in all types of soils of size 2.2x2.2x0.85Mts.for Construction of Plinths for VCB (33KV & 11 KV ) | Earth work | Excavate-Pit for 33KV VCB | As per relevent standard specification | 331 | M3 | 5448.26
15 | SWR20685 | 22.24 | Providing of Base concreting (2.2x2.2x0.15 Mts) with 1:3:6 Concrete mix. Using form boxes, Providing of Concreting (2x2x1.0mts) with 1:3:6 Cocrete mix. Plastering of the plinth for smooth finishing with 12mm thick 1:3 cement motor and providing two coats white washing for part of the plinth above groung level. | Civil work | Cement concrete with 40MM metal VCB plin | As per relevent standard specification | 5160 | M3 | 114758.4
16 | SWR10461 | 4 | Erection of Switchgear complete for 11 kV VCB includes Assembling the VCB Structures and mounting the VCBs over the already erected foudation including wiring of Breaker Control Panel/CTs, erection of CTs and control pannel providing Jumpers. | Electrical work | Erection of 11kv VCB | As per relevent standard specification | 12000 | EA | 48000
17 | SWR10396 | 2 | Erection of 33KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 1760
18 | SWR10397 | 1 | Erection of 11 KV Lightening Arrestors station type complete including jumpering. | Electrical work | Erect of 11kv LA stn type incl earthing | As per relevent standard specification | 559 | SET | 559
19 | SWR10398 | 3 | Erection of 11 KV Lightening Arrestors line type complete including jumpering. | Electrical work | Erect of 11kvLA line type incl earthing | As per relevent standard specification | 505 | SET | 1515
20 | SMR11607 | 1 | Supply of 33kv HG fuse set including providing of jumpers | Electrical work | S-33KV HG Fuse Set excl Ins & Chnl | As per relevent standard specification | 6431 | SET | 6431
21 | SWR10394 | 1 | Erection of 33kv HG fuse set including providing of jumpers | Electrical work | Erect. of 33kv HG Fuseset incl earthing | As per relevent standard specification | 1331.81 | SET | 1331.81
22 | SMR11608 | 1 | Supply of 11kv HG fuse set including providing of jumpers | Electrical work | S-11KV HG Fuse Set | As per relevent standard specification | 1733.75 | SET | 1733.75
23 | SWR10395 | 1 | Erection of 11kv HG fuse set including providing of jumpers | Electrical work | Erect. of 11kv HG Fuseset incl earthing | As per relevent standard specification | 740.52 | SET | 740.52
24 | SMR11482 | 22 | Supply of C I earth pipe of size 100mm dia, 2.75mtrs long for earth electrode | Electrical work | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 76692
25 | SWR10357 | 22 | Erection of Earth Electrode including Providing of earthing with excavation of earth pit (0.6x0.6x2.4Mtrs) duly filling with Bentonite, earth, running of earth wire etc., complete including cost of Bentonite, RCC collar of size 0.6M dia x 0.5M height. Bentonite powder (2bags)of quanity 50kgs per each earth pit shall be provided. | Earth work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 27152.4
26 | SWR10920 | 500 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification.75x8 mm MS flat for Earth mat and connecting to electrodes. | Electrical work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 32500
27 | SWR10919 | 950 | Formation of Earth mat includes Laying of earth mat with MS Flat including fixing of earth flat, welding connecting to equipment & including connecting to cast iron pipes as per technical specification. 50x6 mm MS flat for raisers, double flat shall be run for structure poles raisers & equipment earthing. | Electrical work | Earthing for raisers of SS Flat 50x6 mm. | As per relevent standard specification | 41 | RMT | 38950
28 | SMR40033 | 2 | Providing of double earthing for neutral with flexible copper jumpers of adequate size including arrangement by fixing M.S.Channel 100x50mm. | Electrical work | SupCU Flexi jumper for Power T/F Neutral | As per relevent standard specification | 4725 | EA | 9450
29 | SWR11771 | 4 | Erection of 24 Volts Battery along with Charger on the VCB plinth and giving DC supply to VCB's. | Electrical work | Erect-24V Batery with Chrgr incl grot-SS | As per relevent standard specification | 1050 | EA | 4200
30 | SWR11474 | 600 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable includes excavation of earth and back filling with sand and earth in alternate layers . The cable termination shall be made by providing proper size lugs and shall be identified with colours. | Electrical work | Laying-4 core cable | As per relevent standard specification | 15 | RMT | 9000
31 | SWR10463 | 1 | Erection of 25 kVA Three phase Station Transformer on the Substation Structures and giving jumpers/connections on HT side to the 11kV bus. Belting angle shall be provided both sides of DTR for securing DTR firmly in position. | Electrical work | Erection of Three Phase DTRs | As per relevent standard specification | 1139.95 | EA | 1139.95
32 | SMR40045 | 1 | Supply of AC Panel Board includes: Fixing of 1 No.100A, MCCB, 10kA capacity of any standard make including material cost. Fixing of suitable panel box 3x3x1 with M.S.Sheet of 16 SWG with front door compartments inclusive of material cost & powder coating (with C Channel ). Fabrication of panel Fixing of 96x96mm analog voltmeter with VSS switch Fixing of 20A HRC fuse Fixing of 3 phase supply indicator kwith HRC fuses Supply and fixing of 6 Sqmm copper flexible wire (PVC) Fixing of Stud type TBs for outgoing feeder Fixing of Epoxy bus supports. | Electrical work | Supply of AC Supply panel complete | As per relevent standard specification | 42000 | EA | 42000
33 | SMR40044 | 1 | Supply of DC Panel Board Fixing of suitable panel box of size 6'x6'x1' with M S sheet of 16 SWG with back doors (4'x6') and on front side with provision to fix up bakelite hylam sheet size of 4'x6' including cost of the panel with powder coating. Fixing of best quality of angles for panel. Fixing of C Channelfor panel. Fabrication of control panel including making suitable holes and board Fixing of Stud type TBs for outgoing feeder Fixing of 24V DC pilot lamps of standard make Fixing of healthy trip push buttons with LED lamp Fixing of plain switches for alarm acceptance and for PTR signal Fixing of ON/OFF push buttons Fixing of digital volt meter for 11kV Fixing of VSS of standard make, Fixing of Engraved AL plates for Alarm panel of various VCB Laying of 2.5Sqmm copper flexible wire for internal wiring . Fixing of digital frequency meter Fixing of Copper lugs and ferrules for internal wiring. Fixing of 4" Gang bells 24V DC Fixing of flow diagram with rading strip Fixing of HRC fuse units | Electrical work | Supply of DC Anunc.relay panel 8 feeders | As per relevent standard specification | 42500 | EA | 42500
34 | SWR20025 | 1 | fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supplied by tenderer. | Electrical work | Erect-Contrl/Relay, AC, Announ. Panels | As per relevent standard specification | 7871.85 | EA | 7871.85
35 | SWR10342 | 8 | Erection of 8.0 Mts PSCC Poles complete with necessary hard ware for yard lighting excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 12000
36 | SWR10956 | 8 | Fixing of Metal halide/LED lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5M GI pipe complete. | Electrical work | Fixing of LED/Metal halide complete. | As per relevent standard specification | 1268 | EA | 10144
37 | SWR20028 | 8 | Supply and Fixing of junction box and Providing with proper Fuse protection and required glauds suitable for Cable Terminations. The box shall be fixed on the pole. | Electrical work | 33/11kv S.S Yard lighting junction box | As per relevent standard specification | 351.9 | EA | 2815.2
38 | SWR20526 | 1 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply & fixing of marshall box | As per relevent standard specification | 3085.5 | EA | 3085.5
39 | SMR40088 | 1 | Supply and fixing of filled sand bucket set complete (4 Nos. Buckets) with stand to mount fire buckets. | Electrical work | Sup Fire Buckets Stand with Buckets | As per relevent standard specification | 1386 | SET | 1386
40 | SMR40087 | 2 | Supply and fixing of CO2 Cylinder set as per IS2878 Specifications. | Electrical work | Sup TrollyMounted Co2 Cylinders(IS-2878) | As per relevent standard specification | 9240 | EA | 18480
41 | SWR11895 | 1 | Supplying and fixing of feeder indicator board to each of the 3Nos feeder breakers and LV breaker, danger boards made of 1'x1' and properly mounted on the structures. The letters written on the borad shall be 1.5"size with blue colour and background shall be of white colour | Electrical work | S&F-33/11KV SS Feeder Indicator Board | As per relevent standard specification | 551 | SET | 551
42 | SWR20032 | 1 | Supply and fixing of wooden board of size 3'x2'.5'indicating the layout of the Switch yard. | Electrical work | Sup &fix of board ind Switchyard layout | As per relevent standard specification | 1654 | EA | 1654
43 | SMR40086 | 1 | Supply and Erection of Permanent Name Board of on 3'x4' steel sheetmounted on steel frame as described in Specification. | Electrical work | Sup 33/11kv S.S Permanent name board | As per relevent standard specification | 10238 | EA | 10238
44 | SMR40076 | 1 | Supply of Digital clamp meter. | Electrical work | Supply of Digital clamp meter. | As per relevent standard specification | 2888 | EA | 2888
45 | SMR40064 | 1 | Supply of Rechargeable LED torch light of Standard make. | Electrical work | Sup Rechargeable LED torch light. | As per relevent standard specification | 1733 | EA | 1733
46 | SMR40063 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box containing ‘D’Spanners from size 6 to 54, Hammer small and big size, Ring spanners from 6 to 28, Adjustable spanner, Pipe wrench, Cutting Plier, Nose plier, Tester, insulated Screw drive. | Electrical work | SupTaparia Tool kit complete as per Spec | As per relevent standard specification | 4925 | SET | 4925
47 | SWR22090 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Electrical work | Sup& fix safety inst/SS Op. inst board | As per relevent standard specification | 2205 | EA | 2205
48 | SMR11598 | 8 | Supply of 25 W LED lamp with fitting of philips make | Electrical work | S-25W LED fixture set | As per relevent standard specification | 3200 | EA | 25600
49 | SMR12378 | 1 | Supply of Alluminum Ladder(20 feet) | Electrical work | S-10ft Aluminium Ladder | As per relevent standard specification | 1654 | EA | 1654
50 | SMR40075 | 1 | Supply of Megger (2000 ohms, 0-2.5kv) | Electrical work | Supply of Earth megger (1000v) | As per relevent standard specification | 8085 | EA | 8085
51 | SMR40067 | 2 | Supply of Hand Gloves | Electrical work | Supply of Hand Gloves | As per relevent standard specification | 289 | SET | 578
52 | SMR40071 | 2 | Supply of Safety Helmets of standard make | Electrical work | Supply of Safety Helmet of standard make | As per relevent standard specification | 231 | EA | 462
53 | SMR11599 | 4 | Supply of Earth Discharging Rod 10' length. | Electrical work | S-Earth Rod 8ft Long 3mm Thick | As per relevent standard specification | 1000 | EA | 4000
54 | SMR11488 | 200 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 23500
55 | SMR11591 | 66 | Supply of PG clamps for panther 2 bolted 800 A. | Electrical work | S-Al. alloy three bolted PG clamps 800A | As per relevent standard specification | 130 | EA | 8580
56 | SWR20029 | 350 | Supply and Laying of 2 core/4 core cable includes excavation earth and back filling with sand and earth in alternate layers as shown in the sketch. The cable termination shall be made by providing proper size of lugs at both ends of the cable termination. | Electrical work | 33/11kv S.S laying of 2/4core for light | As per relevent standard specification | 50 | M | 17500
57 | SWR20308 | 31 | Sub Transportation of 9.1 M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 12625.99
58 | SWR20307 | 8 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM. | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 2172.16
59 | SWR11860 | 2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip. | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 5440.68
60 | SWR10150 | 10.5 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM. | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 6479.55
61 | SWR10206 | 10.5 | Loading of MS Channel,Angles,Flats&Rods. | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 2320.5
62 | SWR10524 | 10.5 | Unloading of MS Channel,Angles,Flats&Rod. | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 1942.5
63 | SWR11220 | 350 | Loading and unwinding of Panther conductor. | Electrical work | Load-Unwinding Panther conductor | As per relevent standard specification | 3 | M | 1050
64 | SWR11221 | 350 | Unloading of Panther conductor. | Electrical work | Unload-Unwinding Panther conductor | As per relevent standard specification | 2 | M | 700
65 | SWR12416 | 2 | Loading of 33 KV and 11 KV Disc insulators. | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 4
66 | SWR10631 | 2 | Unloading of 33 KV and 11 KV Disc insulators. | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 4
67 | SWR10618 | 2 | Loading of 33KV Metal parts bag of 25 nos. | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 130
68 | SWR10632 | 2 | Unloading of 33 KV Metal parts bag of 25 nos. | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 130
69 | SWR10212 | 2 | Loading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | LOADING of 11kv Pin/Post/Solid Core Insu | As per relevent standard specification | 1 | CRT | 2
70 | SWR10530 | 2 | Unloading of of 11kv Pin insulator/Post type insulator/Solid Core Insulators. | Electrical work | UNLOADING of 11kv Pin/Post/Solid Core In | As per relevent standard specification | 1 | CRT | 2
71 | SWR11701 | 600 | Loading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | Load-PVC Control Cable 10C | As per relevent standard specification | 1 | M | 600
72 | SWR11712 | 600 | Unloading of PVC Copper Control Cable 4 core and 10 core. | Electrical work | UnLoad-PVC Control Cable 10C | As per relevent standard specification | 1.02 | M | 612
73 | SWR11691 | 1 | Loading of 3Ph 25KVA Distribution Transformer. | Electrical work | Load-3Ph 25KVA DTR | As per relevent standard specification | 252 | EA | 252
74 | SWR11692 | 1 | UnLoading of 3Ph 25KVA Distribution Transformer. | Electrical work | UnLoad-3Ph 25KVA DTR | As per relevent standard specification | 202 | EA | 202
75 | SWR10200 | 1 | Loading of 33/11 KV Current Transformers/ Potential Transformers. | Electrical work | LOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 165 | EA | 165
76 | SWR10266 | 6 | Loading of 33 KV10 KA LAs Station type. | Electrical work | LOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 41 | EA | 246
77 | SWR10584 | 6 | Unloading of 33 KV10 KA LAs Station type. | Electrical work | UNLOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 35 | EA | 210
78 | SWR10265 | 9 | Loading of 11 KV10 KA LAs Line type. | Electrical work | LOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 288
79 | SWR10583 | 9 | Unloading of 11 KV10 KA LAs Line type. | Electrical work | UNLOADING of 11 KV, 10 KA LAs Line type | As per relevent standard specification | 32 | EA | 288
80 | SWR10264 | 3 | Loading of 11 KV10 KA LAs Station type. | Electrical work | LOADING of 11 KV,10 KA LAs Station type | As per relevent standard specification | 32 | EA | 96
81 | SWR10582 | 3 | Unloading of 11 KV10 KA LAs Station type. | Electrical work | UNLOADING of 11 KV,10 KA LAs Station typ | As per relevent standard specification | 32 | EA | 96
82 | SWR10239 | 2 | Loading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 252
83 | SWR10557 | 2 | Unloading of 33 KV AB Switch Conventional 400/800 Amp. | Electrical work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 158
84 | SWR10238 | 10 | loading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 800
85 | SWR10556 | 10 | Unloading of 11 KV AB Switch Conventional 200/400 Amp. | Electrical work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 800
86 | SWR11224 | 4 | Loading and Unloading of 12V/24V Battery Set. | Electrical work | Load/Unload-12V/24V Battery Set | As per relevent standard specification | 23 | EA | 92
87 | SWR10356 | 2.66 | ERECTION OF S.S. STRUCTURE: Providing of base concreting of size 0.76x0.76x0.15M with CC mix of ratio 1:3:6 Using form boxes(0.087Cu.Mt)x31 with 20mm HBG metal. | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 17500.14
88 | SWR10402 | 1 | Erection of 11kv Potential Transformer sets complete including jumpering. The LV side of the PT shall be provided with proper fuse protection mounted in separate marshalling boxwith proper size cable glands etc. The box shall be mounted on the Substation structure. | Electrical work | Erection of 11kv three phase PT s | As per relevent standard specification | 800 | SET | 800
89 | SWR10518 | 1 | Unloading of 33/11 KV Current Transformers/ Potential Transformers | Electrical work | UNLOADING of 33/11 KV CTs/ PTs | As per relevent standard specification | 128 | EA | 128 | 1121406.76
90 | SWR10674 | 1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
91 | SWR10356 | 4.32 | Concreting the location after erection of 8.0 Mtrs pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) ( 0.6x0.6x1.5)mtrs x 8 . | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 28421.28
92 | SWR21750 | 2 | Erection of marshalling box on the structure (pole mounted type) marshalling boxes shall be supplied by the constractor | Electrical work | Supply and fixing of PT Marshalling box | As per relevent standard specification | 1139.85 | EA | 2279.7
93 | SWR10884 | 350 | Connectionof equipment to bus and or another equipmentwithsingle zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Electrical work | Conn. of equip/bus single zebra/panther | As per relevent standard specification | 224 | EA | 78400
94 | swr20102 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Electrical work | Erection of 11kv TT type AB Switch | As per relevent standard specification | 1813.49 | EA | 1813.49
95 | SWR20905 | 1 | Erection of 3 Phase DTR including loading and Unloading DTR on the Structure/Plinth etc | Electrical work | E/r 3ph DTR inclu L&Un-T&C on plinth | As per relevent standard specification | 1650 | EA | 1650
96 | SMR40009 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for First coat of 1st GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 11995.5
97 | SWR10877 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 1st coat of Aluminium | Electrical work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 4680.5
98 | SMR40010 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.including supply of material cost for second coat of 2nd GradeAluminiumPaint, brushes etc. | Electrical work | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 7111.5
99 | SWR10879 | 5.5 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting includingscratchingandcleaningof Sub station structures of 2nd coat of Aluminium | Electrical work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 2651
100 | SMR25233 | 31 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 96391.71
101 | SMR22745 | 5500 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 315975
102 | SMR12321 | 2350 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 132587
103 | SMR12322 | 2280 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 128820
104 | SMR25232 | 8 | Supply of 8.0Mtr PSCC 140 Kg Pole | Electrical work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 12640
105 | SMR12315 | 2 | Supply of 33KV 800A DB Break AB Switch | Electrical work | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 81317.56
106 | SMR12316 | 3 | Supply of 11KV 800A DB Break AB Switch | Electrical work | S-11KV 800A DB Break AB Switch | As per relevent standard specification | 30847.46 | EA | 92542.38
107 | SMR12317 | 7 | Supply of 11KV 400A DB Break AB Switch | Electrical work | S-11KV 400A DB Break AB Switch | As per relevent standard specification | 18150 | EA | 127050
108 | SMR25200 | 1 | Supply of LT Distribution Box (SMC) | Electrical work | S-LT Distribution Box (SMC) | As per relevent standard specification | 7797 | EA | 7797
109 | SWR10674 | 1 | Fixing of Distribution Box and Providing with proper Fuse protection system and reqired Cable Terminations at Station T/F LT side and AC/DC Panel and fixing meter. Power cable of adequate size shall be provided from station DTR to control room AC Panel. | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
110 | SWR22092 | 0.63 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 33 kv line | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 481.95
111 | SWR10107 | 10 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 7000
112 | SWR10112 | 3 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | As per relevent standard specification | 1680 | EA | 5040
113 | SWR10105 | 8 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/ excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 4800
114 | SWR10978 | 13 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 54148.64
115 | SWR10343 | 8 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 19200
116 | SWR10981 | 4 | Formation of 33 kv cut points (Vertical/Horizantal) including fixing of Clamps and top cleat and fixing of pin insulator complete with necessary hard wear for stud locations excluding the cost of pit Excavation and the pole shall be numbered with colour paint and earthing. | Electrical work | Horizontal Cut point for 33 KV line | As per relevent standard specification | 1759.5 | EA | 7038
117 | SWR10356 | 6.342 | Concreting the location after erection of 11 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes (0.76X0.76X1.83 Mts)*6 = 6.342 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 41724.018
118 | SWR10366 | 0.63 | Paving of the 100 sqmm AAA conductor and stringing duly arranging temporary guys, tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pin binding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 12600.06 | KM | 7938.0378
119 | SMR11488 | 26 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 3055
120 | SWR11180 | 13 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 5615.61
121 | SWR20308 | 8 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 3258.32
122 | SWR10191 | 1 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 202
123 | SWR10509 | 1 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 100
124 | SWR11860 | 1 | Transport of VCB , Control pannels, current transformater, bosster etc, above 10 KM and upto 50 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 2720.34
125 | SWR10150 | 0.38 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL MATERIAL 30 TO 50KM | As per relevent standard specification | 617.1 | TO | 234.498
126 | SWR10206 | 0.38 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 83.98
127 | SWR10524 | 0.38 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 70.3
128 | SWR10211 | 4 | Loading of 33 KV Pin insulators | Electrical work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 12
129 | SWR10529 | 4 | Unloading of 33 KV Pin insulators | Electrical work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | CRT | 12
130 | SWR12416 | 3 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 6
131 | SWR10631 | 3 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 6
132 | SWR10618 | 1 | Loading of 33KV Metal parts bag of 25 nos | Electrical work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 65
133 | SWR10632 | 1 | Unloading of 33 KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 33 KV Metal parts-bagof 25 | As per relevent standard specification | 65 | BAG | 65
134 | SWR10252 | 10 | Loading of 33KV Top fittings | Electrical work | LOADING of 33 KV Top fittings | As per relevent standard specification | 1 | EA | 10
135 | SWR10570 | 10 | Unloading of 33 KV Top fittings | Electrical work | UNLOADING of 33 KV Top fittings | As per relevent standard specification | 1 | EA | 10
136 | SWR10319 | 17 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 75 x 8 mm MS Flat | Electrical work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31 | EA | 527
137 | SWR10322 | 32 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 75 x 8 mm MS Flat | Electrical work | Fab Stay clamps with 75x8 mm MM Flat | As per relevent standard specification | 42 | EA | 1344
138 | SWR10378 | 13 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevent standard specification | 32 | EA | 416
139 | SWR10354 | 4 | Erection of 33 kv Stay set complete including fixing of bow ,fixing and binding of Eye bolt, Anchor rod, guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. | Electrical work | Assembly and erection of Stay set 33kv | As per relevent standard specification | 684.53 | SET | 2738.12
140 | SWR21190 | 4 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In all soils except Hard gravel Hard Murram, Disintegrated Rock,Hard rock Requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 2080
141 | SMR25236 | 13 | Supply of 11Mtr PSCC 365 Kg Pole | Electrical work | S-PSCC Pole 11Mtr 365 Kg | As per relevent standard specification | 5399 | EA | 70187
142 | SMR25233 | 8 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 24875.28
143 | SMR25229 | 10 | Supply of 33KV V-Cross Arm without Clamps | Electrical work | S-33KV V-Cross Arm without Clamps | As per relevent standard specification | 1678 | EA | 16780
144 | SMR25207 | 100 | Supply of MS Angle 65X65X6 | Electrical work | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 5725
145 | SMR22745 | 150 | Supply of MS Channel 100x50mm | Electrical work | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 8617.5
146 | SMR12321 | 150 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 8463
147 | SMR25231 | 4 | Supply of 33KV MS Stay Set with BasePlate | Electrical work | S-33KV MS Stay Set with BasePlate | As per relevent standard specification | 1035 | SET | 4140
148 | SWR22092 | 4.61 | Detailed Survey and way leave clearance. The work includes Peg marking and necessary tree clearance for erection of 11 kv line. | Earth work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 3526.65
149 | SWR10107 | 45 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 31500
150 | SWR10105 | 52 | Excavation of Pole pits of size 0.76x0.76x1.52 for 9.1 mts PSCC Poles for structure as per layout drawings including watering,shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 5.0') | As per relevent standard specification | 600 | EA | 31200
151 | SWR10112 | 20 | Excavation of Pole pits of size 0.76x0.76x1.83 Mts' for 11 mts PSCC Poles including dewatering, shoring, shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 1680 | EA | 33600
152 | SWR10110 | 9 | Excavation of Pole pits of size (2.6" x 2.6" x 5.0') 0.88 cum 0.76 M x 0.76M x 1.52M for 9.1 mtrs PSCC Poles including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting of poles whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead. Pole to pole span shall be maintained as 60Mts.In all soils except Hard gravel Hard Murram, Disintegrated Rock, Hard rock Requiring blasting. | Earth work | EXCAV. OF PIT HARD(2.6" x 2.6" x 5.0") | As per relevent standard specification | 1440 | EA | 12960
153 | SWR10978 | 65 | Erection of 11 Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4165.28 | EA | 270743.2
154 | SWR10343 | 49 | Erection of 9.1Mtr pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. The contractor has to supply GI Bolts and Nuts | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 117600
155 | SWR10342 | 12 | Erection of 8.0 Mts PSCC Poles including fixing of 11 KV X arm and top cleats and fixing of Pin insulators complete with necessary hard ware for tangential locations excluding the cost of Pit Excavation. Each Location of pole shall be numbered with colour paints.The contractor has to supply GI Bolts and Nuts. | Electrical work | ERECTION OF LINES-Erection of 8M Pole | As per relevent standard specification | 1500 | EA | 18000
156 | SWR11974 | 30 | Laying of 33 KV 185 sqmm XLPE UG cable including excavation of trench of size 1050mm for 11 KV from road level providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Change and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site including the cost of lead and lift etc.depth of the trench for 11KV 1.05 mtrs. | Electrical work | Lay-DR 11KV 3x185sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 631.06 | M | 18931.8
157 | SWR10988 | 30 | Laying of 11 KV 3x185 sqmm XLPE UG cable double run in Hard Rock(1.2*0.5x1=0.6cum) including excavation of trench of size 1200mm for 33 KV from road level providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Change and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site including the cost of lead and lift etc. | Electrical work | Lay-2nd Cable in Excavated Trench | As per relevent standard specification | 204.1 | M | 6123
158 | SWR12006 | 30 | Raising of 11 KV 185 sqmm XLPE UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe | Electrical work | Raise-DR 11KV 3x185sqmm UG Cb on support | As per relevent standard specification | 243.53 | M | 7305.9
159 | SWR10390 | 4 | Making of Outdoor End Termination 33KV XLPE Out-Door End kit (3x400sqmm) | Electrical work | OD/Idoor end termination 11kv 3x185 xlpe | As per relevent standard specification | 2370.63 | EA | 9482.52
160 | SWR11171 | 4 | Loading of 11/33 KV IN/OUT door kits | Electrical work | Loading of 11/33 KV IN/OUT door kits | As per relevent standard specification | 6 | EA | 24
161 | SWR11152 | 4 | Unloading of 11/33 KV IN/OUT door kits | Electrical work | Un-loading of 11/33 KV IN/OUT door kits | As per relevent standard specification | 4 | EA | 16
162 | SWR10653 | 20 | Formation of 11 kv cut points (Vertical/Horizantal) including fixing of 11 KV Cross arms,clamps, strain insulators sets complete with hardware and stays (Bows and Eye-bolts), Excluding the cost of pit Excavation and pole erection. The contractor has to supply GI Bolts and Nuts. | Electrical work | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1350 | EA | 27000
163 | SWR10356 | 37.673 | Concreting the location after erection of 11 mtrs/ 9.1 mt pole with CC (1:4:8) using 40 mm,HBG metal including the cost of all materials and curing , Dewatering the pits before after concreting (River sand, Metal, Cement, water shall be procured by the contractor) for cut points location / PSCC pole.Using form boxes for 2 no's 11 Mtrs poles (0.76X0.76X1.83 Mts)*22 = 23.122 Cu.Mt and 9 no's 9 Mtrs poles (0.76X0.76X1.52 Mts)*16 = 14.032 Cu.Mt | Civil work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 247850.667
164 | SWR10365 | 4.61 | Paving of the conductor 55 Sqmm AAAC and stringing duly arranging temporary guys,tensioning, sagging of conductor maintaing the ground clearences as per IE rules1956, pinbinding, strain insulator binding and giving jumpers Etc.Stiffner pieces shall be be provided for all pin insulator locations. | Electrical work | Stringing of 55sqmm 33/11kv Line 3 Cond | As per relevent standard specification | 8500 | KM | 39185
165 | SMR11488 | 200 | Supply of GI Bolts,Nuts and Washers etc. | Electrical work | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 23500
166 | SWR10206 | 1.3 | Loading of MS Channel,Angles,Flats&Rods | Electrical work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 287.3
167 | SWR10524 | 1.3 | Unloading of MS Channel,Angles,Flats&Rod | Electrical work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 240.5
168 | SWR11248 | 276 | Loading 11KV Polymer Pin Insulator- with GI pins | Electrical work | Load-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 276
169 | SWR11249 | 276 | Unloading 11KV Polymer Pin Insulator with GI pins | Electrical work | Unload-11KV Polymer Pin Insulator-GI pin | As per relevent standard specification | 1 | EA | 276
170 | SWR10134 | 1.3 | Transport of steel including line materital such as cross arm,clamps,hard ware(including loading and unloading) above 30KM and upto 50KM | Electrical work | TRANSPORT OF STEEL 30 TO 50KM | As per relevent standard specification | 587.52 | TO | 763.776
171 | SWR11862 | 2 | Transport of VCB , Control pannels, current transformater, bosster etc, above 20 KM and upto 30 KM with lorry for each trip | Electrical work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 7382.76
172 | SWR10191 | 2 | Loading of Conductor drums | Electrical work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 404
173 | SWR10509 | 2 | Unloading of Conductor drums | Electrical work | UNLOADING of Conductor drums | As per relevent standard specification | 100 | EA | 200
174 | SWR11180 | 65 | Sub Transportation of 11.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 431.97 | EA | 28078.05
175 | SWR20307 | 12 | Sub Transportation of 8.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 8M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 271.52 | EA | 3258.24
176 | SWR20308 | 49 | Sub Transportation of 9.0M PSCC Pole including Loading and Unloading<10KM | Electrical work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 19957.21
177 | SWR10228 | 74 | Loading of 11 KV V - Cross arms | Electrical work | LOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 296
178 | SWR10546 | 74 | Unloading of 11 KV V - Cross arms | Electrical work | UNLOADING of 11 KV V - Cross arms | As per relevent standard specification | 4 | EA | 296
179 | SWR12402 | 6 | Loading of 11KV Metal parts bag of 25 nos | Electrical work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 288
180 | SWR12421 | 6 | Unloading of 11KV Metal parts bag of 25 nos | Electrical work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 288
181 | SWR10251 | 74 | Loading of 11 KV Top fittings | Electrical work | LOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 74
182 | SWR10569 | 74 | Unloading of 11 KV Top fittings | Electrical work | UNLOADING of 11 KV Top fittings | As per relevent standard specification | 1 | EA | 74
183 | SWR12416 | 6 | Loading of 33 KV and 11 KV Disc insulators | Electrical work | LOADING of 33 & 11 KV Disc insulators | As per relevent standard specification | 2 | CRT | 12
184 | SWR10631 | 6 | Unloading of 33 KV and 11 KV Disc insulators | Electrical work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | CRT | 12
185 | SWR10353 | 18 | Erection of 11 kv Stay set complete including fixing of bow, fixing and binding of Eye bolt,Anchor rod,guy insultors including the back filling with earth and boulders and ramming for consolidation, but excluding the cost of pit excavation. The contractor has to supply GI Bolts and Nuts. | Electrical work | Assembly and erection of Stay set11kv&LT | As per relevent standard specification | 606.85 | SET | 10923.3
186 | SWR21190 | 18 | Excavation of Stay pits of size 0.45x0.45x1.34 Mts' for burying the anchor rod with anchor plateof stay sets including dewatering, shoring,shuttering wherever necessary and back filling the pit (after erection and concreting the same whever is necessary) with the excavated earth/extra earth/excavated rock bits if any and leveling the site without any lead.In Hard Gravel and Hard murram not requiring blasting. | Earth work | Excavate-StayPit .45x.45x1.34mSoil ex Hr | As per relevent standard specification | 520 | EA | 9360
187 | SWR10319 | 78 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 75 x 8 mm MS Flat | Electrical work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31 | EA | 2418
188 | SWR10322 | 96 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 75 x 8 mm MS Flat | Electrical work | Fab Stay clamps with 75x8 mm MM Flat | As per relevent standard specification | 42 | EA | 4032
189 | SWR10320 | 35 | Fabrication of materials including 2 coats of Red oxide painting for Back clamps with 50 x 6 mm MS Flat | Electrical work | Fab Back clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 15 | EA | 525
190 | SWR10323 | 48 | Fabrication of materials including 2 coats of Red oxide painting for Stay clamps with 50 x 6 mm MS Flat | Electrical work | Fab Stay clamps with 50 x 6 mm MS Flat | As per relevent standard specification | 25 | EA | 1200
191 | SWR10378 | 92 | Numbering of poles incl. cost of paint | Electrical work | Numbering of poles incl. cost of paint | As per relevent standard specification | 32 | EA | 2944
192 | SMR25236 | 65 | Supply of 11Mtr PSCC 365 Kg Pole | Electrical work | S-PSCC Pole 11Mtr 365 Kg | As per relevent standard specification | 5399 | EA | 350935
193 | SMR25233 | 49 | Supply of 9.1Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 152361.09
194 | SMR25232 | 12 | Supply of 8.0Mtr PSCC 280 Kg Pole | Electrical work | S-PSCC Pole 8Mtr 140kg | As per relevent standard specification | 1580 | EA | 18960
195 | SMR25218 | 74 | Supply of 11KV V X-Arms with MS Angle 65x65x6 | Electrical work | S-11KV V X-Arms with MS Angle 65x65x6 | As per relevent standard specification | 743 | EA | 54982
196 | SMR25205 | 400 | Supply of MS Channel 75x40 mm | Electrical work | S-MS Channel 75x40 mm | As per relevent standard specification | 58.45 | KG | 23380
197 | SMR25206 | 320 | Supply of MS Angle 50x50x6 | Electrical work | S-MS Angle 50x50x6 | As per relevent standard specification | 58.15 | KG | 18608
198 | SMR12321 | 450 | Supply of MS Flat 75x8mm | Electrical work | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 25389
199 | SMR12322 | 130 | Supply of MS Flat 50x6mm | Electrical work | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 7345
200 | SMR25214 | 18 | Supply of LT/11KV MS Stay Sets with Base Plate | Electrical work | S-LT/11KV MS Stay Sets with Base Plate | As per relevent standard specification | 1168 | SET | 21024
201 | SMR25208 | 4 | Supply of 11KV 3x300 Heat Shble O/d End Term Kit | Electrical work | S-11KV 3x300 Heat Shble O/d End Term Kit | As per relevent standard specification | 1372.88 | EA | 5491.52
[6 empty] | Total |  |  | 4238399.7968
1 | SWR34179 | 12 | Cutting and Levelling the site with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work. | JCB | NA | As per relevant standard specification | 2164.1 | H | 25969.2
2 | SWR33015 | 125.33 | Earth Work Excavation to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions, labour and material charges etc., complete as directed by the engineer-incharge. | Earth Work | NA | As per relevant standard specification | 347 | M3 | 43489.51
3 | SWR33028 | 16.99 | PCC (1:4:8) for levelling course using 40mm size hard broken Granite stone including cost and conveyance of all materials, HBG metal for foundations and leveling course and as directed by the Engineer- in - charge etc complete for finished item of work. | PCC | NA | As per relevant standard specification | 4064 | M3 | 69047.36
4 | SWR33041 | 113.27 | CRS masonry in CM (1:6) using Hard Granite Stones including cost and conveyance of all materials, seignorage charges, labour charge for construction and for dressing stones to required size and shape, dewatering, scaffolding, cutting for all leads and lifts, all incidental charges etc .complete for finished item of work as directed by the Engineer - in - charge. | Masonry | NA | As per relevant standard specification | 4437 | M3 | 502578.99
5 | SWR33068 | 19.2 | Construction of brick masonary in CM(1:6) including cost and conveyance of all materials, labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Masonry | NA | As per relevant standard specification | 7624 | M3 | 146380.8
6 | SWR33052 | 1110.16 | Supplying and filling with borrowed gravel, watering, ramming, consolidating thoroughly complying with the standard specification including cost and conveyance of all materials, labour charges,hire charges of machnery,with all leads and incidental charges etc complete for finished item work as directed by the Engineer - in - charge. | Gravel | NA | As per relevant standard specification | 435 | M3 | 482919.6
7 | SWR33098 | 6.74 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel (a) Footings | RCC | NA | As per relevant standard specification | 8227 | M3 | 55449.98
8 | SWR33100 | 2.36 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel (b) Columns | RCC | NA | As per relevant standard specification | 10922 | M3 | 25775.92
9 | SWR33099 | 1.61 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel (c) Plinth Beams | RCC | NA | As per relevant standard specification | 10647 | M3 | 17141.67
10 | SWR33107 | 0.33 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel (d) Lintels | RCC | NA | As per relevant standard specification | 11082 | M3 | 3657.06
11 | SWR33114 | 7.68 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel (e) Sunshade | RCC | NA | As per relevant standard specification | 1162 | M2 | 8924.16
12 | SWR33121 | 2.44 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel (f) Roof Beams | RCC | NA | As per relevant standard specification | 10657 | M3 | 26003.08
13 | SWR33128 | 6.94 | R.C.C M20 nominal mix using 12 to 20 mm HBG metal incldg cost & conveyance of all materials machine mixing, centering,curing ,all labour charges,etc comp.excluding cost of steel (g) Slab of 130 mm thick | RCC | NA | As per relevant standard specification | 10208 | M3 | 70843.52
14 | SWR33144 | 2.2 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) / Mild steel (MS) steel bars (Fe 415/ Fe 500 grade as per IS 1786-1979) of different diameters for RCC works complete for finished item of work in all floors.( APSS No.126) | Steel | NA | As per relevant standard specification | 75077 | TO | 165169.4
15 | SWR33163 | 359.51 | Providing plastering of 20mm thick to all uneven faces of walls and ceiling of superstructure in two coats with base coat in CM 1:6 of 16mm thick and top coat in Cm 1:4 4mm thick with dubara sponge finish | Plastering | NA | As per relevant standard specification | 410 | M2 | 147399.1
16 | SWR33184 | 134.1 | Raised pointing in CM(1:3) including curing, cost and conveyance of all materials and labour charges for complete item of work. | Plastering | NA | As per relevant standard specification | 94 | M2 | 12605.4
17 | SWR33156 | 51.52 | Providing impervious coat over RCC roof slab surfaces to requried slopes with 20mm thick in CM 1:3 pro mixed with approvaled brand of water proffing compound as the raet of 1 kg per bag of cement inclding cost and conveyance of all materials | Plastering | NA | As per relevant standard specification | 440 | M2 | 22668.8
18 | SWR33264 | 5.7 | Supply and fixing of Flush type Doors with 35mm Thick Flush Shutters with Bondwood solied Block Board Type Faced on Both the sides with Commercial Type Plywood for finished item work as directed by the Engineer - in- charge. | Doors | NA | As per relevant standard specification | 6799.02 | M2 | 38754.414
19 | SWR33277 | 5.76 | Supply and Fixing of Aluminium sliding windows with fixed glass panels using aluminium sections 62x32x1.2mm providing 5mm plain glass fixed to frame with beading gasket and glazing clips with all accessories,locking arrangements including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Windows | NA | As per relevant standard specification | 3381.54 | M2 | 19477.6704
20 | SWR33310 | 6.25 | Supplying and fixing of MS safety grill with peripheral frame of ISA 25x25x4mm and horizontal & vertical 8mm square rods and including cost and coveyance of all mateirals with all leads and lifts, labour charges, painting charges complete for finished item of work | Windows | NA | As per relevant standard specification | 2539 | M2 | 15868.75
21 | SWR33219 | 36.3 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and approved size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and pointing with cement, labour etc, complete for finished item of work. | Flooring | NA | As per relevant standard specification | 659 | M2 | 23921.7
22 | SWR33236 | 5.24 | Providing skirting with tandoor blue slabs including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Flooring | NA | As per relevant standard specification | 726 | M2 | 3804.24
23 | SWR33029 | 21.6 | Plain Cement contrete - Nominal Mix (1:3:6) using 40 mm metal with concrete mixture including cost and conveyance of all materials labour charges etc. complete for finished iitem of work and as directed by the engineer-in-charge. | PCC | NA | As per relevant standard specification | 4371 | M3 | 94413.6
24 | SWR33030 | 6.86 | PCC(1:2:4) using 10 to 12 mm aggregate including cost and conveyance of all materials labour charges etc., complete for finished iitem of work and as directed by the engineer-in-charge. | PCC | NA | As per relevant standard specification | 5504 | M3 | 37757.44
25 | SWR33057 | 51.77 | Supply and Spreading of 20mm machine crushed metal including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | HBG metal | NA | As per relevant standard specification | 1514 | M3 | 78379.78
26 | SWR33403 | 110 | Supply and fixing of fencing of welded wire mesh (2" x 2") of 3mm dia with support channels of 75x 40mm and angles around of 30x30x3 mm including cost and conveyance of all materials, fabrication charges,painting charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Welded mesh | NA | As per relevant standard specification | 2042 | M2 | 224620
27 | SWR33404 | 10.07 | Supply and fixing of MS gates of approved design including cost and conveyance of all materials,fabrication charges etc complete for finished item of work. | Paint | NA | As per relevant standard specification | 4579.89 | M2 | 46119.4923
28 | SWR33415 | 7.3 | Manufacture, supply ,laying and fixing of 450mm dia. NP3 class R.C.C. socket and spigot pipes (rate per meter of effective length) including transportaion ,taxes and duties etc. complete for finished item of work and as directed by the Engineer-in-charge. | Paint | NA | As per relevant standard specification | 1344 | Rmt | 9811.2
29 | SWR33333 | 122.1 | Painting with two coats of OBD over a coat of primer including cost and conveyance of all materials ,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Paint | NA | As per relevant standard specification | 109.9 | M2 | 13418.79
30 | SWR33336 | 177.9 | Painting with two coats of ACE paint over a coat of primer including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Gate | NA | As per relevant standard specification | 195.91 | M2 | 34852.389
31 | SWR33329 | 177.2 | Painting with lovely cem three coats including cost and conveyance of all materials , labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | NA | As per relevant standard specification | 70.47 | M2 | 12487.284
32 | SWR33442 | 25 | Supply and fixing 25mm dia 1.5mm thick recessed( concealed) PVC pipe alnog with reinforcement to be laid in slab including No 14 SWG GI wire for earth contunity, cost of pipe, binding wire and all labour charges etc complete | Electrification | NA | As per relevant standard specification | 85 | RMT | 2125
33 | SWR33441 | 15 | Supply and fixing 20mm dia 1.5mm thick recessed( concealed) PVC pipe in walls including No 14 SWG GI wire for earth contunity, cost of pipe, binding wire and all labour charges etc complete | Electrification | NA | As per relevant standard specification | 89 | RMT | 1335
34 | SWR33457 | 15 | Wiring with 2X1.0 Sqm(14/.3mm) PVC insulated flexiable copper cable in the existing metalic/Non metalic conduit pipe with 6A mini modular SP switch, mounted on metalic box covereds with appropriate front plate modules etc ceiling rose including cot and conveyance of all mateials, labour charges complete for light points, bell points and fan points in non residential builsing except circuit moving finished in all types masonary as directed by department. | Electrification | NA | As per relevant standard specification | 580 | EA | 8700
35 | SWR33461 | 2 | Supply and fixing of 6A 3/2 pin flush type plug socket with 6A flush type marked switch control on a common board with earth continuity including wire leads earth connections along with all labour charges etc. complete | Electrification | NA | As per relevant standard specification | 469 | EA | 938
36 | SWR33464 | 2 | Supply and fixing of 16A 3pin flush type plug socket and 16A flush type fuse unit and 16A switch control. | Electrification | NA | As per relevant standard specification | 437 | EA | 874
37 | SWR33484 | 4 | Supply and fixing of slanting holders with 100W bulb with all connections and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | NA | As per relevant standard specification | 116 | EA | 464
38 | SWR33545 | 3 | Supply and fixing of patty type tube light fitting with 4' 0" - 40W tube light,40W copper choke,starter,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | NA | As per relevant standard specification | 868 | EA | 2604
39 | SWR33494 | 90 | Supply and run of 2 of 14/.3mm(1.00Sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | NA | As per relevant standard specification | 48 | RMT | 4320
40 | SWR33497 | 30 | Supply and run of 2 of 36/0.3 (2.5sqmm) pvc insulated flexible copper cable in the existing metalic/non-metalic conduit pipe. | Electrification | NA | As per relevant standard specification | 95 | RMT | 2850
41 | SWR33520 | 1 | SPN Distribution board with IP-20 protection suitable for single phase 40A DP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 4Nos as out going MCBs in sheet steel enclosure including connections and cost of all material labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | NA | As per relevant standard specification | 5038 | EA | 5038
42 | SWR33596 | 1 | Providing independent earthing for main switches,IC cutouts and motors using 40mm. Dia. B-class G.I.Pipe of 2.5' length duly providing 12mm. Dia. 6No. Holes and required bolts,nuts and washers,including filling with equal preparation of salt and charcoal in layers and labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Electrification | NA | As per relevant standard specification | 4891 | EA | 4891
43 | SWR33597 | 15 | Supply and run of No.8 SWG Copper wire including cost of all accessories and labour charges etc., Complete | Flooring | NA | As per relevant standard specification | 140 | RMT | 2100
44 | SWR33563 | 2 | Supply and Fixing of 48" ceiling fan of bajaj make(or equivalent make) including cost material,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 2215 | EA | 4430
45 | SWR33224 | 13.9 | Supply and fixing of ceramic tiles fantacy for dadoing including cost and conveyance of all materials,labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 759 | M2 | 10550.1
46 | SWR34311 | 1 | Supply and fixing of 580mm x 440mm long Orissa pan of Parry, Neycer or Hindhusthan, make with 'P' or 'S' trap etc complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 2178 | EA | 2178
47 | SWR34386 | 2 | Supply and Fixing 4" PVC floor trap including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 269 | EA | 538
48 | SWR34382 | 2 | Supply,fixing 90mm dia. PVC Plain Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 84 | EA | 168
49 | SWR34385 | 2 | Supply,fixing 90mm dia. PVC Door Bend including cost etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 81 | EA | 162
50 | SWR34286 | 1 | S&Fixing 150mm x 100mm SWG gully traps Ist class grating & constg brick masonry in CM (1:6) prop inter mediate chamber and fitted with CI frame etc complete. | Plumbing | NA | As per relevant standard specification | 749 | EA | 749
51 | SWR34377 | 6 | Supply and Fixing 4" dia 3M Single socket PVC pipe including labour charges etc. complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 422 | RMT | 2532
52 | SWR34453 | 1 | Supply and Fixing 4" dia PVC cowl including labour charges etc. complete for finished item of work. | Plumbing | NA | As per relevant standard specification | 23 | EA | 23
53 | SWR34444 | 1 | Construction of soak pit with 4' dia RCM rings upto a depth of 6' including cost and conveyance of all materials as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 2950 | EA | 2950
54 | SWR34361 | 35 | CPVC Pipes and Fittings a) 15.90mm OD Pipe - SDR 11 | Plumbing | NA | As per relevant standard specification | 239 | Rmt | 8365
55 | SWR34362 | 100 | CPVC Pipes and Fittings b) 22.20mm OD Pipe - SDR 11 | Plumbing | NA | As per relevant standard specification | 313 | RMT | 31300
56 | SWR34363 | 80 | CPVC Pipes and Fittings c) 28.60mm OD Pipe - SDR 11 | Plumbing | NA | As per relevant standard specification | 410 | RMT | 32800
57 | SWR34344 | 18 | Supply and fixing of 15mm dia. SS coated taps including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 230 | EA | 4140
58 | SWR34345 | 1 | Supply and fixing of 20mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 331 | EA | 331
59 | SWR34346 | 2 | Supply and fixing of 25mm dia. GM Ball valve including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Plumbing | NA | As per relevant standard specification | 466 | EA | 932
60 | SWR34329 | 3 | Supply and fixing of 12.7mm bib tap Indian make including labour charges complete for finished item of work and as directed by the engineer-in-charge. | Furniture | NA | As per relevant standard specification | 271 | EA | 813
61 | SWR34375 | 500 | Providing and placing on Terrace polyetheylene water storage tank with double layer approved brand and manufacture with cover complete for finished item of work and as directed by the engineer-in-charge. | Furniture | NA | As per relevant standard specification | 10 | L | 5000
62 | SWR33746 | 1 | Supply of steel table of size 4'x2.5'x30" with 18 mm plywood fixed with rubber beeding with drawers on right side with automatic locking arrangements etc complete for finished item of work and as directed by the engineer-in-charge. | Furniture | NA | As per relevant standard specification | 4200 | EA | 4200
63 | SWR33857 | 1 | Supply of 'S' type chair with arms teakwood frame with seat back 's' type on G.I pipe including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | Board | NA | As per relevant standard specification | 3850 | EA | 3850
64 | SWR33858 | 2 | Supply of P V C chairs of Neelkamal of approved quality & make including cost and conveyance complete for finished item of work and as directed by the engineer-in-charge. | LDPE sheet | NA | As per relevant standard specification | 1150 | EA | 2300
65 | SWR33608 | 1 | Geophysical Investgation Charges | Stone Dust | NA | As per relevant standard specification | 5000 | EA | 5000
66 | SWR33609 | 90 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work. 0 to 90M | Hume pipe | NA | As per relevant standard specification | 336 | M | 30240
67 | SWR34830 | 30 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work. 90m to 120M | Fencing poles | NA | As per relevant standard specification | 369 | M | 11070
68 | SWR34831 | 30 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work. 120m to 150M | Fencing poles | NA | As per relevant standard specification | 394 | M | 11820
69 | SWR33611 | 30 | Supply and fixing of 160mm dia PVC casing including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Barbed wire | NA | As per relevant standard specification | 844 | M | 25320
70 | SWR34410 | 160 | Supply and fixing of HDPE pipe 40mm dia of 6Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Power Supply | NA | As per relevant standard specification | 160 | Rmt | 25600
71 | SWR33636 | 1 | Supply and fixing of 2HP/Multi stage submercible motor pumpset of approved make(Texmo or equivalent type)including cost and conveyance of all materials etc. complete for finished item of work as directed by the engineer-in-charge. | Borewell | NA | As per relevant standard specification | 34237 | EA | 34237
72 | SWR33641 | 185 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Power Flex / Fortune Art | Borewell | NA | As per relevant standard specification | 190 | EA | 35150
73 | SWR33644 | 1 | Supply and fixing of D.O.L Starter 250V, single phase motor with no volt coil and over load protection including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Borewell | NA | As per relevant standard specification | 1040 | EA | 1040
74 | SWR34203 | 2 | Supply and fixing of flange clamps including cost of all materials complete for finished item of work as directed by the engineer-in-charge. | Borewell | NA | As per relevant standard specification | 182 | EA | 364
75 | SWR33406 | 150 | S&Fixing of R.C.C fencing poles of size 0.115x0.115x2.75 m in pits of size 0.5x0.5x0.5 m and refilled with P.C.C(1:4:8) using 20 mm HBG metal including cost & conveyance of all materials,labour chargesv etc complete for finished item of work. | Borewell | NA | As per relevant standard specification | 1433.9 | EA | 215085
76 | SWR33407 | 280 | S&Fixing of barbed wire 8 straight strands and 2 cross strands including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Borewell | NA | As per relevant standard specification | 260.05 | Rmt | 72814
77 | SWR33421 | 1.35 | Supply and Fixing of Substation name board of size 5'x3' iron sheet with angle frame and channel supports of size 75x40mm, 8' height including concreting of channel supports and painting with enamel paint complete. | Borewell | NA | As per relevant standard specification | 4542.3 | M2 | 6132.105
78 | SWR33422 | 2.16 | S&F Glow Sign Board including cost and conveyance of labour and material charges | Borewell | NA | As per relevant standard specification | 3730.36 | M2 | 8057.5776
79 | SWR34656 | 759 | S-LDPE Sheet 500Micron including cost and conveyance of labour and material charges | Borewell | NA | As per relevant standard specification | 95 | M2 | 72105
80 | SWR33054 | 65.92 | S&Filling with Borrowed Stone Dust including cost and conveyance of labour and material charges | Borewell | NA | As per relevant standard specification | 1052 | M3 | 69347.84
81 | SWR33425 | 1 | Prov supply of electricity to the site | Borewell | NA | As per relevant standard specification | 5677.88 | EA | 5677.88
82 | SWR34470 | 147 | Seigniorage Charges - Sand | Seignorages | NA | As per relevant standard specification | 40 | M3 | 5880
83 | SWR34471 | 231.7 | Seigniorage Charges - Metal | Seignorages | NA | As per relevant standard specification | 97.5 | M3 | 22590.75
84 | SWR34472 | 1110.2 | Seigniorage Charges - Gravel | Seignorages | NA | As per relevant standard specification | 30 | M3 | 33306
3325097.5523
[7 empty] | Elec & Civil Total |  | 7563497.3491

## 13. Venkatapura SS
Venkatapur Elec Schedule (S-1701-14-06-01-02-001)
Name of the work :- The Proposal envisages for erection of 33/11KV Sub-station with 2 X 8.0 MVA Power Transformer with 5No's 11kV feeders at Venkatapuram of Survey no. 835 in Venkatapuram village in Ghatkesar Mandal in operation Narapally Section in Ghatkesar Sub-Division in Keesara Division of Habsiguda Circle.
Sl.No | SAP Code | Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg.Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR11041 | 25 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) for 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") | Civil Work | Exc of Hard pit w/o blast 0.92X0.92X2.3M | As per relevent standard specification | 1466.25 | EA | 36656.25
2 | SWR11039 | 30 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) for 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Civil Work | Exca Hard pit w/o blast 0.76X0.76X1.83M | As per relevent standard specification | 928 | EA | 27840
3 | SWR10343 | 10 | Erection of 9.1 M long PSCC pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 24000
4 | SWR10356 | 5.4 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. | Civil Work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 35526.6
5 | SWR10348 | 45 | Erection of R.S. Joists 150 x 150 mm pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical work | Erection of RS Joist 150 x 150 mm | As per relevent standard specification | 1952.61 | EA | 87867.45
6 | SWR10868 | 27.9 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels,R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation te,including erection. | Fabrication work | Fabrication of struc.with power drilling | As per relevent standard specification | 6852 | TO | 191170.8
7 | SMR40009 | 31 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Civil Work | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 67611
8 | SWR10356 | 47.25 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. | Civil Work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 310857.75
9 | SWR11890 | 1.395 | Mass Concreting for pole Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Civil Work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | M3 | 5430.74
10 | SWR10743 | 45 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of coping with two coats of white cement (including cost of paint) | Civil Work | Painting of supports to a height of 0.3M | As per relevent standard specification | 686 | EA | 30870
11 | SMR40010 | 31 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before rection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete for Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Civil Work | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 40083
12 | SWR10879 | 31 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before rection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete for Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Civil Work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 14942
13 | SWR21240 | 6 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 33kv | As per relevent standard specification | 781 | EA | 4686
14 | SWR21241 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Electrical work | Hoisting post ins&hrd wr 1panther 11kv | As per relevent standard specification | 507 | EA | 1014
15 | SWR10884 | 65 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring,cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Electrical work | Conn. of equip/bus single zebra/panther | As per relevent standard specification | 224 | EA | 14560
16 | SMR40011 | 45 | Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating | Supply of Material | Sup T clamp LM6 Al alloy of 12 mm, 800 A | As per relevent standard specification | 299 | EA | 13455
17 | SMR11915 | 18 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | Supply of Material | S-Tension HW 3Bolt 1Zebra/Pnthr 150mm | As per relevent standard specification | 2055 | SET | 36990
18 | SMR40039 | 12 | Supply of Bimetalic Copper die clamps suitable for power ransformer/ Lclamps HV of 1/2 inch bush rod and other end suitable for panther conductor and with bimetallic sheet on the pad of size 75X75X10mm with four holes of 14mm diameter (hole to hole distance 40mm) with suitable GI bolts and nuts including washers | Supply of Material | Sup Bimetalic Copper die clamps for PTR | As per relevent standard specification | 909 | EA | 10908
19 | SMR40030 | 6 | Supply of Alluminum Post type insulator suupport clamps conforming to A6 of IS 617, with hot dip alvanised bolts and nuts suitable for 11 kV | Supply of Material | SupPost type insulator suupp clamps 11kV | As per relevent standard specification | 381 | EA | 2286
20 | SMR22473 | 12 | Supply of I-Bolts clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367- 1961) | Supply of Material | Supply of I-Bolts | As per relevent standard specification | 294 | EA | 3528
21 | SWR10423 | 12 | Fixing of I-bolts clamps | Electrical work | Fixing of I-bolts | As per relevent standard specification | 20 | EA | 240
22 | SMR40023 | 33 | Supply of CT stud clamps with hot dip galvanised bolts and nuts suitable for zebra / Panther conductor on one side and 28/30/40 mm CT stud on other side with stud size for single zebra / panther (4 bolted) with bimetallic sleeve for carrying 800 A | Supply of Material | Sup CT stud clamps 1Zebra/Panth for 800A | As per relevent standard specification | 399 | EA | 13167
23 | SMR40019 | 54 | Supply of Alluminum alloy Pad clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR/Zebra of pad size 100 X 100 X 15mm for carrying 600 A current rating . | Supply of Material | SupPad clamps 100X100X15 mm 1 panth 600A | As per relevent standard specification | 264 | EA | 14256
24 | SMR40027 | 33 | Supply of Alluminum LA clamps conforming to A6 of IS 617, with hot dip galvanised bolts and nuts suitable for single zebra / Panther | Supply of Material | Sup LA clamps for single zebra / Panther | As per relevent standard specification | 357 | EA | 11781
25 | SWR10917 | 75 | Labour for Fixing of all types of clamps | Civil Work | Labour for Fixing of all types of clamps | As per relevent standard specification | 65 | EA | 4875
26 | SWR10392 | 8 | Erection of 33 KV AB Switch including alignment and earthing | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 36000
27 | SWR10393 | 17 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 54400
28 | SWR10881 | 23 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Erection work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 3266
29 | SWR23224 | 63.76 | Excavate-Pit for 33KV VCB | Civil Work | Excavate-Pit for 33KV VCB | As per relevent standard specification | 331 | M3 | 21104.56
30 | SWR20685 | 67 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Civil Work | Cement concrete with 40MM metal VCB plin |  | 5160 | M3 | 345720
31 | SWR10461 | 7 | Erection of 11 KV VCB with Control Panel AB Switches, VCBs, LAs, PTs, CTs, DTRs etc | Electrical work | Erection of 11kv VCB | As per relevent standard specification | 12000 | EA | 84000
32 | SWR10460 | 3 | Erection of 33 KV VCB with Control Panel AB Switches, VCBs, LAs, PTs, CTs, DTRs etc | Electrical work | Erection of 33kv VCB | As per relevent standard specification | 12500 | EA | 37500
33 | SMR40045 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification | Supply of Material | Supply of AC Supply panel complete | As per relevent standard specification | 42000 | EA | 42000
34 | SWR20025 | 1 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | Electrical work | 33/11kv S.S Erection of AC&DC Panel | As per relevent standard specification | 7871.85 | SET | 7871.85
35 | SWR11166 | 1 | Loading of 220 V Batterry with charger | Civil Work | Loading 220 V Battery with Charger | As per relevent standard specification | 1612 | SET | 1612
36 | SWR11147 | 1 | Un loading of 220 V Batterry with charger | Civil Work | Un-loading 220 V Battery with Charger | As per relevent standard specification | 1024 | SET | 1024
37 | SWR11772 | 1 | Erection-220V Batery with Chrgr incl all-SS | Electrical work | Erect-220V Batery with Chrgr incl all-SS | As per relevent standard specification | 6442.58 | EA | 6442.58
38 | SWR10402 | 2 | Erection of 11 KV three phase PTs | Electrical work | Erection of 11kv three phase PT s | As per relevent standard specification | 800 | SET | 1600
39 | SWR10396 | 2 | Erection of 33 KV LAS station/Line type including earthing | Electrical work | Erection of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 1760
40 | SWR20976 | 2 | Erection of 33kv LA-3Nos Line type | Electrical work | Erection of 33kv LA-3Nos Line type | As per relevent standard specification | 880 | SET | 1760
41 | SWR10397 | 2 | Erection of 11 KV LAS station type including earthing | Electrical work | Erect of 11kv LA stn type incl earthing | As per relevent standard specification | 559 | SET | 1118
42 | SWR10357 | 32 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Civil Work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 39494.4
43 | SWR10359 | 32 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Civil Work | ERECT. OF LINES-Providing of RCC collar | As per relevent standard specification | 386 | EA | 12352
44 | SWR10920 | 800 | Laying of 75x 8mm MS Flat / GI Flat. earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication. | Civil Work | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 52000
45 | SWR10919 | 1200 | Fabrication and M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) connecting to risers from earth mat to structures, equipment,marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Fabrication work | Earthing for raisers of SS Flat 50x6 mm. | As per relevent standard specification | 41 | RMT | 49200
46 | SWR11880 | 440 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Electrical work | Lay-Cable Terminations to Switchgear | As per relevent standard specification | 34.43 | EA | 15149.2
47 | SMR11594 | 14 | Supply of 90W LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE / CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA.LED MAKE: PHILIPS REE/NICHIA/OSRAM/ SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty | Supply of Material | S-90W LED fixture set | As per relevent standard specification | 8200 | EA | 114800
48 | SWR20028 | 14 | Supply and Fixing of junction box and Providing with proper Fuse protection and required glauds suitable for Cable Terminations. The box shall be fixed on the pole. | Supply of Material | 33/11kv S.S Yard lighting junction box | As per relevent standard specification | 351.9 | EA | 4926.6
49 | SWR11879 | 3000 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Civil Work | Lay-4C/10C 2.5Sqmm Control Cable | As per relevent standard specification | 27 | M | 81000
50 | SMR40049 | 3 | Supply of MS Powder coted PT Marshalling Box | Supply of Material | Sup of MSPowder coted PT Marshalling Box | As per relevent standard specification | 4095 | EA | 12285
51 | SMR40072 | 12 | Supply of LC Boards | Supply of Material | Supply of LC Boards | As per relevent standard specification | 116 | EA | 1392
52 | SMR40070 | 24 | Supply of Danger boards with clamps | Supply of Material | Supply of Danger boards with clamps | As per relevent standard specification | 116 | EA | 2784
53 | SWR10963 | 12 | Painting of Name Plates for any equipment | Civil Work | Painting of Name Plates for any equipmen | As per relevent standard specification | 122 | EA | 1464
54 | SMR12488 | 500 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | Supply of Material | S-Hot dip gal./Zinc bolts & nuts washer | As per relevent standard specification | 90 | KG | 45000
55 | SWR10199 | 7 | Loading of 11 KV VCBs along with Panel boards | Civil Work | LOADING of 11 KV VCBs&Panel boards | As per relevent standard specification | 1024 | EA | 7168
56 | SWR10198 | 3 | Loading of 33 KV VCBs along with Panel boards | Civil Work | LOADING of 33 KV VCBs&Panel boards | As per relevent standard specification | 1024 | EA | 3072
57 | SWR10516 | 3 | Un loading of 33 KV VCBs along with Panel boards | Civil Work | UNLOADING of 33 KV VCBs&Panel boards | As per relevent standard specification | 1044.48 | EA | 3133.44
58 | SWR10517 | 7 | Un loading of 11 KV VCBs along with Panel boards | Civil Work | UNLOADING of 11 KV VCBs&Panel boards | As per relevent standard specification | 1044.48 | EA | 7311.36
59 | SWR10940 | 3 | Erection of Marshalling boxes | Civil Work | Erection of Marshalling boxes | As per relevent standard specification | 374.85 | EA | 1124.55
60 | SWR10401 | 1 | Erection of 33 KV single phase PTs AB Switches, VCBs, LAs, PTs, CTs, DTRs etc | Electrical work | Erection of 33kv single phase PT s | As per relevent standard specification | 1079 | SET | 1079
61 | SWR10402 | 2 | Erection of 11 KV three phase PTs AB Switches, VCBs, LAs, PTs, CTs, DTRs etc | Electrical work | Erection of 11kv three phase PT s | As per relevent standard specification | 800 | SET | 1600
62 | SWR10132 | 34.7 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading | Civil Work | TRANSPORT OF STEEL 10 TO 20KM | As per relevent standard specification | 412.08 | TO | 14299.18
63 | SWR10206 | 34.7 | Loading of M.S.Channels, Angles, Flats & Rods etc. | Civil Work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 7668.7
64 | SWR10524 | 34.7 | Un loading of M.S.Channels, Angles, Flats & Rods etc. | Civil Work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 6419.5
65 | SWR10238 | 15 | Loading of 11KV AB Switch Conventional type | Civil Work | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 1200
66 | SWR10239 | 8 | Loading of 33KV 800 Amps AB Switch Con 400/800 A | Civil Work | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 1008
67 | SWR10264 | 6 | Loading of 11 KV, 10 KA LAs Station type | Civil Work | LOADING of 11 KV,10 KA LAs Station type | As per relevent standard specification | 32 | EA | 192
68 | SWR10266 | 9 | Loading of 33 KV, 10 KA LAs Station type | Civil Work | LOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 41 | EA | 369
69 | SWR10582 | 6 | Un loading of 11 KV, 10 KA LAs Station type | Civil Work | UNLOADING of 11 KV,10 KA LAs Station typ | As per relevent standard specification | 32 | EA | 192
70 | SWR10584 | 9 | Un loading of 33 KV, 10 KA LAs Station type | Civil Work | UNLOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 35 | EA | 315
71 | SWR11701 | 3000 | Loading of PVC Control Cable 10 Core | Civil Work | Load-PVC Control Cable 10C | As per relevent standard specification | 1 | M | 3000
72 | SWR11712 | 3000 | Un loading of PVC Control Cable 10 Core | Civil Work | UnLoad-PVC Control Cable 10C | As per relevent standard specification | 1.02 | M | 3060
73 | SWR10556 | 15 | Un loading of 11KV AB Switch Conventional type Con 200/400 A | Civil Work | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 1200
74 | SWR10557 | 8 | Un loading of 33KV 800 Amps AB Switch Con 400/800 A | Civil Work | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 632
75 | SMR12239 | 3 | Supply Neutral link for PT Marshalling Box for indoor SS | Supply of Material | S-Neutral Link for PT Marshl Box | As per relevent standard specification | 385 | EA | 1155
76 | SWR11417 | 2 | Earthing of arrangement labour for PTR Neutral | Electrical work | Earthing arangemnt labour for PTRNeutral | As per relevent standard specification | 838 | EA | 1676
77 | SWR34621 | 4 | S&F-Nylon Neutral Link Base | Erection work | S&F-Nylon Neutral Link Base | As per relevent standard specification | 106.25 | EA | 425
78 | SWR20308 | 10 | Sub-transport of 9.1 Mtrs long PSCC Poles upto Workspot upto 10KM (Including loading and unloading) | Trasportaion work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 4072.9
79 | SWR10631 | 36 | Un loading of 33 & 11 KV Disc insulators | Civil Work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | KI | 72
80 | SWR10618 | 2 | Loading of 33 KV Metal parts bag of 25no | Civil Work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 130
81 | SWR12421 | 2 | Un loading of 11 KV Metal parts Bag | Civil Work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 96
82 | SWR21321 | 2 | Erection of 8 MVA PTR. PTR on constructed plinth | Electrical work | Erec 33/11 KV, 8 MVA PTR as per Spec | As per relevent standard specification | 49480.2 | EA | 98960.4
83 | SMR40051 | 14 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | Supply of Material | Supply 9mtrs tubular poles single way | As per relevent standard specification | 13913 | EA | 194782
84 | SWR10955 | 14 | Errection of tubular poles | Civil Work | Errection of tubular poles | As per relevent standard specification | 1379 | EA | 19306
85 | SWR10956 | 14 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete | Electrical work | Fixing of LED/Metal halide complete. | As per relevent standard specification | 1268 | EA | 17752
86 | SWR10205 | 45 | Loading of R.S. Joists 150 x 150mm / Rail poles | Civil Work | LOADING of RSJoists150 x 150 mm/RailPole | As per relevent standard specification | 176 | EA | 7920
87 | SWR10523 | 45 | Un loading of R.S. Joists 150 x 150mm / Rail poles | Civil Work | UNLOADING of RSJoists150 x150 mm/RailPol | As per relevent standard specification | 107 | EA | 4815
88 | SWR10867 | 27.9 | Fabrication & erection of Channels Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | Fabrication work | Alligning the Main/Aux. structures. | As per relevent standard specification | 1470 | TO | 41013
89 | SWR10873 | 500 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Supply of Material | Supply,fabricati of 6mm Checkerd plates | As per relevent standard specification | 83 | KG | 41500
90 | SMR40017 | 8 | Supply of Tension clamps for earth wire 3 bolted | Supply of Material | SupTension clamps for earthwire 3bolted | As per relevent standard specification | 715 | SET | 5720
91 | SMR40021 | 31 | Supply of Alluminum alloy Pad clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for twin panther ACSR/Zebra of pad size 100 X 100 X 15mm for carrying 1200 A current rating | Supply of Material | SupPad clamps 100X100X15mm 2 panth 1200A | As per relevent standard specification | 284 | EA | 8804
92 | SMR40025 | 12 | Supply of Alluminum PT clamps conforming to A6 of IS 617,with hot dip galvanised bolts and nuts suitable for single zebra / Panther | Supply of Material | Sup PT clamps for single zebra / Panther | As per relevent standard specification | 368 | EA | 4416
93 | SWR10404 | 200 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | Electrical work | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 65536
94 | SWR11893 | 1 | Erection of control/Relay panels, AC Panels, announciation panels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Electrical work | Erect-Contrl/Relay, AC, Announ. Panels | As per relevent standard specification | 2122 | EA | 2122
95 | SWR10856 | 21.6 | Excavation of Earth work excavtion hard rock boulders pits in hard rock not requiring blasting. (In hard murram / rock boulders) (other than SS) | Civil Work | Earth work excav hard rock bould <3cum | As per relevent standard specification | 1318.35 | M3 | 28476.36
96 | SMR40033 | 4 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral | Supply of Material | SupCU Flexi jumper for Power T/F Neutral | As per relevent standard specification | 4725 | EA | 18900
97 | SWR10398 | 8 | Erection of 11 KV LAS line type including earthing AB Switches, VCBs, LAs, PTs, CTs, DTRs etc | Electrical work | Erect of 11kvLA line type incl earthing | As per relevent standard specification | 505 | SET | 4040
98 | SMR11482 | 32 | Supply of CI earthing pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Supply of Material | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 111552
99 | SWR10263 | 32 | Loading of CI earth pipe 100 mm dia, 2.75 mt long | Civil Work | LOADING of CI Earth pipe upto 2.7 Mtr | As per relevent standard specification | 29 | EA | 928
100 | SWR10581 | 32 | Un loading of CI earth pipe 100 mm dia, 2.75 mt long | Civil Work | UNLOADING of CI Earth pipe upto 2.7 Mtr | As per relevent standard specification | 29 | EA | 928
101 | SWR12510 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Electrical work | L-Cable Termination to Switchgear | As per relevent standard specification | 27 | EA | 7290
102 | SWR22093 | 90 | Providing of control cable trench as per DATA-XII | Electrical work | Providing of cable trench as per DATA-IX | As per relevent standard specification | 3148 | RMT | 283320
103 | SWR21843 | 1 | RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Civil Work | Column type DTR Plinth topslab 4'x4'x6" | As per relevent standard specification | 25967.57 | EA | 25967.57
104 | SWR10195 | 1 | Loading of 50,63, 75 & 100 KVA DTR | Civil Work | LOADING of 50,63,75&100kva DTR | As per relevent standard specification | 350 | EA | 350
105 | SWR10513 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | Civil Work | UNLOADING of 50,63,75&100kva DTR | As per relevent standard specification | 280 | EA | 280
106 | SWR10463 | 1 | Erection of 3 Ph DTRs upto 25KVA DTR's including loading and nloading DTR on the Structure/Plinth etc | Electrical work | Erection of Three Phase DTRs | As per relevent standard specification | 1139.95 | EA | 1139.95
107 | SWR11920 | 30 | Laying of 11KV 3x185 Sqmm XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. | Electrical work | Lay-SR 11KV 3x185sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 465.46 | M | 13963.8
108 | SWR11956 | 20 | Raising of 11 KV 3x185 Sqmm cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Electrical work | Raise-SR 11KV 3x185sqmm UG Cb on support | As per relevent standard specification | 126.23 | M | 2524.6
109 | SWR10390 | 2 | Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | Electrical work | OD/Idoor end termination 11kv 3x185 xlpe | As per relevent standard specification | 2370.63 | EA | 4741.26
110 | SWR10674 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs | Electrical work | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
111 | SMR40044 | 1 | Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification | Supply of Material | Supply of DC Anunc.relay panel 8 feeders | As per relevent standard specification | 42500 | EA | 42500
112 | SMR40048 | 3 | Supply of FRP PT Marshalling Box | Supply of Material | Supply of FRP PT Marshalling Box | As per relevent standard specification | 4463 | EA | 13389
113 | SWR10942 | 10 | Testing of Sub-Station Equipment''Wirring, commissioning and testing of Outdoor Sub-station switchgear duly conducting the pre commissioning test as per relevent standards & issue of certificate by CEIG authorised testing Engineer | Electrical work | Testing of Outdoor SS switchgear | As per relevent standard specification | 1825 | EA | 18250
114 | SWR10854 | 2 | Transport of 8MVA Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading ) | Trasportaion work | Transport of 8MVA power transformer | As per relevent standard specification | 21945 | EA | 43890
115 | SWR10613 | 2 | Loading of 8MVA PTR and unloading of PTR on constructed plinth | Civil Work | LOADING of 8 MVA PTR | As per relevent standard specification | 5805.84 | EA | 11611.68
116 | SWR10627 | 2 | Unloading of 8MVA PTR | Civil Work | UNLOADING of 8 MVA PTR | As per relevent standard specification | 5805.84 | EA | 11611.68
117 | SWR10944 | 2 | Testing of Sub-Station Equipment'' Testing of Power Transformer duly conducting the pre commissioning tests as per relevent standard & issue of certificate by CEIG authorised testing Engineer | Electrical work | Testing of Power Transformer. | As per relevent standard specification | 4000 | EA | 8000
118 | SMR11485 | 75 | Supply of GI Flat 25X3 mm earthing pipe with materials | Supply of Material | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 7875
119 | SWR11923 | 90 | Laying of LT 3 1/2 x 185 Sqmm XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. | Electrical work | Lay-SR LT 3.5x185sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 377.63 | M | 33986.7
120 | SWR11959 | 10 | Raising of LT 3 1/2 x 185 Sqmm cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Electrical work | Raise-SR LT 3.5x185sqmm UG Cb on support | As per relevent standard specification | 85.43 | M | 854.3
121 | SMR40140 | 2 | Supply of 31/2x185Sqmm UG O/D end termination kits | Supply of Material | Sup of 31/2x185Sqmm UG O/D end term kits | As per relevent standard specification | 550 | EA | 1100
122 | SWR10231 | 1 | Loading of 11 KV HG Fuse Sets | Civil Work | LOADING of 11 KV HG Fuse Sets | As per relevent standard specification | 18 | EA | 18
123 | SWR10549 | 1 | Un loading of 11 KV HG Fuse Sets | Civil Work | UNLOADING of 11 KV HG Fuse Sets | As per relevent standard specification | 18 | EA | 18
124 | SWR10395 | 1 | Erection of 11 KV HG Fuse set including earthing AB Switches, VCBs, LAs, PTs, CTs, DTRs etc | Electrical work | Erect. of 11kv HG Fuseset incl earthing | As per relevent standard specification | 740.52 | SET | 740.52
125 | SWR10765 | 2 | Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x 185 Sqmm Cable | Erection work | OD/Idoor end termination LT 3 1/2 x 185 | As per relevent standard specification | 968.9 | EA | 1937.8
126 | SWR20102 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Erection work | Erection of 11kv TT type AB switch | As per relevent standard specification | 1813.49 | EA | 1813.49
127 | SMR40032 | 3 | Supply of 11kv, 200Amps copper Flexible jumpers | Supply of Material | Sup11kv, 200Amps copper Flexible jumpers | As per relevent standard specification | 131 | EA | 393
128 | SWR20032 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard | Supply of Material | Sup &fix of board ind Switchyard layout | As per relevent standard specification | 1654 | EA | 1654
129 | SWR22090 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Supply of Material | Sup& fix safety inst/SS Op. inst board | As per relevent standard specification | 2205 | EA | 2205
130 | SMR40059 | 1 | Supply of Wall clock standard make | Supply of Material | Supply of Wall clock standard make | As per relevent standard specification | 578 | EA | 578
131 | SMR12378 | 1 | Supply of -10ft Aluminium Ladder | Supply of Material | S-10ft Aluminium Ladder | As per relevent standard specification | 1654 | EA | 1654
132 | SMR40063 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19,20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make . | Supply of Material | SupTaparia Tool kit complete as per Spec | As per relevent standard specification | 4925 | SET | 4925
133 | SMR40064 | 1 | Rechargeable LED torch light of Standard make | Supply of Material | Sup Rechargeable LED torch light. | As per relevent standard specification | 1733 | EA | 1733
134 | SMR40061 | 1 | Supply of Steel almarah(61/2 X 3ft) Godrej | Supply of Material | Sup Steel almarah(61/2 X 3ft) Godrej | As per relevent standard specification | 9818 | EA | 9818
135 | SMR40057 | 1 | Supply of Table (3x6ft) Godrej | Supply of Material | Supply of Table (3x6ft) Godrej | As per relevent standard specification | 6050 | EA | 6050
136 | SMR40058 | 4 | Supply of type chairs (Godrej) | Supply of Material | Supply of S type chairs (Godrej) | As per relevent standard specification | 924 | EA | 3696
137 | SMR40060 | 1 | Supply of Angle racks(18x36.6inches) Godrej | Supply of Material | Sup Angle racks(18x36.6inches) Godrej | As per relevent standard specification | 1733 | EA | 1733
138 | SMR40065 | 1 | Supply of Hack saw (12 inches) | Supply of Material | Supply of Hack saw (12 inches) | As per relevent standard specification | 289 | EA | 289
139 | SMR40066 | 4 | Supply of Earthing Rods (8ft) Screw & clamp type | Supply of Material | Sup Earth Rods (8ft) Screw & clamp type | As per relevent standard specification | 578 | EA | 2312
140 | SMR40067 | 2 | Supply of Hand Gloves | Supply of Material | Supply of Hand Gloves | As per relevent standard specification | 289 | SET | 578
141 | SMR40068 | 12 | Supply of Rubber mats ( 6’x3’) size for indoor SS | Supply of Material | SupRubber mats( 6’x3’)size for indoorSS | As per relevent standard specification | 1386 | EA | 16632
142 | SMR40069 | 1 | Supply of Standard basic cell phone with charger | Supply of Material | Sup Stand basic cell phone with charger | As per relevent standard specification | 1386 | EA | 1386
143 | SMR40088 | 1 | Supply of Fire bucket stand with 3 buckets (8 -10 ltr capacity) | Supply of Material | Sup Fire Buckets Stand with Buckets | As per relevent standard specification | 1386 | SET | 1386
144 | SMR40089 | 2 | Supply of Room fire extinguisher (2 ltrs capacity) for control room | Supply of Material | Sup Fire Extinguisher for Control Room | As per relevent standard specification | 4620 | EA | 9240
145 | SMR40087 | 4 | Supply of Trolley mounted CO2 (6.5Kgs) | Supply of Material | Sup TrollyMounted Co2 Cylinders(IS-2878) | As per relevent standard specification | 9240 | EA | 36960
146 | SMR40071 | 6 | Supply of Safety Helmets of standard make | Supply of Material | Supply of Safety Helmet of standard make | As per relevent standard specification | 231 | EA | 1386
147 | SMR40073 | 4 | Supply of Gum Boots (Pair) | Supply of Material | Supply of Gum Boots | As per relevent standard specification | 693 | EA | 2772
148 | SMR40074 | 1 | Supply of 5000v megger | Supply of Material | Supply of 5000v megger | As per relevent standard specification | 13860 | EA | 13860
149 | SMR40075 | 1 | Supply of Earth megger (1000v) | Supply of Material | Supply of Earth megger (1000v) | As per relevent standard specification | 8085 | EA | 8085
150 | SMR40076 | 1 | Supply of Digital clamp meter. | Supply of Material | Supply of Digital clamp meter. | As per relevent standard specification | 2888 | EA | 2888
151 | SMR40086 | 1 | Supply of Name board of the 33/11kV Sub-Station(As per Standard Specification) | Supply of Material | Sup 33/11kv S.S Permanent name board | As per relevent standard specification | 10238 | EA | 10238
152 | SWR10862 | 27.5 | Plastering 2 Coats,20/16mm(1:6)(1:4) | Civil Work | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | As per relevent standard specification | 373 | M2 | 10257.5
153 | SMR22718 | 700 | S/o rail poles 90/105lb (250x2N) | Supply of Material | S/o rail poles 90/105lb (250x2N) | As per relevent standard specification | 47.27 | KG | 33089
154 | SWR10344 | 4 | Erection of Rail pole 90 lbs | Electrical work | Erection of Rail Pole 90Lbs | As per relevent standard specification | 3510 | EA | 14040
155 | SWR10877 | 31 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete.Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Civil Work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 26381
156 | SWR11267 | 1 | Erection of Erect-12Meter Box pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Supply of Material | Erect-12Meter Box pole | As per relevent standard specification | 3901.37 | EA | 3901.37
157 | SWR10107 | 1 | Excavation of 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum pits in all soils except hard rock requiring blasting | Civil Work | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 700
158 | SMR12302 | 17200 | Supply-RS Joist Grider Pole (150x150mm) | Supply of Material | S-RS Joist Grider Pole (150x150mm) | As per relevent standard specification | 59.25 | KG | 1019100
159 | SMR25233 | 10 | Supply-PSCC Pole 9.1Mtr 280kg | Supply of Material | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 31094.1
160 | SMR22745 | 10500 | Supply- MS Channel 100x50mm | Supply of Material | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 603225
161 | SMR12321 | 3800 | Supply-MS Flat 75x8mm | Supply of Material | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 214396
162 | SMR12322 | 3000 | Supply-MS Flat 50x6mm | Supply of Material | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 169500
163 | SMR12315 | 8 | Supply-33KV 800A DB Break AB Switch | Supply of Material | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 325270.24
164 | SMR12316 | 15 | Supply-11KV 800A DB Break AB Switch | Supply of Material | S-11KV 800A DB Break AB Switch | As per relevent standard specification | 30847.46 | EA | 462711.9
165 | SMR12317 | 2 | Supply-11KV 400A DB Break AB Switch | Supply of Material | S-11KV 400A DB Break AB Switch | As per relevent standard specification | 18150 | EA | 36300
166 | SMR25204 | 100 | Supply-LT XLPE Cable 3 1/2 C 185 sqmm | Supply of Material | S-LT XLPE Cable 3 1/2 C 185 sqmm | As per relevent standard specification | 547 | M | 54700
167 | SMR12318 | 1 | Supply-11KV 200A Tilting Type AB Switch | Supply of Material | S-11KV 200A Tilting Type AB Switch | As per relevent standard specification | 8991 | EA | 8991
168 | SMR12324 | 1 | Supply-11KV HG FuseSet for StationTransformer | Supply of Material | S-11KV HG FuseSet for StationTransformer | As per relevent standard specification | 1974 | EA | 1974
169 | SMR25200 | 1 | Supply-LT Distribution Box (SMC) | Supply of Material | S-LT Distribution Box (SMC) | As per relevent standard specification | 7797 | EA | 7797
170 | SMR25030 | 40 | Supply-LT 1Core 120Ssqmm XLPE Al. Cable | Supply of Material | S-LT 1Core 120Ssqmm XLPE Al. Cable | As per relevent standard specification | 3118.66 | M | 124746.4
171 | SMR12303 | 1000 | Supply-RS Joist Pole (175x85mm) | Supply of Material | S-RS Joist Pole (175x85mm) | As per relevent standard specification | 60.75 | KG | 60750
172 | SWR22092 | 8.2 | survey line&cabl inc peg mark&tree clear | Civil Work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 6273
173 | SWR11040 | 52 | Excavation of 0.75 M x 0.9 M x 1.95 M pits for 11 Mtrs PSCC Poles/ Box poles in hard rock not requiring blasting. (In hard murram / rock boulders) | Civil Work | Ex of Hard pit w/o blast 0.75X0.9X1.95M | As per relevent standard specification | 990.68 | EA | 51515.36
174 | SWR10978 | 102 | Erection of 11 Mtrs PSCC poles in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical work | Errection of 11 M long PSCC pole | As per relevent standard specification | 4336.85 | EA | 442358.7
175 | SWR10356 | 62.4 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. | Civil Work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 410529.6
176 | SWR10466 | 20 | Formation of Cut point for 33 KV Double circuit line excluding pole erection and stays | Electrical work | Formation of 33kvline vertical cutpoint | As per relevent standard specification | 3198.72 | EA | 63974.4
177 | SWR10366 | 5.1 | Paving out and stringing of 100 Sqmm Single Circuit (3 Conductors) conductor by providing temporary stays, tensioning,sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location. | Electrical work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 13856.7 | KM | 70669.17
178 | SWR10149 | 3 | Transport of steel including line materials such as cross arms, clamps, hardware, cable (loose) and other line materials (Including loading and unloading) Above 20 KM and upto 30 KM | Trasportaion work | TRANSPORT OF STEEL MATERIAL 20 TO 30KM | As per relevent standard specification | 527.34 | TO | 1582.02
179 | SWR10206 | 3 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Civil Work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 663
180 | SWR10524 | 3 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Civil Work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 555
181 | SWR10211 | 279 | Loading of 33 KV Pin insulators | Civil Work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | KI | 837
182 | SWR10529 | 120 | Un loading of 33 KV Pin insulators | Civil Work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | KI | 360
183 | SWR10618 | 8 | Loading of 33 KV Metal parts | Civil Work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 520
184 | SWR11863 | 6 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) above 30 Km and upto 50 Km with Lorry for each trip | Trasportaion work | Transport of Cond Drum,VCBs >30 & <50Km | As per relevent standard specification | 4372.74 | EA | 26236.44
185 | SMR11488 | 650 | Supply of GI Bolts & Nuts etc | Supply of Material | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 76375
186 | SWR11863 | 10 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) above 30 Km and upto 50 Km with Lorry for each trip | Trasportaion work | Transport of Cond Drum,VCBs >30 & <50Km | As per relevent standard specification | 4372.74 | EA | 43727.4
187 | SWR11230 | 21 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Civil Work | Load-11/33KV XLPE UG Cable for all sizes | As per relevent standard specification | 1024 | DR | 21504
188 | SWR11231 | 21 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Civil Work | Unload-11/33KV XLPE UG Cable all sizes | As per relevent standard specification | 1024 | DR | 21504
189 | SWR11972 | 1200 | Laying of XLPE UG 33 KV 3x400 Sqmm Cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters ,providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts | Electrical work | Lay-DR 33KV 3x400sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 749 | M | 898800
190 | SWR11980 | 1800 | Laying of 33 KV 3x400 Sqmm UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters ,providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor | Electrical work | Lay-DR 33KV 3x400sqmm UG Cb CC/BT Compsr | As per relevent standard specification | 1388.84 | M | 2499912
191 | SWR10988 | 3000 | Laying of 2nd cable in excavated trench | Electrical work | Lay-2nd Cable in Excavated Trench | As per relevent standard specification | 204.1 | M | 612300
192 | SWR12004 | 200 | Raising of 33 KV 3x400 Sqmm Cable double run on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Electrical work | Raise-DR 33KV 3x400sqmm UG Cb on support | As per relevent standard specification | 323.85 | M | 64770
193 | SMR40081 | 400 | Supply of 6" B class GI pipe | Supply of Material | S-6" B Class GI pipe 5mm thck 20Kg/M | As per relevent standard specification | 1044 | M | 417600
194 | SWR10387 | 20 | Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination | Electrical work | OD/Idoor end termination 33kv 3x400 xlpe | As per relevent standard specification | 2764.76 | EA | 55295.2
195 | SWR10382 | 16 | Making of Straight through joints 33 KV 3x400 Sqmm Cable | Electrical work | Straight through joint 33kv 3x400 xlpe | As per relevent standard specification | 5700.78 | EA | 91212.48
196 | SWR10392 | 4 | Erection of 33 KV AB Switch including alignment and earthing | Electrical work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 18000
197 | SWR10881 | 4 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint)with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. | Civil Work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 568
198 | SWR10108 | 50 | Excavation of 0.75 M x 0.9 M x 1.95 M (1.31cum) for 11 Mtrs PSCC Poles/ Box poles pits in all soils except hard rock requiring blasting | Civil Work | EXCAV. OF PIT 0.75 M x 0.9 M x 1.95 M | As per relevent standard specification | 629.85 | EA | 31492.5
199 | SWR10191 | 5 | Loading of Conductor drums | Civil Work | LOADING of Conductor drums | As per relevent standard specification | 202 | EA | 1010
200 | SMR40009 | 3 | Painting of Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete | Civil Work | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 6543
201 | SWR10877 | 3 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. for Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Civil Work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 2553
202 | SMR40010 | 3 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. | Civil Work | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 3879
203 | SWR10879 | 3 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. for Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Civil Work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 1446
204 | SMR12315 | 4 | Supply-33KV 800A DB Break AB Switch | Supply of Material | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 162635.12
205 | SMR22745 | 1900 | Supply- MS Channel 100x50mm | Supply of Material | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 109155
206 | SMR12321 | 860 | Supply-MS Flat 75x8mm | Supply of Material | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 48521.2
207 | SMR25207 | 270 | Supply-MS Angle 65X65X6 | Supply of Material | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 15457.5
208 | SMR22223 | 16 | Supply of 33KV3x400Sqmm Straight thr kit | Supply of Material | Supply of 33KV3x400Sqmm Straight thr kit | As per relevent standard specification | 24151 | EA | 386416
209 | SMR22222 | 20 | Supply of 33KV 3x400Sqmm O/D End Kit | Supply of Material | Supply of 33KV 3x400Sqmm O/D End Kit | As per relevent standard specification | 4554 | EA | 91080
210 | SMR25234 | 102 | Supply-PSCC Spun Pole 11Mtr | Supply of Material | S-PSCC Spun Pole 11Mtr | As per relevent standard specification | 6540 | EA | 667080
211 | SWR22092 | 2.1 | survey line&cabl inc peg mark&tree clear | Civil Work | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 1606.5
212 | SWR10466 | 10 | Formation of Cut point for 33 KV Double circuit line excluding pole erection and stays | Electrical work | Formation of 33kvline vertical cutpoint | As per relevent standard specification | 3198.72 | EA | 31987.2
213 | SMR40009 | 3.325 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. | Supply of Material | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 7251.83
214 | SWR10877 | 3.325 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. for Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Civil Work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 2829.58
215 | SMR40010 | 3.325 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete for Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Supply of Material | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 4299.23
216 | SWR10879 | 3.325 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. for Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Civil Work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 1602.65
217 | SWR10366 | 2.1 | Paving out and stringing of 100 Sqmm Single Circuit (3 Conductors) by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location. | Electrical work | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 13856.7 | KM | 29099.07
218 | SWR10149 | 3.325 | Transport of steel including line materials such as cross arms, clamps, hardware,cable (loose) and other line materials (Including loading and unloading) for Above 20 KM and upto 30 KM Ton ₹ | Trasportaion work | TRANSPORT OF STEEL MATERIAL 20 TO 30KM | As per relevent standard specification | 527.34 | TO | 1753.41
219 | SWR10206 | 3.325 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Civil Work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 734.83
220 | SWR10524 | 3.325 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Civil Work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 615.13
221 | SWR10211 | 306 | Loading of 33 KV Pin insulators | Civil Work | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | KI | 918
222 | SWR10529 | 306 | Un loading of 33 KV Pin insulators | Civil Work | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | KI | 918
223 | SWR10618 | 2 | Loading of 33 KV Metal parts | Civil Work | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 130
224 | SWR11863 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) above 30 Km and upto 50 Km with Lorry for each trip | Trasportaion work | Transport of Cond Drum,VCBs >30 & <50Km | As per relevent standard specification | 4372.74 | EA | 8745.48
225 | SMR11488 | 420 | Supply of GI Bolts & Nuts etc Kg ₹ | Supply of Material | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 49350
226 | SWR10392 | 1 | Erection of 33 KV AB Switch including alignment and earthing | Erection work | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 4500
227 | SWR10881 | 1 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Civil Work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 142
228 | SMR12315 | 1 | Supply-33KV 800A DB Break AB Switch | Supply of Material | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 40658.78
229 | SMR22745 | 2088 | Supply- MS Channel 100x50mm | Supply of Material | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 119955.6
230 | SMR12321 | 945 | Supply-MS Flat 75x8mm | Supply of Material | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 53316.9
231 | SMR25207 | 292 | Supply-MS Angle 65X65X6 | Supply of Material | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 16717
232 | SWR11039 | 125 | Excavation of 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") pits for 9.1 Mtrs PSCC Poles in hard rock not requiring blasting. (In hard murram / rock boulders) | Civil Work | Exca Hard pit w/o blast 0.76X0.76X1.83M | As per relevent standard specification | 928 | EA | 116000
233 | SWR10112 | 125 | Excavation of 0.76 M x 0.76M x 1.83M(2.6" x 2.6" x 6.0") pits for 9.1Mtrs PSCC Pole in hard rock requiring blasting. (other than SS) | Civil Work | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | As per relevent standard specification | 1770 | EA | 221250
234 | SWR10343 | 250 | Erection of 9.1 M long PSCC pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming incl | Electrical work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 600000
235 | SWR10356 | 34.02 | Mass concreting of Including the cost of cement supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. | Civil Work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 223817.58
236 | SWR10653 | 20 | Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays | Electrical work | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1435.81 | EA | 28716.2
237 | SMR40009 | 5.955 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. | Supply of Material | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 12987.86
238 | SWR10877 | 5.955 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. for Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Civil Work | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 5067.71
239 | SMR40010 | 5.955 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete for (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Supply of Material | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 7699.82
240 | SWR10879 | 5.955 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. for Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Civil Work | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 2870.31
241 | SWR10365 | 10 | Paving out and stringing of 55 Sqmm Single Circuit (3 Conductors by providing temporary stays, tensioning,sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location. | Electrical work | Stringing of 55sqmm 33/11kv Line 3 Cond | As per relevent standard specification | 9454.81 | KM | 94548.1
242 | SWR20308 | 250 | Sub-transport of 9.1 Mtrs long PSCC Poles upto Workspot upto 10KM (Including loading and unloading) | Trasportaion work | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 101822.5
243 | SWR10393 | 2 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Electrical work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 6400
244 | SWR10881 | 2 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Civil Work | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 284
245 | SMR11485 | 50 | Supply of earthing pipe with materials: GI Flat 25X3 mm | Electrical work | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 5250
246 | SWR10206 | 5.955 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Civil Work | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 1316.06
247 | SWR10149 | 5.955 | Transport of steel including line materials such as cross arms, clamps, hardware, cable (loose) and other line materials (Including loading and unloading) above 20 KM and upto 30 KM | Trasportaion work | TRANSPORT OF STEEL MATERIAL 20 TO 30KM | As per relevent standard specification | 527.34 | TO | 3140.31
248 | SWR10524 | 5.955 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Civil Work | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 1101.68
249 | SWR10212 | 750 | Loading of 11KV pin insulators/Post type insulators/ Solid core insulators | Civil Work | LOADING of 11kv Pin/Post/Solid Core Insu | As per relevent standard specification | 1 | KI | 750
250 | SWR10631 | 750 | Un loading of 33 & 11 KV Disc insulators | Civil Work | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | KI | 1500
251 | SWR12402 | 8 | Loading of 11 KV Metal parts | Civil Work | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 384
252 | SWR12421 | 8 | Un loading of 11 KV Metal parts | Civil Work | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 384
253 | SWR11862 | 8 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) for Above 20 Km and upto 30 Km with Lorry for each trip | Trasportaion work | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 29531.04
254 | SMR11484 | 4 | Supply of CI eath pipe with 50mm dia,2.0 M Length | Supply of Material | S-CI Pipe earthing 50mm dia 2m long | As per relevent standard specification | 2441 | EA | 9764
255 | SWR10359 | 4 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Civil Work | ERECT. OF LINES-Providing of RCC collar | As per relevent standard specification | 386 | EA | 1544
256 | SWR10357 | 4 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Erection work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 4936.8
257 | SMR11485 | 50 | Supply GI Flat 25X3 mm of earthing pipe with materials | Supply of Material | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 5250
258 | SMR25233 | 250 | Supply-PSCC Pole 9.1Mtr 280kg | Supply of Material | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 777352.5
259 | SMR25205 | 3800 | Supply-MS Channel 75x40 mm | Supply of Material | S-MS Channel 75x40 mm | As per relevent standard specification | 58.45 | KG | 222110
260 | SMR25206 | 1800 | Supply-MS Angle 50x50x6 | Supply of Material | S-MS Angle 50x50x6 | As per relevent standard specification | 58.15 | KG | 104670
261 | SMR12322 | 355 | Supply-MS Flat 50x6mm | Supply of Material | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 20057.5
262 | SMR12317 | 2 | Supply-11KV 400A DB Break AB Switch | Supply of Material | S-11KV 400A DB Break AB Switch | As per relevent standard specification | 18150 | EA | 36300
|  | Total Service Cost: | [6 empty] | 17171759.95 | 6370000 | 10801759.95
1 |  | 1 | Geophysical investigation charges | Geophysical investigation | Geophysical investigation | As per relevent standard specification | 5000 | EA | 5000
2 |  | 90 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work.Drilling-165mm Bore Well 0 to 90M | Drilling borewell | Drilling borewell | As per relevent standard specification | 336 | M | 30240
3 |  | 30 | Drill-165mm Bore Well 90M to 120M | Drilling borewell | Drilling borewell | As per relevent standard specification | 369 | M | 11070
4 |  | 30 | Drill-165mm Bore Well 120 M to 150M | Drilling borewell | Drilling borewell | As per relevent standard specification | 394 | M | 11820
5 |  | 1 | Drill-165mm Bore Well 150M to 180M | Drilling borewell | Drilling borewell | As per relevent standard specification | 492 | M | 492
6 |  | 20 | Suppy & fixing of 180 mm dia. 6 kg/cm2 PVC casing pipe including cost and conveyance of all materials labour charges etc complete for finished item of work. | PVC Casing | PVC Casing | As per relevent standard specification | 883 | M | 17660
7 |  | 130 | Supply and fixing of HDPE pipe 40mm dia. including cost and conveyance of all materials labour charges etc complete for finished item of work. | HDPE Pipe | HDPE Pipe | As per relevent standard specification | 180 | M | 23400
8 |  | 1 | Supply and Fixing of 1.5HP Texmo/Kirloskar make motor of single phase submersible of multiple stage including all materials and labour charges complete for finished item. | 1.5HP submersbile pump | 1.5HP submersbile pump | As per relevent standard specification | 29047 | EA | 29047
9 |  | 175 | Supply and fixing of 2.5mm single core copper cable complete for finished item. | Copper cable | Copper cable | As per relevent standard specification | 192 | M | 33600
10 |  | 1 | Supply and Fixing of Flange Clamps including cost and conveyance of all materials | Flange Clamps | Flange Clamps | As per relevent standard specification | 182 | EA | 182
11 |  | 1 | Supply and erecting D.O.L Starter 250V, Single phase, 50Hz with SS enclouser comprising of contactor with bi-metallic relay with necessary push buttons, transportation and all labour charges etc. complete. | Single phase starter | Single phase starter | As per relevent standard specification | 1040 | EA | 1040
12 |  | 30 | Hiring of JCB for site levelling and cleaning | Hiring of JCB | Hiring of JCB | As per relevent standard specification | 2165 | H | 64950
13 |  | 257.9 | Earth Work Mass Excavation to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water (either sub soil water, storm water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete | Earth Work Mass Excavation | Earth Work Mass Excavation | As per relevent standard specification | 486 | M3 | 125339.4
14 |  | 11 | Back Filling the foundation Columns, for lift wells ,Staircase foundation ,U.G Sump Septic tank, Road work ,storm water drain ,cable trench,soak pit and outside of hte reataining wall with the useful avilable excavated earth ,in layers not exceeding 150mm thick, conslidating each deposited layer by eatering and ramming including cost and conveyance of all materials labour chargess,hire charges of T&P,all leads and lifts etc,complete for finished item of work | Back Filling | Back Filling | As per relevent standard specification | 34 | M3 | 374
15 |  | 37 | Providing and laying Plain Cement concrete of (1:4:8) for levelling course using 40mm size hard broaken Granite stone including cost and conveyance of all materials, se HBG metal for foundations and leveling course, including cost and conveyance of all materials,seignorage, water, labour charges, hire charges of nachinery, at all levels, depths,heights and floors consolidation by watering ,ramming in layers,bailing of water if any, and removal of form work after completion of work curing for reqired number of days,all incidental charges etc complete for finished item of work. | PCC (1:4:8) 40mm metal | PCC (1:4:8) 40mm metal | As per relevent standard specification | 4887 | M3 | 180819
16 |  | 8 | Providing and laying Plain Cement Concrete of (1:2:4) with well graded machine crushed granite metal of 20mm nominal size from approved quarry for Bed Blocks, Hold Fasts including cost and conveyance of all materials, labour charges,hire charges of machnery,with all leads and lifts, for all floors curing for required number of days, all incidental charges etc complete for finished item work | PCC (1:2:4) 20mm metal | PCC (1:2:4) 20mm metal | As per relevent standard specification | 6304 | M3 | 50432
17 |  | 266 | CRS masonry in CM(1:6) using Hard Granite Stones including cost and conveyance of all materials, seignorage charges, labour charge for construction and for dressing stones to required size and shape, dewatering,scaffolding,cutting for all leads and lifts, all incidental charges etc .complete for finished item of work | CRS Masonary | CRS Masonary | As per relevent standard specification | 5018 | M3 | 1334788
18 |  | 744 | Supplying and filling with borrowed gravel, watering, ramming, consolidating thoroughly complying with the standard specification including cost and conveyance of all materials, labour charges,hire charges of machnery,with all leads and incidental charges etc complete for finished item work | filling with gravel | filling with gravel | As per relevent standard specification | 640 | M3 | 476160
19 |  | 5.2 | Reinforced Cement concerete M20 GRADE Nominal Mix for footings , columns, Beams and Slab using 12mm to 20mm size graded HBG machine crushed metal from approvaed quary giving cube crushing strenth of 20 N /sqmm and a minimum of 400 kgs of cement for 1 cum of concrete including cost and conveyance charges for cement and all other materials to site, scaffolding charge , seignorage charges, centering, shuttering, machine mixing,laying concrete, curing for specified number of days vibrating etc compaction by pen vibrator or needle vibrator supplemented by hand spreeding rodding and tamping ,all incident and operational charges , all leads and lifts and for all leaving gaps and pockets etc complete, but excuding cost of ssteel and its fabrication,all incidental charges etc .complete for finshed item of workA)Ground floora)Footings | RCC Footings | RCC Footings | As per relevent standard specification | 9357 | M3 | 48656.4
20 |  | 3.7 | b)Columns | RCC Columns | RCC Columns | As per relevent standard specification | 12579 | M3 | 46542.3
21 |  | 2.15 | c)Plinth beams | RCC Plinth beams | RCC Plinth beams | As per relevent standard specification | 12002 | M3 | 25804.3
22 |  | 2.71 | d)Roof beams | RCC Roof beams | RCC Roof beams | As per relevent standard specification | 11965 | M3 | 32425.15
23 |  | 0.55 | e)Lintels | RCC Lintels | RCC Lintels | As per relevent standard specification | 12573 | M3 | 6915.15
24 |  | 3.4 | f)Sun shade 0.6m width 3" thick | RCC Sunshades | RCC Sunshades | As per relevent standard specification | 1306 | M2 | 4440.4
25 |  | 13.02 | g)Slab | RCC Slab | RCC Slab | As per relevent standard specification | 11035 | M3 | 143675.7
26 |  | 105 | Brick masonry for wall in superstructure (230mm thick) in CM 1:6 using traditional Local madeSecound Class Bricks from approved sourse and quality having crushing strength of not less than 100 Kg/sq cm and water absorption not exceeding 20% by weight including cost and conveyance of all mateerials, seigniorage charge, all labour charges, curing for number of days as specified, for all leads, lifts scaffolding chargess, at all heght levels and floors all incidental charges etc completed item of work. A)Ground floor | Brick masonary | Brick masonary | As per relevent standard specification | 8182 | M3 | 859110
27 |  | 3.1 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) / Mild steel (MS) steel bars (Fe 415/ Fe 500 grade as per IS 1786-1979) of different diameters for RCC works , including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying including sales and other taxes on all materials etc.,complete for finished item of work | HYSD Steel | HYSD Steel | As per relevent standard specification | 78657 | MT | 243836.7
28 |  | 1193 | Providing plastering of 20mm thick to all uneven faces of walls and ceiling of superstructure in two coats with base coat in CM 1:5of 16mm thick and top coat in Cm 1:3 4mm thick with dubara sponge finish including cost and conveyance of all materials . water. all labour charges, curing for specified number of days, cutting grooves, at allheghits, level and floro, all leads, lifts and scaffolding charges, all incidental and scaffolding charges, seigniorage charges, all incidental charges etc. complete for finished item of work A)Ground floor | Plastering 20mm thick | Plastering 20mm thick | As per relevent standard specification | 498 | M2 | 594114
29 |  | 351 | Raised pointing in CM(1:3) including curing, cost and conveyance of all materials and labour charges for complete item of work. | Raised pointing | Raised pointing | As per relevent standard specification | 113 | M2 | 39663
30 |  | 64.05 | Providing impervious coat over RCC roof slab surfaces to requried slopes with 20mm thick in CM 1:3 pro mixed with approved brand of water proofing compound as the rate of 1 kg per bag of cement including cost and conveyance of all materials, water, all labour charges, chemicals, curing for specifed number of days,rounding off junctions of wall and slab, all leads, lifts, heights,levels and floors etc.complete for finished item of work. | impervious coat | impervious coat | As per relevent standard specification | 524 | M2 | 33562.2
31 |  | 15 | Providing Reinforced cement Drop Walls in CM 1:2 of 40mm thick over rabbit wire mesh including cost and conveyance of all meterials, labour charges, curing for specified number of days,at all levels, floors, height, leads and lifts, seignioage charges all incidental charges etc . complete, but excluding cost of steel as per the approved drawing for finished item of work | RCM Drop Walls | RCM Drop Walls | As per relevent standard specification | 2953 | M2 | 44295
32 |  | 6 | Supply and fixing of doors with the frames of the door shall be made well seasoned MT wood of cross section 100x75mm. The shutter shall be made ISI mark flushed door with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary on both sides with 3 no 150mm hinges, 1 no door stoper, 1 no 250mm aldrop, 1 no 300 mm tower bolts, 2 no 150mm door handlers of MS Powder coated, including cost and conveyance of the meterials,fixing,labour carges,tools,handles,locking arrangementts and other fixtures & fittings for finished item work | MT Wood Doors Shutter with frame | MT Wood Doors Shutter with frame | As per relevent standard specification | 7314 | M2 | 43884
33 |  | 5.8 | S&F-UPVC Sliding Windows of approved make including cost and coveyance of all mateirals with all leads and lifts, labour charges, painting charges complete for finished item of work | UPVC Sliding Windows | UPVC Sliding Windows | As per relevent standard specification | 6063 | M2 | 35165.4
34 |  | 6.8 | Supplying and fixing of MS safety grill with peripheral frame of ISA 25x25x4mm and 8mm square rods at 100mm c/c both in horizontal & vertical direction including cost and coveyance of all mateirals with all leads and lifts, labour charges, painting charges complete for finished item of work | MS safety grill | MS safety grill | As per relevent standard specification | 2990 | M2 | 20332
35 |  | 3.7 | Flooring with ceramic tiles of 1st class quality of approved brand shade and design of different size laid over a floor bed of CM 1:3 of 12 mm thick base coat and neat grey cement slurry of honey like consistancy spread at the ratet of 3.3 kg of cement per sqm and pointed to full deapth, (joints must be flushed) with white cement paste mixed with pigment when requied including cost and conveyance of cement and all materials ,labour charges, at all levels, heights and floors,curing etc. complete for finished item of work. | ceramic tiles flooring | ceramic tiles flooring | As per relevent standard specification | 844 | M2 | 3122.8
36 |  | 14.4 | Providing skirting to internal walls to 15 cm height/risers of steps with ceramic tile length equal to floor tile, set over base coat of CM (1:3) 12 mm thick with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointed with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like Shahabad stone, cement, sand and water etc., complete for finished item of work | ceramic tiles dadoing | ceramic tiles dadoing | As per relevent standard specification | 979 | M2 | 14097.6
37 |  | 40 | Flooring with polished shabads stone quality and approved size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and pointing with cement, labour etc, complete | Polished Shabad stone flooring | Polished Shabad stone flooring | As per relevent standard specification | 730 | M2 | 29200
38 |  | 5.3 | Skirting with polished shabads stone quality and approved size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and pointing with cement, labour etc, complete | Polished Shabad stone Skirting | Polished Shabad stone Skirting | As per relevent standard specification | 808 | M2 | 4282.4
39 |  | 106 | Painting in all floors as specified with two coats of Plastic emulation paint of approved colour make and shade over one coat of white primer including cost and conveyance of all materials, labour charges at all leads, lifts, hights, levels and floors,all incidental charges etc. complete for finished item of work . | Plastic emulsion | Plastic emulsion | As per relevent standard specification | 155 | M2 | 16430
40 |  | 1095 | Painting to External Faces of walls(outside) in all floors as specified with two coats of ACE or equivalent quality paint of approved colour make and shade over one coat of white cement primer including cost and conveyance of all materials, labour charges at all leads, lifts, hights, levels and floors,all incidental charges etc. complete for finished item of work . | ACE painting | ACE painting | As per relevent standard specification | 259 | Sqm | 283605
41 |  | 402.1 | Providing and applying Surya Cem of three coats of approved brand and shade to give an even shade after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, incidental, labour charges etc. complete for finished item of work | Surya cem 3coats | Surya cem 3coats | As per relevent standard specification | 85 | M2 | 34178.5
42 |  | 2 | Conducting of DGPS & Total Staion Survey and Providing of maps including preparation of boundary and contour levels with 2 Nos hard copies and soft copies complete for finished items of work as directed by the Engineer in charge of the work. | Total Station Survey | Total Station Survey | As per relevent standard specification | 5000 | EA | 10000
43 |  | 54.5 | Supply&Spreading ofHBG metal 20 mm size of 80mm thick including cost&conveyance labour charges etc complete for finished item of work | 20mm HBG metal | 20mm HBG metal | As per relevent standard specification | 1672 | Cum | 91124
44 |  | 114 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 1") of 2.8mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) including cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work. | MS Security fencing | MS Security fencing | As per relevent standard specification | 2310 | Sqm | 263340
45 |  | 7.5 | Supply&Fixing of R.C.C hume pipe of 450 mm dia including cost & conveyance of all materials labour charges etc complete for finished item of work. | RCC hume pipes | RCC hume pipes | As per relevent standard specification | 1474 | Rmt | 11055
46 |  | 40 | Supply and fixing 25mm dia 1.5mm thick recessed( concealed) PVC pipe alog with reinforcement to be laid in slab including No 14 SWG GI wire for earth contunity, cost of pipe, binding wire and all labour charges etc complete | concealed PVC casing | concealed PVC casing | As per relevent standard specification | 97 | M | 3880
47 |  | 30 | Supplying and fixing of 25mm dia 1.5mm thick PVC conduit pipe conceald in wall with all required accessories with No 14 SWG wire for earth conitunity including chisiling the wall whereever necessary, including masonary work and all labour charges complete. | concealed PVC casing | concealed PVC casing | As per relevent standard specification | 108 | M | 3240
48 |  | 15 | Wiring with 2X1.0 Sqm(14/.3mm) PVC insulated flexiable copper cable in the existing metalic/Non metalic conduit pipe with 6A modular SP switch, mounted on metalic box covereds with appropriate front plate modules etc ceiling rose including cot and conveyance of all mateials, labour charges complete for light points, bell points exhaust fan points in non residential builsing except circuit moving finished in all types masonary as directed by department (Anchor Roma/GM/HAVELLS/FINOLEX) | light points | light points | As per relevent standard specification | 642 | EA | 9630
49 |  | 6 | Supplying and erection of approved make 6 Amps one modular SP switch with 6 Amps 6 pin mudular type plug socket mounted on metallic box covered with appropriate front plate as including all labour and material charges etc., complete for finished item of work. | 6 A sockets | 6 A sockets | As per relevent standard specification | 542 | EA | 3252
50 |  | 30 | supplying and run of 2 of 14/0.3 mm(1.0 sqmm) PVC insulated flexiable copper cable in existing conduit pipe for run of mains including all labour charges and materials chages etc. complete. (FINOLEX/HAVELS) | 1.0 sqmm wiring | 1.0 sqmm wiring | As per relevent standard specification | 56 | M | 1680
51 |  | 120 | supplying and run of 2 of 28/0.3 mm(2.5 sqmm) PVC insulated flexiable copper cable in existing conduit pipe for run of mains including all labour charges and materials chages etc. complete. (FINOLEX/HAVELS) | 2.5 sqmm wiring | 2.5 sqmm wiring | As per relevent standard specification | 103 | M | 12360
52 |  | 1 | Supply and fixing of 12 way SPN Distribution board with IP-20 protection suitable for single phase 40A DP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 6Nos as out going including connections and all labour charges concealed in wall by chiseling and masonaqry work etc complete. | 12 way SPN Distribution | 12 way SPN Distribution | As per relevent standard specification | 6394 | EA | 6394
53 |  | 8 | Supply and erecting of approved make crom/bajaj make as directed by department 1x40W patty type fluorscent fitting made of CRCA sheet,completed with polyster filled 40W.choke,starter and side holders etc.complete with 40W tube all lobour charges etc complete (PHILIPS/CROMPTON) | tube lights | tube lights | As per relevent standard specification | 755 | EA | 6040
54 |  | 4 | Supply and fixing of batten holder/slanting holder in lieu of ceiling rose of light point complete with all connections and all labour charges with 11 to CF2 etc complete.(PHILIPS/CROMPTON) | batten holder | batten holder | As per relevent standard specification | 141 | EA | 564
55 |  | 2 | Supply and errection ceiling fan of selected colour and delux model high breeze with 3 blades and double ball bearing and with condenser AC 250 V 50 C/S of 48" 600 mm sweep completed erected in position with resistance type regulator, canopy down rod upto 304.8 mm in length is provided with hook/clamps nuts and bolts and 24/0.2 flexible copper wire etc.,complete and pointed with lettering by enamel paint the Sr.No and date of erection including cost and conveyance of all labour charges (Almonard/CG/Khaitan/Bajaj) and as per the direction of Engineer in charge. | ceiling fan | ceiling fan | As per relevent standard specification | 2277 | EA | 4554
56 |  | 2 | Supply and fixing of Electronic Regulator of Modular of GM / Legrand Myrius / L & T / North West / Indo Simon / ABB /Schneider ZEN celo including cost and conveyance of all labour charges and as per the direction of Engineer in charge. | Regulator for ceiling fan | Regulator for ceiling fan | As per relevent standard specification | 589 | EA | 1178
57 |  | 1 | Providing independent earthing for sophisticated equipment like computer, medical equipment electronic gadgets etc with 600X600X3.15mm thick copper plate rigidly fixed to the 40mm dia GI pipe 2.5m long pipe and 19mm dia B class GI pipe of .3 mts long connectd with reducer providing of stggred holes of 16 Nos of 12 mm dia to earth electrode, enclosed in in a CC chamber of (400X400X400) mm with suitable reinforced RCC slab cover duly filling with betonite powder and clay in (1:6) prop from bottom of pipe to bottom of CC chamber giving earth connection from the electrode throuh necessary GI strip of 25X6X200 mm length provided with suitable size o 14 Nos holes GI washers nuts and bolts and all labour charges etc complete. | earthing | earthing | As per relevent standard specification | 5345 | EA | 5345
58 |  | 40 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)a)15.90mm OD Pipe - SDR 11 | 15.90mm OD CPVC pipes & fittings | 15.90mm OD CPVC pipes & fittings | As per relevent standard specification | 239 | M | 9560
59 |  | 80 | b) 22.20mm OD Pipe - SDR 11 | 22.20mm OD CPVC pipes & fittings | 22.20mm OD CPVC pipes & fittings | As per relevent standard specification | 313 | M | 25040
60 |  | 90 | c) 28.60mm OD Pipe - SDR 11 | 28.60mm OD CPVC pipes & fittings | 28.60mm OD CPVC pipes & fittings | As per relevent standard specification | 410 | M | 36900
61 |  | 20 | S & F Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type a) 20 mm NB Size | 20mm Ball valve | 20mm Ball valve | As per relevent standard specification | 331 | EA | 6620
62 |  | 2 | b) 25 mm NB Size | 25mm Ball valve | 25mm Ball valve | As per relevent standard specification | 466 | EA | 932
63 |  | 20 | Supply and Fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand including cost and conveyance, labour charges of all materials etc. complete for finished item of work. | 110mm PVC/SWR pipe | 110mm PVC/SWR pipe | As per relevent standard specification | 462 | M | 9240
64 |  | 2 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) including cost and conveyance, labour charges of all materials etc. complete for finished item of work. | 110mm PVC/SWR Plain bend | 110mm PVC/SWR Plain bend | As per relevent standard specification | 96 | EA | 192
65 |  | 2 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) including cost and conveyance, labour charges of all materials etc. complete for finished item of work. | 110mm PVC/SWR door bend | 110mm PVC/SWR door bend | As per relevent standard specification | 128 | EA | 256
66 |  | 2 | Supply & fixing of Floor Trap (Bell Mouth ) 110 mm - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) including cost and conveyance, labour charges of all materials etc. complete for finished item of work. | 110mm PVC/SWR floor trap | 110mm PVC/SWR floor trap | As per relevent standard specification | 269 | EA | 538
67 |  | 2 | Supply&fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) including cost and conveyance, labour charges of all materials etc. complete for finished item of work. | 4" Nahany trap | 4" Nahany trap | As per relevent standard specification | 134 | EA | 268
68 |  | 1 | Constructing 457.2 mm x 457.2 mm (1'6"x1'6") brick in CM 1:6 prop. Masonry. Inspection chamber up to 914.4 mm (3'0") and fitted with light weight 457.2 mm x 457.2 mm (1'6"x1'6") C.I frame and cover of 20 Kg. | (1'6"x1'6") brick inspection chamber | (1'6"x1'6") brick inspection chamber | As per relevent standard specification | 4610 | EA | 4610
69 |  | 1 | Supplying and Fixing European Water Closet of 1st quality conforming to IS:2556-Part-2-1973 of Hindustan / Neycer or Parryware make white glazed with 'S' trap including cost and conveyance, labour charges etc complete. | European Water Closet | European Water Closet | As per relevent standard specification | 2228 | EA | 2228
70 |  | 2 | Supplying and fixing of best indian make plastic seat and lid for European water closets and buffers as per IS 2548-1963 | plastic seat and lid for EWC | plastic seat and lid for EWC | As per relevent standard specification | 1324 | EA | 2648
71 |  | 2 | Supply and fixing of PVC low level system parryware/slim line with internal component and short bend of 10 lits capacity with choice color etc., complete. | PVC low level tank | PVC low level tank | As per relevent standard specification | 2032 | EA | 4064
72 |  | 2 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Hand wash basin | Hand wash basin | As per relevent standard specification | 1717 | EA | 3434
73 |  | 2 | Suplying and fixing of angle stop cock 12.7mm dia fisrt quality indian make seiko or equivalent. | 12.7mm stop cock | 12.7mm stop cock | As per relevent standard specification | 721 | EA | 1442
74 |  | 2 | Suplying and fixing of bib tap 12.7mm dia fisrt quality indian make seiko or equivalent. | 12.7mm bib tap | 12.7mm bib tap | As per relevent standard specification | 298 | EA | 596
75 |  | 1000 | Providing and placing on terrace (at all floor levels) Sintex /Aqua tech or equivalent Polyethylene water storage tank double layer conforming to ISI 12701/96 mark with lid and suitable locking arraqngments and making necessary holes for inlet and outleta and over flow pipes labour charges etc complete for finished item of work. | PVC Sintex tank | PVC Sintex tank | As per relevent standard specification | 10 | L | 10000
76 |  | 1 | Suplying and fixing of 31.75mm PVC waste pipe for wash basin including cost and conveyance of all materials and labour charges et complete | PVC waste pipe | PVC waste pipe | As per relevent standard specification | 33 | EA | 33
77 |  | 1 | Supplying and fixing of TV shape mirror with plastic size 609mmX 457.2 m | TV shape mirror | TV shape mirror | As per relevent standard specification | 564 | EA | 564
78 |  | 1 | Constructing 1220.0 mm (4’0”) dia Septic tank with CC collars/rings including excavating pit up to a depth of 1800 mm (6'-0") in all sorts of soils (excluding rock), laying cement concrete (1:4:8) 150 mm thick using 40mm HBG Metal, Plastering 20mm thick for jointing CC collars and Providing M-20(Nominal mix) grade 3" thick RCC cover and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site and all incidental and operational, labour charges etc., complete for finished item of work as directed by the Engineer in charge. | 4’0” dia Septic tank | 4’0” dia Septic tank | As per relevent standard specification | 8215 | EA | 8215
79 |  | 1 | Constructing 1220.0 mm (4’0”) dia Soak pit with reinforced brick masonary(honey-comb wall) including excavating pits up to a depth of 1500 mm (5'-0") in all sorts of soils (excluding rock) as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site and all incidental and operational, labour charges etc., complete for finished item of work as as directed by the Engineer in charge. | 4’0” dia Soak pit | 4’0” dia Soak pit | As per relevent standard specification | 5560 | EA | 5560
80 |  | 1 | Supply of steel table of size 4'x2.'x30" with 18 mm plywood fixed with rubber beeding with drawers on right side with automatic locking arrangements etc copmlete. | steel table | steel table | As per relevent standard specification | 7800 | Each | 7800
81 |  | 2 | supply of 'S' type chair with arms teakwood frame with seat back 's' type on G.I pipe.(Make: Godraj) | S type chairs | S type chairs | As per relevent standard specification | 3650 | Each | 7300
82 |  | 2 | Supply of P V C chairs of approved quality & make incldg cost etc complete | PVC Chairs | PVC Chairs | As per relevent standard specification | 1150 | Each | 2300
83 |  | 15 | S&F ACP Vinyl Sign Board with MS Frame | Name boards | Name boards | As per relevent standard specification | 584 | FT2 | 8760
84 |  | 1.62 | Supply and Fixing of Substation name board of size 6'x3' iron sheet with angle frame and channel supports of size 75x40mm, 8' height including concreting of channel supports and painting with enamel paint complete. | Name boards | Name boards | As per relevent standard specification | 4326 | Sqm | 7008.12
85 |  | 76.89 | Seigniorage Charges - Sand | Seigniorage Charges | Seigniorage Charges |  | 40 | M3 | 3075.6
86 |  | 76.89 | Seigniorage Charges -M Sand | Seigniorage Charges | Seigniorage Charges |  | 97.5 | M4 | 7496.78
87 |  | 412.43 | Seigniorage Charges - Metal | Seigniorage Charges | Seigniorage Charges |  | 97.5 | M3 | 40211.925
88 |  | 744 | Seigniorage Charges - Garvel | Seigniorage Charges | Seigniorage Charges |  | 30 | M3 | 22320
[8 empty] | Civil total | 5676599.825
[8 empty] | Elec & civil total | 22848359.775

## 14. Medipally SS
Medipally Eelectrical Schedule (WBS.No: S-1702-14-06-01-02-001)
Name of the work :- The Proposal envisages for erection of 33/11KV Sub-station with 2 X 8.0 MVA Power Transformer with 5No's 11kV feeders at Medipally village in Medipally Mandal in operation Narapally Section in Ghatkesar Sub-Division in Keesara Division of Habsiguda Circle, Medchal-Mallakajigiri District.
Sl.No | SAP Code | Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR11041 | 25 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) for 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") | Labour | Exc of Hard pit w/o blast 0.92X0.92X2.3M | As per relevent standard specification | 1466.25 | EA | 36656.25
2 | SWR11039 | 30 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) for 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Labour | Exca Hard pit w/o blast 0.76X0.76X1.83M | As per relevent standard specification | 928 | EA | 27840
3 | SWR10343 | 10 | Erection of 9.1 M long PSCC pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Labour | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 24000
4 | SWR10356 | 5.4 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. | Labour | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 35526.6
5 | SWR10348 | 45 | Erection of R.S. Joists 150 x 150 mm pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Labour | Erection of RS Joist 150 x 150 mm | As per relevent standard specification | 1952.61 | EA | 87867.45
6 | SWR10356 | 47.25 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. | Labour | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 310857.75
7 | SWR10868 | 27.9 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, hannels,R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site,including erection. | Labour | Fabrication of struc.with power drilling | As per relevent standard specification | 6852 | TO | 191170.8
8 | SMR40010 | 31 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before rection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete for Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Supply of Materials | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 40083
9 | SWR10879 | 31 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before rection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete for Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Labour | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 14942
10 | SWR21240 | 6 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt) | Labour | Hoisting post ins&hrd wr 1panther 33kv | As per relevent standard specification | 781 | EA | 4686
11 | SWR21241 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Labour | Hoisting post ins&hrd wr 1panther 11kv | As per relevent standard specification | 507 | EA | 1014
12 | SWR10884 | 65 | Connection of equipment to bus and or another equipment with single zebra/ Panther conductor including measuring,cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Labour | Conn. of equip/bus single zebra/panther | As per relevent standard specification | 224 | EA | 14560
13 | SMR40011 | 45 | Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating | Supply of Materials | Sup T clamp LM6 Al alloy of 12 mm, 800 A | As per relevent standard specification | 299 | EA | 13455
14 | SMR11915 | 18 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | Supply of Materials | S-Tension HW 3Bolt 1Zebra/Pnthr 150mm | As per relevent standard specification | 2055 | SET | 36990
15 | SMR40039 | 12 | Supply of Bimetalic Copper die clamps suitable for power ransformer/ Lclamps HV of 1/2 inch bush rod and other end suitable for panther conductor and with bimetallic sheet on the pad of size 75X75X10mm with four holes of 14mm diameter (hole to hole distance 40mm) with suitable GI bolts and nuts including washers | Supply of Materials | Sup Bimetalic Copper die clamps for PTR | As per relevent standard specification | 909 | EA | 10908
16 | SMR40030 | 6 | Supply of Alluminum Post type insulator suupport clamps conforming to A6 of IS 617, with hot dip alvanised bolts and nuts suitable for 11 kV | Supply of Materials | SupPost type insulator suupp clamps 11kV | As per relevent standard specification | 381 | EA | 2286
17 | SMR22473 | 12 | Supply of I-Bolts clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367- 1961) | Supply of Materials | Supply of I-Bolts | As per relevent standard specification | 294 | EA | 3528
18 | SWR10423 | 12 | Fixing of I-bolts clamps | Labour | Fixing of I-bolts | As per relevent standard specification | 20 | EA | 240
19 | SMR40023 | 33 | Supply of CT stud clamps with hot dip galvanised bolts and nuts suitable for zebra / Panther conductor on one side and 28/30/40 mm CT stud on other side with stud size for single zebra / panther (4 bolted) with bimetallic sleeve for carrying 800 A | Supply of Materials | Sup CT stud clamps 1Zebra/Panth for 800A | As per relevent standard specification | 399 | EA | 13167
20 | SMR40019 | 54 | Supply of Alluminum alloy Pad clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR/Zebra of pad size 100 X 100 X 15mm for carrying 600 A current rating . | Supply of Materials | SupPad clamps 100X100X15 mm 1 panth 600A | As per relevent standard specification | 264 | EA | 14256
21 | SMR40027 | 33 | Supply of Alluminum LA clamps conforming to A6 of IS 617, with hot dip galvanised bolts and nuts suitable for single zebra / Panther | Supply of Materials | Sup LA clamps for single zebra / Panther | As per relevent standard specification | 357 | EA | 11781
22 | SWR10917 | 75 | Labour for Fixing of all types of clamps | Labour | Labour for Fixing of all types of clamps | As per relevent standard specification | 65 | EA | 4875
23 | SWR10392 | 8 | Erection of 33 KV AB Switch including alignment and earthing | Labour | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 36000
24 | SWR10393 | 17 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Labour | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 54400
25 | SWR10881 | 23 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Labour | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 3266
26 | SWR23224 | 63.76 | Excavate-Pit for 33KV VCB | Labour | Excavate-Pit for 33KV VCB | As per relevent standard specification | 331 | M3 | 21104.56
27 | SWR20685 | 67 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Labour | Cement concrete with 40MM metal VCB plin | As per relevent standard specification | 5160 | M3 | 345720
28 | SWR10461 | 7 | Erection of 11 KV VCB with Control Panel AB Switches, VCBs, LAs, PTs, CTs, DTRs etc | Labour | Erection of 11kv VCB | As per relevent standard specification | 12000 | EA | 84000
29 | SWR10460 | 3 | Erection of 33 KV VCB with Control Panel AB Switches, VCBs, LAs, PTs, CTs, DTRs etc | Labour | Erection of 33kv VCB | As per relevent standard specification | 12500 | EA | 37500
30 | SMR40045 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification | Supply of Materials | Supply of AC Supply panel complete | As per relevent standard specification | 42000 | EA | 42000
31 | SWR20025 | 1 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | Labour | 33/11kv S.S Erection of AC&DC Panel | As per relevent standard specification | 7871.85 | SET | 7871.85
32 | SWR11166 | 1 | Loading of 220 V Batterry with charger | Labour | Loading 220 V Battery with Charger | As per relevent standard specification | 1612 | SET | 1612
33 | SWR11147 | 1 | Un loading of 220 V Batterry with charger | Labour | Un-loading 220 V Battery with Charger | As per relevent standard specification | 1024 | SET | 1024
34 | SWR11772 | 1 | Erection-220V Batery with Chrgr incl all-SS | Labour | Erect-220V Batery with Chrgr incl all-SS | As per relevent standard specification | 6442.58 | EA | 6442.58
35 | SWR10402 | 2 | Erection of 11 KV three phase PTs | Labour | Erection of 11kv three phase PT s | As per relevent standard specification | 800 | SET | 1600
36 | SWR10396 | 2 | Erection of 33 KV LAS station/Line type including earthing | Labour | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 1760
37 | SWR20976 | 2 | Erection of 33kv LA-3Nos Line type | Labour | Erection of 33kv LA-3Nos Line type | As per relevent standard specification | 880 | SET | 1760
38 | SWR10397 | 2 | Erection of 11 KV LAS station type including earthing | Labour | Erect of 11kv LA stn type incl earthing | As per relevent standard specification | 559 | SET | 1118
39 | SWR10357 | 32 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Labour | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 39494.4
40 | SWR10359 | 32 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Labour | ERECT. OF LINES-Providing of RCC collar | As per relevent standard specification | 386 | EA | 12352
41 | SWR10920 | 800 | Laying of 75x 8mm MS Flat / GI Flat. earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication. | Labour | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 52000
42 | SWR10919 | 1200 | Fabrication and M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) connecting to risers from earth mat to structures, equipment,marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Labour | Earthing for raisers of SS Flat 50x6 mm. | As per relevent standard specification | 41 | RMT | 49200
43 | SWR11880 | 440 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Labour | Lay-Cable Terminations to Switchgear | As per relevent standard specification | 34.43 | EA | 15149.2
44 | SMR11594 | 14 | Supply of 90W LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE / CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA.LED MAKE: PHILIPS REE/NICHIA/OSRAM/ SUMSANG/ LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty | Supply of Materials | S-90W LED fixture set | As per relevent standard specification | 8200 | EA | 114800
45 | SWR20028 | 14 | Supply and Fixing of junction box and Providing with proper Fuse protection and required glauds suitable for Cable Terminations. The box shall be fixed on the pole. | Labour | 33/11kv S.S Yard lighting junction box | As per relevent standard specification | 351.9 | EA | 4926.6
46 | SWR11879 | 3300 | Laying of 4 core/10 core 2.5 sq. mm. Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Labour | Lay-4C/10C 2.5Sqmm Control Cable | As per relevent standard specification | 27 | M | 89100
47 | SMR40049 | 3 | Supply of MS Powder coted PT Marshalling Box | Supply of Materials | Sup of MSPowder coted PT Marshalling Box | As per relevent standard specification | 4095 | EA | 12285
48 | SMR40072 | 12 | Supply of LC Boards | Supply of Materials | Supply of LC Boards | As per relevent standard specification | 116 | EA | 1392
49 | SMR40070 | 24 | Supply of Danger boards with clamps | Supply of Materials | Supply of Danger boards with clamps | As per relevent standard specification | 116 | EA | 2784
50 | SWR10963 | 12 | Painting of Name Plates for any equipment | Labour | Painting of Name Plates for any equipmen | As per relevent standard specification | 122 | EA | 1464
51 | SMR12488 | 500 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. | Supply of Materials | S-Hot dip gal./Zinc bolts & nuts washer | As per relevent standard specification | 90 | KG | 45000
52 | SWR10199 | 7 | Loading of 11 KV VCBs along with Panel boards | Labour | LOADING of 11 KV VCBs&Panel boards | As per relevent standard specification | 1024 | EA | 7168
53 | SWR10198 | 3 | Loading of 33 KV VCBs along with Panel boards | Labour | LOADING of 33 KV VCBs&Panel boards | As per relevent standard specification | 1024 | EA | 3072
54 | SWR10516 | 3 | Un loading of 33 KV VCBs along with Panel boards | Labour | UNLOADING of 33 KVVCBs&Panel boards | As per relevent standard specification | 1044.48 | EA | 3133.44
55 | SWR10517 | 7 | Un loading of 11 KV VCBs along with Panel boards | Labour | UNLOADING of 11 KVVCBs&Panel boards | As per relevent standard specification | 1044.48 | EA | 7311.36
56 | SWR10940 | 3 | Erection of Marshalling boxes | Labour | Erection of Marshalling boxes | As per relevent standard specification | 374.85 | EA | 1124.55
57 | SWR10401 | 1 | Erection of 33 KV single phase PTs AB Switches, VCBs, LAs, PTs, CTs, DTRs etc | Labour | Erection of 33kv single phase PT s | As per relevent standard specification | 1079 | SET | 1079
58 | SWR10402 | 2 | Erection of 11 KV three phase PTs AB Switches, VCBs, LAs, PTs, CTs, DTRs etc | Labour | Erection of 11kv three phase PT s | As per relevent standard specification | 800 | SET | 1600
59 | SWR10132 | 34.7 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading | Labour | TRANSPORT OF STEEL 10 TO 20KM | As per relevent standard specification | 412.08 | TO | 14299.18
60 | SWR10206 | 34.7 | Loading of M.S.Channels, Angles, Flats & Rods etc. | Labour | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 7668.7
61 | SWR10524 | 34.7 | Un loading of M.S.Channels, Angles, Flats & Rods etc. | Labour | UNLOADING of MS annel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 6419.5
62 | SWR10238 | 15 | Loading of 11KV AB Switch Conventional type | Labour | LOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 1200
63 | SWR10239 | 8 | Loading of 33KV 800 Amps AB Switch Con 400/800 A | Labour | LOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 126 | EA | 1008
64 | SWR10264 | 6 | Loading of 11 KV, 10 KA LAs Station type | Labour | LOADING of 11 KV,10 KA LAs Station type | As per relevent standard specification | 32 | EA | 192
65 | SWR10266 | 9 | Loading of 33 KV, 10 KA LAs Station type | Labour | LOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 41 | EA | 369
66 | SWR10582 | 6 | Un loading of 11 KV, 10 KA LAs Station type | Labour | UNLOADING of 11 KV,10 KA LAs Station typ | As per relevent standard specification | 32 | EA | 192
67 | SWR10584 | 9 | Un loading of 33 KV, 10 KA LAs Station type | Labour | UNLOADING of 33 KV10 KA LAs Station type | As per relevent standard specification | 35 | EA | 315
68 | SWR11701 | 3500 | Loading of PVC Control Cable 10 Core | Labour | Load-PVC Control Cable 10C | As per relevent standard specification | 1 | M | 3500
69 | SWR11712 | 3500 | Un loading of PVC Control Cable 10 Core | Labour | UnLoad-PVC Control Cable 10C | As per relevent standard specification | 1.02 | M | 3570
70 | SWR10556 | 15 | Un loading of 11KV AB Switch Conventional type Con 200/400 A | Labour | UNLOADING of 11 KV AB SWCH Con 200/400 A | As per relevent standard specification | 80 | EA | 1200
71 | SWR10557 | 8 | Un loading of 33KV 800 Amps AB Switch Con 400/800 A | Labour | UNLOADING of 33 KV AB SWCH Con 400/800 A | As per relevent standard specification | 79 | EA | 632
72 | SMR12239 | 3 | Supply Neutral link for PT Marshalling Box for indoor SS | Supply of Materials | S-Neutral Link for PT Marshl Box | As per relevent standard specification | 385 | EA | 1155
73 | SWR11417 | 2 | Earthing of arrangement labour for PTR Neutral | Labour | Earthing arangemnt labour for PTRNeutral | As per relevent standard specification | 838 | EA | 1676
74 | SWR34621 | 4 | S&F-Nylon Neutral Link Base | Labour | S&F-Nylon Neutral Link Base | As per relevent standard specification | 106.25 | EA | 425
75 | SWR20308 | 10 | Sub-transport of 9.1 Mtrs long PSCC Poles upto Workspot upto 10KM (Including loading and unloading) | Labour | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 4072.9
76 | SWR10631 | 36 | Un loading of 33 & 11 KV Disc insulators | Labour | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | KI | 72
77 | SWR10618 | 2 | Loading of 33 KV Metal parts bag of 25no | Labour | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 130
78 | SWR12421 | 2 | Un loading of 11 KV Metal parts Bag | Labour | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 96
79 | SWR21321 | 2 | Erection of 8 MVA PTR. PTR on constructed plinth | Labour | Erec 33/11 KV, 8 MVA PTR as per Spec | As per relevent standard specification | 49480.2 | EA | 98960.4
80 | SMR40051 | 14 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713 | Supply of Materials | Supply 9mtrs tubular poles single way | As per relevent standard specification | 13913 | EA | 194782
81 | SWR10955 | 14 | Errection of tubular poles | Labour | Errection of tubular poles | As per relevent standard specification | 1379 | EA | 19306
82 | SWR10956 | 14 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete | Labour | Fixing of LED/Metal halide complete. | As per relevent standard specification | 1268 | EA | 17752
83 | SWR10205 | 45 | Loading of R.S. Joists 150 x 150mm / Rail poles | Labour | LOADING of RSJoists150 x 150 mm/RailPole | As per relevent standard specification | 176 | EA | 7920
84 | SWR10523 | 45 | Un loading of R.S. Joists 150 x 150mm / Rail poles | Labour | UNLOADING of RSJoists150 x150 mm/RailPol | As per relevent standard specification | 107 | EA | 4815
85 | SWR10867 | 27.9 | Fabrication & erection of Channels Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | Labour | Alligning the Main/Aux. structures. | As per relevent standard specification | 1470 | TO | 41013
86 | SWR10873 | 500 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Supply of Materials | Supply,fabricati of 6mm Checkerd plates | As per relevent standard specification | 83 | KG | 41500
87 | SMR40017 | 8 | Supply of Tension clamps for earth wire 3 bolted | Supply of Materials | SupTension clamps for earthwire 3bolted | As per relevent standard specification | 715 | SET | 5720
88 | SMR40021 | 31 | Supply of Alluminum alloy Pad clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for twin panther ACSR/Zebra of pad size 100 X 100 X 15mm for carrying 1200 A current rating | Supply of Materials | SupPad clamps 100X100X15mm 2 panth 1200A | As per relevent standard specification | 284 | EA | 8804
89 | SMR40025 | 12 | Supply of Alluminum PT clamps conforming to A6 of IS 617,with hot dip galvanised bolts and nuts suitable for single zebra / Panther | Supply of Materials | Sup PT clamps for single zebra / Panther | As per relevent standard specification | 368 | EA | 4416
90 | SWR10404 | 200 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | Labour | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 65536
91 | SWR11893 | 1 | Erection of control/Relay panels, AC Panels, announciation panels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Labour | Erect-Contrl/Relay, AC, Announ. Panels | As per relevent standard specification | 2122 | EA | 2122
92 | SWR10856 | 21.6 | Excavation of Earth work excavtion hard rock boulders pits in hard rock not requiring blasting. (In hard murram / rock boulders) (other than SS) | Labour | Earth work excav hard rock bould <3cum | As per relevent standard specification | 1318.35 | M3 | 28476.36
93 | SWR10398 | 8 | Erection of 11 KV LAS line type including earthing AB Switches, VCBs, LAs, PTs, CTs, DTRs etc | Labour | Erect of 11kvLA line type incl earthing | As per relevent standard specification | 505 | SET | 4040
94 | SMR11482 | 32 | Supply of CI earthing pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Supply of Materials | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 111552
95 | SWR10263 | 32 | Loading of CI earth pipe 100 mm dia, 2.75 mt long | Labour | LOADING of CI Earth pipe upto 2.7 Mtr | As per relevent standard specification | 29 | EA | 928
96 | SWR10581 | 32 | Un loading of CI earth pipe 100 mm dia, 2.75 mt long | Labour | UNLOADING of CI Earth pipe upto 2.7 Mtr | As per relevent standard specification | 29 | EA | 928
97 | SWR12510 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Labour | L-Cable Termination to Switchgear | As per relevent standard specification | 27 | EA | 7290
98 | SWR22093 | 90 | Providing of control cable trench as per DATA-XII | Labour | Providing of cable trench as per DATA-IX | As per relevent standard specification | 3148 | RMT | 283320
99 | SWR21843 | 1 | RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA | Labour | Column type DTR Plinth topslab 4'x4'x6" | As per relevent standard specification | 25967.57 | EA | 25967.57
100 | SWR10195 | 1 | Loading of 50,63, 75 & 100 KVA DTR | Labour | LOADING of 50,63,75&100kva DTR | As per relevent standard specification | 350 | EA | 350
101 | SWR10513 | 1 | Un loading of 50,63, 75 & 100 KVA DTR | Labour | UNLOADING of 50,63,75&100kva DTR | As per relevent standard specification | 280 | EA | 280
102 | SWR10463 | 1 | Erection of 3 Ph DTRs upto 25KVA DTR's including loading and nloading DTR on the Structure/Plinth etc | Labour | Erection of Three Phase DTRs | As per relevent standard specification | 1139.95 | EA | 1139.95
103 | SWR11920 | 30 | Laying of 11KV 3x185 Sqmm XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. | Labour | Lay-SR 11KV 3x185sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 465.46 | M | 13963.8
104 | SWR11956 | 20 | Raising of 11 KV 3x185 Sqmm cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Labour | Raise-SR 11KV 3x185sqmm UG Cb on support | As per relevent standard specification | 126.23 | M | 2524.6
105 | SWR10390 | 2 | Making 11 KV 3x185 Sqmm Cable Out Door/Indoor end termination | Labour | OD/Idoor end termination 11kv 3x185 xlpe | As per relevent standard specification | 2370.63 | EA | 4741.26
106 | SWR10674 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs | Labour | Erection of LT distribution box | As per relevent standard specification | 1594.67 | EA | 1594.67
107 | SMR40044 | 1 | Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification | Supply of Materials | Supply of DC Anunc.relay panel 8 feeders | As per relevent standard specification | 42500 | EA | 42500
108 | SMR40048 | 3 | Supply of FRP PT Marshalling Box | Supply of Materials | Supply of FRP PT Marshalling Box | As per relevent standard specification | 4463 | EA | 13389
109 | SWR10942 | 10 | Testing of Sub-Station Equipment ''Wirring, commissioning and testing of Outdoor Sub-station switchgear duly conducting the pre commissioning test as per relevent standards & issue of certificate by CEIG authorised testing Engineer | Labour | Testing of Outdoor SS switchgear | As per relevent standard specification | 1825 | EA | 18250
110 | SWR10854 | 2 | Transport of 8MVA Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading ) | Labour | Transport of 8MVA power transformer | As per relevent standard specification | 21945 | EA | 43890
111 | SWR10613 | 2 | Loading of 8MVA PTR and unloading of PTR on constructed plinth | Labour | LOADING of 8 MVA PTR | As per relevent standard specification | 5805.84 | EA | 11611.68
112 | SWR10627 | 2 | Unloading of 8MVA PTR | Labour | UNLOADING of 8 MVA PTR | As per relevent standard specification | 5805.84 | EA | 11611.68
113 | SWR10944 | 2 | Testing of Sub-Station Equipment'' Testing of Power Transformer duly conducting the pre commissioning tests as per relevent standard & issue of certificate by CEIG authorised testing Engineer | Labour | Testing of Power Transformer. | As per relevent standard specification | 4000 | EA | 8000
114 | SMR11485 | 75 | Supply of GI Flat 25X3 mm earthing pipe with materials | Supply of Materials | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 7875
115 | SWR11923 | 90 | Laying of LT 3 1/2 x 185 Sqmm XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. | Labour | Lay-SR LT 3.5x185sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 377.63 | M | 33986.7
116 | SWR11959 | 10 | Raising of LT 3 1/2 x 185 Sqmm cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Labour | Raise-SR LT 3.5x185sqmm UG Cb on support | As per relevent standard specification | 85.43 | M | 854.3
117 | SMR40140 | 2 | Supply of 31/2x185Sqmm UG O/D end termination kits | Supply of Materials | Sup of 31/2x185Sqmm UG O/D end term kits | As per relevent standard specification | 550 | EA | 1100
118 | SWR10231 | 1 | Loading of 11 KV HG Fuse Sets | Labour | LOADING of 11 KV HG Fuse Sets | As per relevent standard specification | 18 | EA | 18
119 | SWR10549 | 1 | Un loading of 11 KV HG Fuse Sets | Labour | UNLOADING of 11 KV HG Fuse Sets | As per relevent standard specification | 18 | EA | 18
120 | SWR10395 | 1 | Erection of 11 KV HG Fuse set including earthing AB Switches, VCBs, LAs, PTs, CTs, DTRs etc | Labour | Erect. of 11kv HG Fuseset incl earthing | As per relevent standard specification | 740.52 | SET | 740.52
121 | SWR10765 | 2 | Supply & fixing of Oout Door/Indoor end termination LT 3 1/2 x 185 Sqmm Cable | Labour | OD/Idoor end termination LT 3 1/2 x 185 | As per relevent standard specification | 968.9 | EA | 1937.8
122 | SWR20102 | 1 | Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Labour | Erection of 11kv TT type AB switch | As per relevent standard specification | 1813.49 | EA | 1813.49
123 | SMR40032 | 3 | Supply of 11kv, 200Amps copper Flexible jumpers | Supply of Materials | Sup11kv, 200Amps copper Flexible jumpers | As per relevent standard specification | 131 | EA | 393
124 | SWR20032 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard | Supply of Materials | Sup &fix of board ind Switchyard layout | As per relevent standard specification | 1654 | EA | 1654
125 | SWR22090 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Supply of Materials | Sup& fix safety inst/SS Op. inst board | As per relevent standard specification | 2205 | EA | 2205
126 | SMR40059 | 1 | Supply of Wall clock standard make | Supply of Materials | Supply of Wall clock standard make | As per relevent standard specification | 578 | EA | 578
127 | SMR12378 | 1 | Supply of -10ft Aluminium Ladder | Supply of Materials | S-10ft Aluminium Ladder | As per relevent standard specification | 1654 | EA | 1654
128 | SMR40063 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19,20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make . | Supply of Materials | SupTaparia Tool kit complete as per Spec | As per relevent standard specification | 4925 | SET | 4925
129 | SMR40064 | 1 | Rechargeable LED torch light of Standard make | Supply of Materials | Sup Rechargeable LED torch light. | As per relevent standard specification | 1733 | EA | 1733
130 | SMR40061 | 1 | Supply of Steel almarah(61/2 X 3ft) Godrej | Supply of Materials | Sup Steel almarah(61/2 X 3ft) Godrej | As per relevent standard specification | 9818 | EA | 9818
131 | SMR40057 | 1 | Supply of Table (3x6ft) Godrej | Supply of Materials | Supply of Table (3x6ft) Godrej | As per relevent standard specification | 6050 | EA | 6050
132 | SMR40058 | 4 | Supply of type chairs (Godrej) | Supply of Materials | Supply of S type chairs (Godrej) | As per relevent standard specification | 924 | EA | 3696
133 | SMR40060 | 1 | Supply of Angle racks(18x36.6inches) Godrej | Supply of Materials | Sup Angle racks(18x36.6inches) Godrej | As per relevent standard specification | 1733 | EA | 1733
134 | SMR40065 | 1 | Supply of Hack saw (12 inches) | Supply of Materials | Supply of Hack saw (12 inches) | As per relevent standard specification | 289 | EA | 289
135 | SMR40066 | 4 | Supply of Earthing Rods (8ft) Screw & clamp type | Supply of Materials | Sup Earth Rods (8ft) Screw & clamp type | As per relevent standard specification | 578 | EA | 2312
136 | SMR40067 | 2 | Supply of Hand Gloves | Supply of Materials | Supply of Hand Gloves | As per relevent standard specification | 289 | SET | 578
137 | SMR40068 | 12 | Supply of Rubber mats ( 6’x3’) size for indoor SS | Supply of Materials | SupRubber mats( 6’x3’)size for indoorSS | As per relevent standard specification | 1386 | EA | 16632
138 | SMR40069 | 1 | Supply of Standard basic cell phone with charger | Supply of Materials | Sup Stand basic cell phone with charger | As per relevent standard specification | 1386 | EA | 1386
139 | SMR40088 | 1 | Supply of Fire bucket stand with 3 buckets (8 -10 ltr capacity) | Supply of Materials | Sup Fire Buckets Stand with Buckets | As per relevent standard specification | 1386 | SET | 1386
140 | SMR40089 | 2 | Supply of Room fire extinguisher (2 ltrs capacity) for control room | Supply of Materials | Sup Fire Extinguisher for Control Room | As per relevent standard specification | 4620 | EA | 9240
141 | SMR40087 | 4 | Supply of Trolley mounted CO2 (6.5Kgs) | Supply of Materials | Sup TrollyMounted Co2 Cylinders(IS-2878) | As per relevent standard specification | 9240 | EA | 36960
142 | SMR40071 | 6 | Supply of Safety Helmets of standard make | Supply of Materials | Supply of Safety Helmet of standard make | As per relevent standard specification | 231 | EA | 1386
143 | SMR40073 | 4 | Supply of Gum Boots (Pair) | Supply of Materials | Supply of Gum Boots | As per relevent standard specification | 693 | EA | 2772
144 | SMR40074 | 1 | Supply of 5000v megger | Supply of Materials | Supply of 5000v megger | As per relevent standard specification | 13860 | EA | 13860
145 | SMR40075 | 1 | Supply of Earth megger (1000v) | Supply of Materials | Supply of Earth megger (1000v) | As per relevent standard specification | 8085 | EA | 8085
146 | SMR40076 | 1 | Supply of Digital clamp meter. | Supply of Materials | Supply of Digital clamp meter. | As per relevent standard specification | 2888 | EA | 2888
147 | SMR40086 | 1 | Supply of Name board of the 33/11kV Sub-Station(As per Standard Specification) | Supply of Materials | Sup 33/11kv S.S Permanent name board | As per relevent standard specification | 10238 | EA | 10238
148 | SWR11890 | 1.395 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Labour | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893 | M3 | 5430.74
149 | SWR10743 | 45 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of coping with two coats of white cement (including cost of paint) | Labour | Painting of supports to a height of 0.3M | As per relevent standard specification | 686 | EA | 30870
150 | SMR40033 | 4 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral | Supply of Materials | SupCU Flexi jumper for Power T/F Neutral | As per relevent standard specification | 4725 | EA | 18900
151 | SWR10862 | 27.5 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Labour | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | As per relevent standard specification | 373 | M2 | 10257.5
152 | SMR22718 | 700 | S/o rail poles 90/105lb (250x2N) | Supply of Materials | S/o rail poles 90/105lb (250x2N) | As per relevent standard specification | 47.27 | KG | 33089
153 | SWR10344 | 4 | Erection of Rail Pole 90Lbs | Labour | Erection of Rail Pole 90Lbs | As per relevent standard specification | 3510 | EA | 14040
154 | SWR10877 | 31 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete.Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Labour | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 26381
155 | SWR11267 | 1 | Erection of Erect-12Meter Box pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Labour | Erect-12Meter Box pole | As per relevent standard specification | 3901.37 | EA | 3901.37
156 | SWR10107 | 1 | Excavation of 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum pits in all soils except hard rock requiring blasting | Labour | EXCAVATION OF PIT (2.6" x 2.6" x 6.0") | As per relevent standard specification | 700 | EA | 700
157 | SMR12302 | 17200 | Supply-RS Joist Grider Pole (150x150mm) | Supply of Materials | S-RS Joist Grider Pole (150x150mm) | As per relevent standard specification | 59.25 | KG | 1019100
158 | SMR25233 | 10 | Supply-PSCC Pole 9.1Mtr 280kg | Supply of Materials | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 31094.1
159 | SMR22745 | 10500 | Supply- MS Channel 100x50mm | Supply of Materials | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 603225
160 | SMR12321 | 4000 | Supply-MS Flat 75x8mm | Supply of Materials | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 225680
161 | SMR12322 | 3000 | Supply-MS Flat 50x6mm | Supply of Materials | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 169500
162 | SMR12315 | 8 | Supply-33KV 800A DB Break AB Switch | Supply of Materials | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 325270.24
163 | SMR12316 | 15 | Supply-11KV 800A DB Break AB Switch | Supply of Materials | S-11KV 800A DB Break AB Switch | As per relevent standard specification | 30847.46 | EA | 462711.9
164 | SMR12317 | 2 | Supply-11KV 400A DB Break AB Switch | Supply of Materials | S-11KV 400A DB Break AB Switch | As per relevent standard specification | 18150 | EA | 36300
165 | SMR25204 | 100 | Supply-LT XLPE Cable 3 1/2 C 185 sqmm | Supply of Materials | S-LT XLPE Cable 3 1/2 C 185 sqmm | As per relevent standard specification | 547 | M | 54700
166 | SMR12318 | 1 | Supply-11KV 200A Tilting Type AB Switch | Supply of Materials | S-11KV 200A Tilting Type AB Switch | As per relevent standard specification | 8991 | EA | 8991
167 | SMR12324 | 1 | Supply-11KV HG FuseSet for StationTransformer | Supply of Materials | S-11KV HG FuseSet for StationTransformer | As per relevent standard specification | 1974 | EA | 1974
168 | SMR25200 | 1 | Supply-LT Distribution Box (SMC) | Supply of Materials | S-LT Distribution Box (SMC) | As per relevent standard specification | 7797 | EA | 7797
169 | SWR22092 | 12.2 | survey line&cabl inc peg mark&tree clear | Labour | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 9333
170 | SMR11683 | 49 | Supply of M+3 Tower (Galvanized) | Supply of Materials | S-M+3 Tower GALV | As per relevent standard specification | 140674.3 | EA | 6893040.7
171 | SMR11684 | 49 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) | Supply of Materials | S-Mat. for Extn of M+3 Tower by 3M GALV | As per relevent standard specification | 28520.64 | EA | 1397511.36
172 | SWR11850 | 49 | Erection of M+3 Tower (Galvanized) | Labour | Erect- M+3 Tower GALV | As per relevent standard specification | 64576 | EA | 3164224
173 | SWR11851 | 49 | Erection of Extension of 3Mtrs for M+3 (Galvanized) | Labour | Erect-Extn of 3M for M+3 Tower GALV | As per relevent standard specification | 5168.95 | EA | 253278.55
174 | SWR20959 | 232.848 | Excavation of pits in hard rock requiring blasting (other than SS) Earth work excavation of pits in hard murram/rock boulders | Labour | Excavate-Earth in Hard Murram | As per relevent standard specification | 1530 | M3 | 356257.44
175 | SWR11041 | 32 | Excavation of pits for 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") in hard rock not requiring blasting. (In hard murram / rock boulders) | Labour | Exc of Hard pit w/o blast 0.92X0.92X2.3M | As per relevent standard specification | 1466.25 | EA | 46920
176 | SWR10978 | 64 | Erection of 11 Mtrs PSCC poles in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Labour | Errection of 11 M long PSCC pole | As per relevent standard specification | 4336.85 | EA | 277558.4
177 | SWR10356 | 48 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. | Labour | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 315792
178 | SWR10466 | 20 | Formation of Cut point for 33 KV Double circuit line excluding pole erection and stays | Labour | Formation of 33kvline vertical cutpoint | As per relevent standard specification | 3198.72 | EA | 63974.4
179 | SWR10366 | 9 | Paving out and stringing of 100 Sqmm Single Circuit (3 Conductors) conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location. | Labour | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 13856.7 | KM | 124710.3
180 | SWR10149 | 8.15 | Transport of steel including line materials such as cross arms, clamps, hardware, cable (loose) and other line materials (Including loading and unloading) above 20 KM and upto 30 KM | Labour | TRANSPORT OF STEEL MATERIAL 20 TO 30KM | As per relevent standard specification | 527.34 | TO | 4297.82
181 | SWR10206 | 8.15 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Labour | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 1801.15
182 | SWR10524 | 8.15 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Labour | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 1507.75
183 | SWR10211 | 480 | Loading of 33 KV Pin insulators | Labour | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | KI | 1440
184 | SWR10529 | 120 | Un loading of 33 KV Pin insulators | Labour | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | KI | 360
185 | SWR10618 | 8 | Loading of 33 KV Metal parts | Labour | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 520
186 | SWR11863 | 8 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) above 30 Km and upto 50 Km with Lorry for each trip | Labour | Transport of Cond Drum,VCBs >30 & <50Km | As per relevent standard specification | 4372.74 | EA | 34981.92
187 | SMR11488 | 600 | Supply of GI Bolts & Nuts etc | Supply of Materials | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 70500
188 | SWR11863 | 10 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) above 30 Km and upto 50 Km with Lorry for each trip | Labour | Transport of Cond Drum,VCBs >30 & <50Km | As per relevent standard specification | 4372.74 | EA | 43727.4
189 | SWR11230 | 19 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Labour | Load-11/33KV XLPE UG Cable for all sizes | As per relevent standard specification | 1024 | DR | 19456
190 | SWR11231 | 19 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Labour | Unload-11/33KV XLPE UG Cable all sizes | As per relevent standard specification | 1024 | DR | 19456
191 | SWR11980 | 2200 | Excavation & Laying of 33 KV 3x400 Sqmm XLPE UG cable Double Run along the CC / BT multi layer road requiring compressor including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, | Labour | Lay-DR 33KV 3x400sqmm UG Cb CC/BT Compsr | As per relevent standard specification | 1388.84 | M | 3055448
192 | SWR11988 | 500 | Excavation & Laying of 33 KV 3x400 Sqmm XLPE UG cable Double Run Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, | Labour | Lay-DR 33KV 3x400sqmm UG Cb CC/BT RdCrsg | As per relevent standard specification | 1587.07 | M | 793535
193 | SWR10988 | 2700 | aying of 2nd cable in excavated trench | Labour | Lay-2nd Cable in Excavated Trench | As per relevent standard specification | 204.1 | M | 551070
194 | SWR12004 | 200 | Raising of double run 33 KV 3x400 Sqmm cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Labour | Raise-DR 33KV 3x400sqmm UG Cb on support | As per relevent standard specification | 323.85 | M | 64770
195 | SMR40001 | 500 | Cost of Pipes and slabs:Suppy of Hume pipe 9" size | Supply of Materials | Hume pipe 9" size | As per relevent standard specification | 125 | M | 62500
196 | SMR40081 | 1000 | Supply of 6" B class GI pipe | Supply of Materials | S-6" B Class GI pipe 5mm thck 20Kg/M | As per relevent standard specification | 1044 | M | 1044000
197 | SWR10387 | 20 | Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination | Labour | OD/Idoor end termination 33kv 3x400 xlpe | As per relevent standard specification | 2764.76 | EA | 55295.2
198 | SWR10382 | 16 | Making of Straight through joints for 33 KV 3x400 Sqmm UG Cable | Labour | Straight through joint 33kv 3x400 xlpe | As per relevent standard specification | 5700.78 | EA | 91212.48
199 | SWR10392 | 4 | Erection of 33 KV AB Switch including alignment and earthing | Labour | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 18000
200 | SWR10881 | 4 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete for Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Labour | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 568
201 | SWR10108 | 32 | Excavation of pits in all soils except hard rock requiring blasting for 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M (1.31 cum) | Labour | EXCAV. OF PIT 0.75 M x 0.9 M x 1.95 M | As per relevent standard specification | 629.85 | EA | 20155.2
202 | SMR12315 | 4 | Supply-33KV 800A DB Break AB Switch | Supply of Materials | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 162635.12
203 | SMR12303 | 2000 | Supply-RS Joist Pole (175x85mm) | Supply of Materials | S-RS Joist Pole (175x85mm) | As per relevent standard specification | 60.75 | KG | 121500
204 | SMR22745 | 5000 | Supply- MS Channel 100x50mm | Supply of Materials | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 287250
205 | SMR12321 | 250 | Supply-MS Flat 75x8mm | Supply of Materials | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 14105
206 | SMR25207 | 2900 | Supply-MS Angle 65X65X6 | Supply of Materials | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 166025
207 | SMR22222 | 20 | Supply of 33KV 3x400Sqmm O/D End Kit | Supply of Materials | Supply of 33KV 3x400Sqmm O/D End Kit | As per relevent standard specification | 4554 | EA | 91080
208 | SMR25234 | 64 | Supply-PSCC Spun Pole 11Mtr | Supply of Materials | S-PSCC Spun Pole 11Mtr | As per relevent standard specification | 6540 | EA | 418560
209 | SMR22223 | 16 | Supply of 33KV3x400Sqmm Straight thr kit | Supply of Materials | Supply of 33KV3x400Sqmm Straight thr kit | As per relevent standard specification | 24151 | EA | 386416
210 | SWR10856 | 6.29 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) (other than SS) | Labour | Earth work excav hard rock bould <3cum | As per relevent standard specification | 1318.35 | M3 | 8292.42
211 | SWR10356 | 6.29 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. | Labour | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 41381.91
212 | SMR40009 | 2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Supply of Materials | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 4362
213 | SMR40010 | 2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete : Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Supply of Materials | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 2586
214 | SWR10877 | 2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Labour | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 1702
215 | SWR10879 | 2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete: Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium | Labour | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 964
216 | SWR10348 | 2 | Erection of R.S. Joists 150 x 150 mm pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Labour | Erection of RS Joist 150 x 150 mm | As per relevent standard specification | 1952.61 | EA | 3905.22
217 | SWR11879 | 900 | Control cable:Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Labour | Lay-4C/10C 2.5Sqmm Control Cable | As per relevent standard specification | 27 | M | 24300
218 | SMR40047 | 2 | Marshalling Box: Supply of MS Powder coated CT Marshalling Box | Supply of Materials | Sup MS Powder coated CT Marshalling Box | As per relevent standard specification | 3675 | EA | 7350
219 | SWR10940 | 2 | Erection of Marshalling boxes | Labour | Erection of Marshalling boxes | As per relevent standard specification | 374.85 | EA | 749.7
220 | SMR11915 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Supply of Materials | S-Tension HW 3Bolt 1Zebra/Pnthr 150mm | As per relevent standard specification | 2055 | SET | 24660
221 | SWR10920 | 32 | Laying of earth mat with 75x 8mm MS Flat / GI Flat. including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication. | Labour | Laying of earth mat,excavation 75x 8mm | As per relevent standard specification | 65 | RMT | 2080
222 | SMR11482 | 5 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Supply of Materials | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 17430
223 | SWR10357 | 5 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Labour | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 6171
224 | SWR10359 | 5 | Providing of RCC Collar to earth pitguarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Labour | ERECT. OF LINES-Providing of RCC collar | As per relevent standard specification | 386 | EA | 1930
225 | SWR21240 | 12 | Bus stringing: Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt) | Labour | Hoisting post ins&hrd wr 1panther 33kv | As per relevent standard specification | 781 | EA | 9372
226 | SWR11880 | 200 | Control panels: Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Labour | Lay-Cable Terminations to Switchgear | As per relevent standard specification | 34.43 | EA | 6886
227 | SWR10396 | 1 | Erection of 33 KV LAS station/Line type including earthing | Labour | Erect of 33kv LA stn type incl earthing | As per relevent standard specification | 880 | SET | 880
228 | SWR10460 | 1 | Erection of 33 KV VCB with Control Panel | Labour | Erection of 33kv VCB | As per relevent standard specification | 12500 | EA | 12500
229 | SWR10860 | 7.5 | Supply of HBG Metal: Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | Labour | Supply & Spreading of 20mm HBG metal | As per relevent standard specification | 2113 | M3 | 15847.5
230 | SWR10881 | 2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.: Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Labour | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 284
231 | SWR10198 | 2 | Loading of 33 KV VCBs along with Panel boards | Labour | LOADING of 33 KV VCBs&Panel boards | As per relevent standard specification | 1024 | EA | 2048
232 | SWR10516 | 1 | Un loading of 33 KV VCBs along with Panel boards | Labour | UNLOADING of 33 KV VCBs&Panel boards | As per relevent standard specification | 1044.48 | EA | 1044.48
233 | SWR11860 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Upto 10 Km with Lorry for each trip | Labour | Transport of Cond Drum,VCBs upto 10Km | As per relevent standard specification | 2720.34 | EA | 2720.34
234 | SWR10392 | 2 | Erection of 33 KV AB Switch including alignment and earthing | Labour | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 9000
235 | SWR10109 | 2 | Excavation of pits for 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") 1.94 cum in all soils except hard rock requiring blasting | Labour | EXCAVATION OF PIT(3.0" x 3.0" x 7.6") | As per relevent standard specification | 842.78 | EA | 1685.56
236 | SWR10917 | 50 | Labour for Fixing of all types of clamps | Labour | Labour for Fixing of all types of clamps | As per relevent standard specification | 65 | EA | 3250
237 | SWR10404 | 20 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | Labour | Stringing of bus with panther conductor | As per relevent standard specification | 327.68 | M | 6553.6
238 | SWR10356 | 2.114 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. | Labour | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 13908.01
239 | SWR10205 | 2 | Loading of R.S. Joists 150 x 150mm / Rail poles | Labour | LOADING of RSJoists150 x 150 mm/RailPole | As per relevent standard specification | 176 | EA | 352
240 | SWR10132 | 2 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) above 10 KM and upto 20 KM | Labour | TRANSPORT OF STEEL 10 TO 20KM | As per relevent standard specification | 412.08 | TO | 824.16
241 | SWR10869 | 1.8 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Labour | Fabrication of struc.with welding. | As per relevent standard specification | 3426 | TO | 6166.8
242 | SWR23224 | 20 | Excavate-Pit for 33KV VCB | Labour | Excavate-Pit for 33KV VCB | As per relevent standard specification | 331 | M3 | 6620
243 | SWR10862 | 20 | Plastering 2 Coats,20/16mm(1:6)(1:4) | Labour | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | As per relevent standard specification | 373 | M2 | 7460
244 | SMR12302 | 1000 | Supply-RS Joist Grider Pole (150x150mm) | Supply of Materials | S-RS Joist Grider Pole (150x150mm) | As per relevent standard specification | 59.25 | KG | 59250
245 | SMR12321 | 150 | Supply-MS Flat 75x8mm | Supply of Materials | S-MS Flat 75x8mm | As per relevent standard specification | 56.42 | KG | 8463
246 | SMR12322 | 90 | Supply-MS Flat 50x6mm | Supply of Materials | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 5085
247 | SMR22745 | 800 | Supply- MS Channel 100x50mm | Supply of Materials | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 45960
248 | SMR12315 | 2 | Supply-33KV 800A DB Break AB Switch | Supply of Materials | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 81317.56
249 | SWR22092 | 2.3 | survey line&cabl inc peg mark&tree clear | Labour | survey line&cabl inc peg mark&tree clear | As per relevent standard specification | 765 | KM | 1759.5
250 | SMR11683 | 30 | Supply of M+3 Tower (Galvanized) | Supply of Materials | S-M+3 Tower GALV | As per relevent standard specification | 140674.3 | EA | 4220229
251 | SMR11684 | 30 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) | Supply of Materials | S-Mat. for Extn of M+3 Tower by 3M GALV | As per relevent standard specification | 28520.64 | EA | 855619.2
252 | SWR11850 | 30 | Erection of M+3 Tower (Galvanized) | Labour | Erect- M+3 Tower GALV | As per relevent standard specification | 64576 | EA | 1937280
253 | SWR11851 | 30 | Erection of Extension of 3Mtrs for M+3 (Galvanized) | Labour | Erect-Extn of 3M for M+3 Tower GALV | As per relevent standard specification | 5168.95 | EA | 155068.5
254 | SWR20959 | 142.56 | Earth work excavation of pits in hard murram/rock boulders | Labour | Excavate-Earth in Hard Murram | As per relevent standard specification | 1530 | M3 | 218116.8
255 | SWR10466 | 10 | Formation of 33kvline vertical cutpoint | Labour | Formation of 33kvline vertical cutpoint | As per relevent standard specification | 3198.72 | EA | 31987.2
256 | SMR40009 | 2.1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.Sup Material for 1st coat Al. Painting. | Supply of Materials | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 4580.1
257 | SWR10877 | 2.1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.Sup Material for 1st coat Al. Painting. Labour for 1st coat Al. Painting. | Labour | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 1787.1
258 | SMR40010 | 2.1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.Sup Material for 1st coat Al. Painting. Labour for 1st coat Al. Painting.Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Supply of Materials | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 2715.3
259 | SWR10879 | 2.1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium | Labour | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 1012.2
260 | SWR10366 | 1.8 | Paving out and stringing of 100 Sqmm Single Circuit (3 Conductors) conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location. | Labour | Stringing 100sqmm 33/11kv Line 3 Cond SC | As per relevent standard specification | 13856.7 | KM | 24942.06
261 | SWR10149 | 2.1 | Transport of steel including line materials such as cross arms, clamps, hardware, cable (loose) and other line materials (Including loading and unloading) above 20 KM and upto 30 KM | Labour | TRANSPORT OF STEEL MATERIAL 20 TO 30KM | As per relevent standard specification | 527.34 | TO | 1107.41
262 | SWR10206 | 2.1 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Labour | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 464.1
263 | SWR10524 | 2.1 | UNLOADING of MS Channel, Angles,Flats&Rod | Labour | UNLOADING of MS Channel,Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 388.5
264 | SWR10211 | 30 | LOADING of 33 KV Pin insulators | Labour | LOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | KI | 90
265 | SWR10529 | 30 | UNLOADING of 33 KV Pin insulators | Labour | UNLOADING of 33 KV Pin insulators | As per relevent standard specification | 3 | KI | 90
266 | SWR10618 | 2 | LOADING of 33KV Metal parts-bag of 25no | Labour | LOADING of 33KV Metal parts-bag of 25no | As per relevent standard specification | 65 | BAG | 130
267 | SWR11863 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) above 30 Km and upto 50 Km with Lorry for each trip | Labour | Transport of Cond Drum,VCBs >30 & <50Km | As per relevent standard specification | 4372.74 | EA | 8745.48
268 | SMR11488 | 50 | Supply of GI Bolts & Nuts etc | Supply of Materials | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 5875
269 | SWR11863 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) above 30 Km and upto 50 Km with Lorry for each trip | Labour | Transport of Cond Drum,VCBs >30 & <50Km | As per relevent standard specification | 4372.74 | EA | 8745.48
270 | SWR11230 | 4 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Labour | Load-11/33KV XLPE UG Cable for all sizes | As per relevent standard specification | 1024 | DR | 4096
271 | SWR11231 | 4 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Labour | Unload-11/33KV XLPE UG Cable all sizes | As per relevent standard specification | 1024 | DR | 4096
272 | SWR11980 | 400 | Excavation Laying of 33 KV 3x400 Sqmm XLPE UG cable Double Run along the CC / BT multi layer road requiring compressorincluding excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, | Labour | Lay-DR 33KV 3x400sqmm UG Cb CC/BT Compsr | As per relevent standard specification | 1388.84 | M | 555536
273 | SWR11988 | 80 | Excavation Laying of 33 KV 3x400 Sqmm XLPE UG cable Double Run across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, | Labour | Lay-DR 33KV 3x400sqmm UG Cb CC/BT RdCrsg | As per relevent standard specification | 1587.07 | M | 126965.6
274 | SWR10988 | 480 | Laying of 2nd cable in excavated trench | Labour | Lay-2nd Cable in Excavated Trench | As per relevent standard specification | 204.1 | M | 97968
275 | SWR12004 | 20 | Raising of 33 KV 3x400 Sqmm Cable double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Labour | Raise-DR 33KV 3x400sqmm UG Cb on support | As per relevent standard specification | 323.85 | M | 6477
276 | SMR40001 | 80 | Suppy of Hume pipe 9" size | Supply of Materials | Hume pipe 9" size | As per relevent standard specification | 125 | M | 10000
277 | SMR40081 | 180 | Supply of 6" B class GI pipe | Supply of Materials | S-6" B Class GI pipe 5mm thck 20Kg/M | As per relevent standard specification | 1044 | M | 187920
278 | SWR10387 | 6 | Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination | Labour | OD/Idoor end termination 33kv 3x400 xlpe | As per relevent standard specification | 2764.76 | EA | 16588.56
279 | SWR10382 | 6 | Making of Straight through joints to 33 KV 3x400 Sqmm UG Cable | Labour | Straight through joint 33kv 3x400 xlpe | As per relevent standard specification | 5700.78 | EA | 34204.68
280 | SWR10392 | 1 | Erection of 33 KV AB Switch including alignment and earthing | Labour | Erection of 33kv ABSwitch incl earthing | As per relevent standard specification | 4500 | EA | 4500
281 | SWR10881 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Labour | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 142
282 | SMR12315 | 1 | Supply-33KV 800A DB Break AB Switch | Supply of Materials | S-33KV 800A DB Break AB Switch | As per relevent standard specification | 40658.78 | EA | 40658.78
283 | SMR22745 | 1100 | Supply- MS Channel 100x50mm | Supply of Materials | S- MS Channel 100x50mm | As per relevent standard specification | 57.45 | KGS | 63195
284 | SMR25207 | 1000 | Supply-MS Angle 65X65X6 | Supply of Materials | S-MS Angle 65X65X6 | As per relevent standard specification | 57.25 | KG | 57250
285 | SMR22223 | 6 | Supply of 33KV3x400Sqmm Straight thr kit | Supply of Materials | Supply of 33KV3x400Sqmm Straight thr kit | As per relevent standard specification | 24151 | EA | 144906
286 | SMR22222 | 6 | Supply of 33KV 3x400Sqmm O/D End Kit | Supply of Materials | Supply of 33KV 3x400Sqmm O/D End Kit | As per relevent standard specification | 4554 | EA | 27324
287 | SWR11039 | 239 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) for 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Labour | Exca Hard pit w/o blast 0.76X0.76X1.83M | As per relevent standard specification | 928 | EA | 221792
288 | SWR10112 | 24 | Excavation of pits in hard rock requiring blasting. (other than SS) for 9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Labour | EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | As per relevent standard specification | 1770 | EA | 42480
289 | SWR10343 | 263 | Erection of 9.1 M long PSCC pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Labour | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 631200
290 | SWR10356 | 23.22 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. | Labour | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 152764.38
291 | SWR10653 | 22 | Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays | Labour | Formatn of Horiz Cut point for 11KV line | As per relevent standard specification | 1435.81 | EA | 31587.82
292 | SMR40009 | 6.3 | Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc for Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. | Supply of Materials | Sup Material for 1st coat Al. Painting. | As per relevent standard specification | 2181 | TO | 13740.3
293 | SWR10877 | 6.3 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium for Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. | Labour | Labour for 1st coat Al. Painting. | As per relevent standard specification | 851 | TO | 5361.3
294 | SMR40010 | 6.3 | Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes etc for Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. | Supply of Materials | Sup Material for 2nd coat Al. Painting. | As per relevent standard specification | 1293 | TO | 8145.9
295 | SWR10879 | 6.3 | Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium for Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. | Labour | Labour for 2nd coat Al. Painting. | As per relevent standard specification | 482 | TO | 3036.6
296 | SWR10365 | 10.5 | Paving out and stringing of 55 Sqmm Single Circuit (3 Conductors) conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location. | Labour | Stringing of 55sqmm 33/11kv Line 3 Cond | As per relevent standard specification | 9454.81 | KM | 99275.51
297 | SWR20308 | 263 | Sub-transport of 9.1 Mtrs long PSCC Poles upto Workspot upto 10KM (Including loading and unloading) | Labour | SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | As per relevent standard specification | 407.29 | EA | 107117.27
298 | SWR10393 | 2 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Labour | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 6400
299 | SWR10881 | 2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.for Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Labour | Painting AB switch OP rods with PO red | As per relevent standard specification | 142 | EA | 284
300 | SMR11485 | 50 | Supply of earthing pipe with materials: Supply of GI Flat 25X3 mm | Supply of Materials | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 5250
301 | SWR10206 | 6.3 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Labour | LOADING of MS Channel,Angles,Flats&Rods | As per relevent standard specification | 221 | TO | 1392.3
302 | SWR10149 | 6.3 | Transport of steel including line materials such as cross arms, clamps, hardware, cable (loose) and other line materials (Including loading and unloading) above 20 KM and upto 30 KM | Labour | TRANSPORT OF STEEL MATERIAL 20 TO 30KM | As per relevent standard specification | 527.34 | TO | 3322.24
303 | SWR10524 | 6.3 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Labour | UNLOADING of MS Channel, Angles,Flats&Rod | As per relevent standard specification | 185 | TO | 1165.5
304 | SWR10212 | 789 | Loading of 11KV pin insulators/Post type insulators/ Solid core insulators | Labour | LOADING of 11kv Pin/Post/Solid Core Insu | As per relevent standard specification | 1 | KI | 789
305 | SWR10631 | 789 | Un loading of 33 & 11 KV Disc insulators | Labour | UNLOADING of 33 & 11 KV Disc insulator | As per relevent standard specification | 2 | KI | 1578
306 | SWR12402 | 8.8 | Loading of 11 KV Metal parts | Labour | LOADING of 11 KV Metal parts | As per relevent standard specification | 48 | BAG | 422.4
307 | SWR12421 | 8.8 | Un loading of 11 KV Metal parts | Labour | UNLOADING of 11 KV Metal parts Bag | As per relevent standard specification | 48 | BAG | 422.4
308 | SWR11862 | 12 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) above 20 Km and upto 30 Km with Lorry for each trip | Labour | Transport of Cond Drum,VCBs >20 & <30Km | As per relevent standard specification | 3691.38 | EA | 44296.56
309 | SMR11484 | 4 | Supply of CI eath pipe with 50mm dia,2.0 M Length | Supply of Materials | S-CI Pipe earthing 50mm dia 2m long | As per relevent standard specification | 2441 | EA | 9764
310 | SWR10359 | 4 | Providing of RCC collar to earth pit.Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Labour | ERECT. OF LINES-Providing of RCC collar | As per relevent standard specification | 386 | EA | 1544
311 | SWR10357 | 4 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Labour | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 4936.8
312 | SMR11485 | 50 | Supply of earthing pipe with materials: Supply of GI Flat 25X3 mm | Supply of Materials | S-Earthing GI flat 25x3 mm incl material | As per relevent standard specification | 105 | KG | 5250
313 | SMR25233 | 263 | Supply -PSCC Pole 9.1Mtr 280kg | Supply of Materials | S-PSCC Pole 9.1Mtr 280kg | As per relevent standard specification | 3109.41 | EA | 817774.83
314 | SMR25205 | 4000 | Supply-MS Channel 75x40 mm | Supply of Materials | S-MS Channel 75x40 mm | As per relevent standard specification | 58.45 | KG | 233800
315 | SMR25206 | 2000 | Supply-MS Angle 50x50x6 | Supply of Materials | S-MS Angle 50x50x6 | As per relevent standard specification | 58.15 | KG | 116300
316 | SMR12322 | 380 | Supply-MS Flat 50x6mm | Supply of Materials | S-MS Flat 50x6mm | As per relevent standard specification | 56.5 | KG | 21470
317 | SMR12317 | 2 | Supply-11KV 400A DB Break AB Switch | Supply of Materials | S-11KV 400A DB Break AB Switch | As per relevent standard specification | 18150 | EA | 36300
|  | Total Service Cost: | [6 empty] | 38941838.41 | 7462000
1 |  | 1 | Geophysical investigation charges | Geophysical investigation | Geophysical investigation | As per relevent standard specification | 5000 | EA | 5000
2 |  | 90 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work.Drilling-165mm Bore Well 0 to 90M | Drilling borewell | Drilling borewell | As per relevent standard specification | 336 | M | 30240
3 |  | 30 | Drill-165mm Bore Well 90M to 120M | Drilling borewell | Drilling borewell | As per relevent standard specification | 369 | M | 11070
4 |  | 30 | Drill-165mm Bore Well 120 M to 150M | Drilling borewell | Drilling borewell | As per relevent standard specification | 394 | M | 11820
5 |  | 30 | Drill-165mm Bore Well 150M to 180M | Drilling borewell | Drilling borewell | As per relevent standard specification | 492 | M | 14760
6 |  | 20 | Suppy & fixing of 180 mm dia. 6 kg/cm2 PVC casing pipe including cost and conveyance of all materials labour charges etc complete for finished item of work. | PVC Casing | PVC Casing | As per relevent standard specification | 883 | M | 17660
7 |  | 160 | Supply and fixing of HDPE pipe 40mm dia. including cost and conveyance of all materials labour charges etc complete for finished item of work. | HDPE Pipe | HDPE Pipe | As per relevent standard specification | 180 | M | 28800
8 |  | 1 | Supply and Fixing of 1.5HP Texmo/Kirloskar make motor of single phase submersible of multiple stage including all materials and labour charges complete for finished item. | 1.5HP submersbile pump | 1.5HP submersbile pump | As per relevent standard specification | 29047 | EA | 29047
9 |  | 175 | Supply and fixing of 2.5mm single core copper cable complete for finished item. | Copper cable | Copper cable | As per relevent standard specification | 192 | M | 33600
10 |  | 1 | Supply and Fixing of Flange Clamps including cost and conveyance of all materials | Flange Clamps | Flange Clamps | As per relevent standard specification | 182 | EA | 182
11 |  | 1 | Supply and erecting D.O.L Starter 250V, Single phase, 50Hz with SS enclouser comprising of contactor with bi-metallic relay with necessary push buttons, transportation and all labour charges etc. complete. | Single phase starter | Single phase starter | As per relevent standard specification | 1040 | EA | 1040
12 |  | 30 | Hiring of JCB for site levelling and cleaning | Hiring of JCB | Hiring of JCB | As per relevent standard specification | 2165 | H | 64950
13 |  | 221.9 | Earth Work Mass Excavation to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water (either sub soil water, storm water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete | Earth Work Mass Excavation | Earth Work Mass Excavation | As per relevent standard specification | 486 | M3 | 107843.4
14 |  | 11 | Back Filling the foundation Columns, for lift wells ,Staircase foundation ,U.G Sump Septic tank, Road work ,storm water drain ,cable trench,soak pit and outside of hte reataining wall with the useful avilable excavated earth ,in layers not exceeding 150mm thick, conslidating each deposited layer by eatering and ramming including cost and conveyance of all materials labour chargess,hire charges of T&P,all leads and lifts etc,complete for finished item of work | Back Filling | Back Filling | As per relevent standard specification | 40 | M3 | 440
15 |  | 40 | Providing and laying Plain Cement concrete of (1:4:8) for levelling course using 40mm size hard broaken Granite stone including cost and conveyance of all materials, se HBG metal for foundations and leveling course, including cost and conveyance of all materials,seignorage, water, labour charges, hire charges of nachinery, at all levels, depths,heights and floors consolidation by watering ,ramming in layers,bailing of water if any, and removal of form work after completion of work curing for reqired number of days,all incidental charges etc complete for finished item of work. | PCC (1:4:8) 40mm metal | PCC (1:4:8) 40mm metal | As per relevent standard specification | 5157 | M3 | 206280
16 |  | 5.62 | Providing and laying Plain Cement Concrete of (1:2:4) with well graded machine crushed granite metal of 20mm nominal size from approved quarry for Bed Blocks, Hold Fasts including cost and conveyance of all materials, labour charges,hire charges of machnery,with all leads and lifts, for all floors curing for required number of days, all incidental charges etc complete for finished item work | PCC (1:2:4) 20mm metal | PCC (1:2:4) 20mm metal | As per relevent standard specification | 6573 | M3 | 36940.26
17 |  | 262.2 | CRS masonry in CM(1:6) using Hard Granite Stones including cost and conveyance of all materials, seignorage charges, labour charge for construction and for dressing stones to required size and shape, dewatering,scaffolding,cutting for all leads and lifts, all incidental charges etc .complete for finished item of work | CRS Masonary | CRS Masonary | As per relevent standard specification | 5454 | M3 | 1430038.8
18 |  | 1020.4 | Supplying and filling with borrowed gravel, watering, ramming, consolidating thoroughly complying with the standard specification including cost and conveyance of all materials, labour charges,hire charges of machnery,with all leads and incidental charges etc complete for finished item work | filling with gravel | filling with gravel | As per relevent standard specification | 646 | M3 | 659178.4
19 |  | 5.2 | Reinforced Cement concerete M20 GRADE Nominal Mix for footings , columns, Beams and Slab using 12mm to 20mm size graded HBG machine crushed metal from approvaed quary giving cube crushing strenth of 20 N /sqmm and a minimum of 400 kgs of cement for 1 cum of concrete including cost and conveyance charges for cement and all other materials to site, scaffolding charge , seignorage charges, centering, shuttering, machine mixing,laying concrete, curing for specified number of days vibrating etc compaction by pen vibrator or needle vibrator supplemented by hand spreeding rodding and tamping ,all incident and operational charges , all leads and lifts and for all leaving gaps and pockets etc complete, but excuding cost of ssteel and its fabrication,all incidental charges etc .complete for finshed item of workA)Ground floor a)Footings | RCC Footings | RCC Footings | As per relevent standard specification | 9956 | M3 | 51771.2
20 |  | 3.7 | b)Columns | RCC Columns | RCC Columns | As per relevent standard specification | 13705 | M3 | 50708.5
21 |  | 2.15 | c)Plinth beams | RCC Plinth beams | RCC Plinth beams | As per relevent standard specification | 12827 | M3 | 27578.05
22 |  | 2.71 | d)Roof beams | RCC Roof beams | RCC Roof beams | As per relevent standard specification | 12743 | M3 | 34533.53
23 |  | 0.55 | e)Lintels | RCC Lintels | RCC Lintels | As per relevent standard specification | 13534 | M3 | 7443.7
24 |  | 3.4 | f)Sun shade 0.6m width 3" thick | RCC Sunshades | RCC Sunshades | As per relevent standard specification | 1410 | M2 | 4794
25 |  | 12.27 | g)Slab | RCC Slab | RCC Slab | As per relevent standard specification | 11331 | M3 | 139031.37
26 |  | 76 | Brick masonry for wall in superstructure (230mm thick) in CM 1:6 using traditional Local madeSecound Class Bricks from approved sourse and quality having crushing strength of not less than 100 Kg/sq cm and water absorption not exceeding 20% by weight including cost and conveyance of all mateerials, seigniorage charge, all labour charges, curing for number of days as specified, for all leads, lifts scaffolding chargess, at all heght levels and floors all incidental charges etc completed item of work. A)Ground floor | Brick masonary | Brick masonary | As per relevent standard specification | 8569 | M3 | 651244
27 |  | 3.1 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) / Mild steel (MS) steel bars (Fe 415/ Fe 500 grade as per IS 1786-1979) of different diameters for RCC works , including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying including sales and other taxes on all materials etc.,complete for finished item of work | HYSD Steel | HYSD Steel | As per relevent standard specification | 81187 | MT | 251679.7
28 |  | 909 | Providing plastering of 20mm thick to all uneven faces of walls and ceiling of superstructure in two coats with base coat in CM 1:5of 16mm thick and top coat in Cm 1:3 4mm thick with dubara sponge finish including cost and conveyance of all materials . water. all labour charges, curing for specified number of days, cutting grooves, at allheghits, level and floro, all leads, lifts and scaffolding charges, all incidental and scaffolding charges, seigniorage charges, all incidental charges etc. complete for finished item of work A)Ground floor | Plastering 20mm thick | Plastering 20mm thick | As per relevent standard specification | 567 | M2 | 515403
29 |  | 356 | Raised pointing in CM(1:3) including curing, cost and conveyance of all materials and labour charges for complete item of work. | Raised pointing | Raised pointing | As per relevent standard specification | 127 | M2 | 45212
30 |  | 64.05 | Providing impervious coat over RCC roof slab surfaces to requried slopes with 20mm thick in CM 1:3 pro mixed with approved brand of water proofing compound as the rate of 1 kg per bag of cement including cost and conveyance of all materials, water, all labour charges, chemicals, curing for specifed number of days,rounding off junctions of wall and slab, all leads, lifts, heights,levels and floors etc.complete for finished item of work. | impervious coat | impervious coat | As per relevent standard specification | 591 | M2 | 37853.55
31 |  | 15 | Providing Reinforced cement Drop Walls in CM 1:2 of 40mm thick over rabbit wire mesh including cost and conveyance of all meterials, labour charges, curing for specified number of days,at all levels, floors, height, leads and lifts, seignioage charges all incidental charges etc . complete, but excluding cost of steel as per the approved drawing for finished item of work | RCM Drop Walls | RCM Drop Walls | As per relevent standard specification | 3174 | M2 | 47610
32 |  | 6 | Supply and fixing of doors with the frames of the door shall be made well seasoned MT wood of cross section 100x75mm. The shutter shall be made ISI mark flushed door with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary on both sides with 3 no 150mm hinges, 1 no door stoper, 1 no 250mm aldrop, 1 no 300 mm tower bolts, 2 no 150mm door handlers of MS Powder coated, including cost and conveyance of the meterials,fixing,labour carges,tools,handles,locking arrangementts and other fixtures & fittings for finished item work | MT Wood Doors Shutter with frame | MT Wood Doors Shutter with frame | As per relevent standard specification | 7314 | M2 | 43884
33 |  | 5.8 | S&F-UPVC Sliding Windows of approved make including cost and coveyance of all mateirals with all leads and lifts, labour charges, painting charges complete for finished item of work | UPVC Sliding Windows | UPVC Sliding Windows | As per relevent standard specification | 6063 | M2 | 35165.4
34 |  | 6.8 | Supplying and fixing of MS safety grill with peripheral frame of ISA 25x25x4mm and 8mm square rods at 100mm c/c both in horizontal & vertical direction including cost and coveyance of all mateirals with all leads and lifts, labour charges, painting charges complete for finished item of work | MS safety grill | MS safety grill | As per relevent standard specification | 2990 | M2 | 20332
35 |  | 3.7 | Flooring with ceramic tiles of 1st class quality of approved brand shade and design of different size laid over a floor bed of CM 1:3 of 12 mm thick base coat and neat grey cement slurry of honey like consistancy spread at the ratet of 3.3 kg of cement per sqm and pointed to full deapth, (joints must be flushed) with white cement paste mixed with pigment when requied including cost and conveyance of cement and all materials ,labour charges, at all levels, heights and floors,curing etc. complete for finished item of work. | ceramic tiles flooring | ceramic tiles flooring | As per relevent standard specification | 918 | M2 | 3396.6
36 |  | 14.4 | Providing skirting to internal walls to 15 cm height/risers of steps with ceramic tile length equal to floor tile, set over base coat of CM (1:3) 12 mm thick with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointed with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like Shahabad stone, cement, sand and water etc., complete for finished item of work | ceramic tiles dadoing | ceramic tiles dadoing | As per relevent standard specification | 1053 | M2 | 15163.2
37 |  | 40 | Flooring with polished shabads stone quality and approved size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and pointing with cement, labour etc, complete | Polished Shabad stone flooring | Polished Shabad stone flooring | As per relevent standard specification | 791 | M2 | 31640
38 |  | 5.3 | Skirting with polished shabads stone quality and approved size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and pointing with cement, labour etc, complete | Polished Shabad stone Skirting | Polished Shabad stone Skirting | As per relevent standard specification | 880 | M2 | 4664
39 |  | 106 | Painting in all floors as specified with two coats of Plastic emulation paint of approved colour make and shade over one coat of white primer including cost and conveyance of all materials, labour charges at all leads, lifts, hights, levels and floors,all incidental charges etc. complete for finished item of work . | Plastic emulsion | Plastic emulsion | As per relevent standard specification | 155 | M2 | 16430
40 |  | 810 | Painting to External Faces of walls(outside) in all floors as specified with two coats of ACE or equivalent quality paint of approved colour make and shade over one coat of white cement primer including cost and conveyance of all materials, labour charges at all leads, lifts, hights, levels and floors,all incidental charges etc. complete for finished item of work . | ACE painting | ACE painting | As per relevent standard specification | 259 | Sqm | 209790
41 |  | 423.7 | Providing and applying Surya Cem of three coats of approved brand and shade to give an even shade after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, incidental, labour charges etc. complete for finished item of work | Surya cem 3coats | Surya cem 3coats | As per relevent standard specification | 85 | Sqm | 36014.5
42 |  | 2 | Conducting of DGPS & Total Staion Survey and Providing of maps including preparation of boundary and contour levels with 2 Nos hard copies and soft copies complete for finished items of work as directed by the Engineer in charge of the work. | Total Station Survey | Total Station Survey | As per relevent standard specification | 5000 | EA | 10000
43 |  | 54.5 | Supply&Spreading ofHBG metal 20 mm size of 80mm thick including cost&conveyance labour charges etc complete for finished item of work | 20mm HBG metal | 20mm HBG metal | As per relevent standard specification | 1678 | Cum | 91451
44 |  | 114 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 1") of 2.8mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) including cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work. | MS Security fencing | MS Security fencing | As per relevent standard specification | 2310 | Sqm | 263340
45 |  | 7.5 | Supply&Fixing of R.C.C hume pipe of 450 mm dia including cost & conveyance of all materials labour charges etc complete for finished item of work. | RCC hume pipes | RCC hume pipes | As per relevent standard specification | 1474 | Rmt | 11055
46 |  | 40 | Supply and fixing 25mm dia 1.5mm thick recessed( concealed) PVC pipe alog with reinforcement to be laid in slab including No 14 SWG GI wire for earth contunity, cost of pipe, binding wire and all labour charges etc complete | concealed PVC casing | concealed PVC casing | As per relevent standard specification | 97 | M | 3880
47 |  | 30 | Supplying and fixing of 25mm dia 1.5mm thick PVC conduit pipe conceald in wall with all required accessories with No 14 SWG wire for earth conitunity including chisiling the wall whereever necessary, including masonary work and all labour charges complete. | concealed PVC casing | concealed PVC casing | As per relevent standard specification | 108 | M | 3240
48 |  | 15 | Wiring with 2X1.0 Sqm(14/.3mm) PVC insulated flexiable copper cable in the existing metalic/Non metalic conduit pipe with 6A modular SP switch, mounted on metalic box covereds with appropriate front plate modules etc ceiling rose including cot and conveyance of all mateials, labour charges complete for light points, bell points exhaust fan points in non residential builsing except circuit moving finished in all types masonary as directed by department (Anchor Roma/GM/HAVELLS/FINOLEX) | light points | light points | As per relevent standard specification | 642 | EA | 9630
49 |  | 6 | Supplying and erection of approved make 6 Amps one modular SP switch with 6 Amps 6 pin mudular type plug socket mounted on metallic box covered with appropriate front plate as including all labour and material charges etc., complete for finished item of work. | 6 A sockets | 6 A sockets | As per relevent standard specification | 542 | EA | 3252
50 |  | 30 | supplying and run of 2 of 14/0.3 mm(1.0 sqmm) PVC insulated flexiable copper cable in existing conduit pipe for run of mains including all labour charges and materials chages etc. complete. (FINOLEX/HAVELS) | 1.0 sqmm wiring | 1.0 sqmm wiring | As per relevent standard specification | 56 | M | 1680
51 |  | 120 | supplying and run of 2 of 28/0.3 mm(2.5 sqmm) PVC insulated flexiable copper cable in existing conduit pipe for run of mains including all labour charges and materials chages etc. complete. (FINOLEX/HAVELS) | 2.5 sqmm wiring | 2.5 sqmm wiring | As per relevent standard specification | 103 | M | 12360
52 |  | 1 | Supply and fixing of 12 way SPN Distribution board with IP-20 protection suitable for single phase 40A DP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 6Nos as out going including connections and all labour charges concealed in wall by chiseling and masonaqry work etc complete. | 12 way SPN Distribution | 12 way SPN Distribution | As per relevent standard specification | 6394 | EA | 6394
53 |  | 8 | Supply and erecting of approved make crom/bajaj make as directed by department 1x40W patty type fluorscent fitting made of CRCA sheet,completed with polyster filled 40W.choke,starter and side holders etc.complete with 40W tube all lobour charges etc complete (PHILIPS/CROMPTON) | tube lights | tube lights | As per relevent standard specification | 755 | EA | 6040
54 |  | 4 | Supply and fixing of batten holder/slanting holder in lieu of ceiling rose of light point complete with all connections and all labour charges with 11 to CF2 etc complete.(PHILIPS/CROMPTON) | batten holder | batten holder | As per relevent standard specification | 141 | EA | 564
55 |  | 2 | Supply and errection ceiling fan of selected colour and delux model high breeze with 3 blades and double ball bearing and with condenser AC 250 V 50 C/S of 48" 600 mm sweep completed erected in position with resistance type regulator, canopy down rod upto 304.8 mm in length is provided with hook/clamps nuts and bolts and 24/0.2 flexible copper wire etc.,complete and pointed with lettering by enamel paint the Sr.No and date of erection including cost and conveyance of all labour charges (Almonard/CG/Khaitan/Bajaj) and as per the direction of Engineer in charge. | ceiling fan | ceiling fan | As per relevent standard specification | 2277 | EA | 4554
56 |  | 2 | Supply and fixing of Electronic Regulator of Modular of GM / Legrand Myrius / L & T / North West / Indo Simon / ABB /Schneider ZEN celo including cost and conveyance of all labour charges and as per the direction of Engineer in charge. | Regulator for ceiling fan | Regulator for ceiling fan | As per relevent standard specification | 589 | EA | 1178
57 |  | 1 | Providing independent earthing for sophisticated equipment like computer, medical equipment electronic gadgets etc with 600X600X3.15mm thick copper plate rigidly fixed to the 40mm dia GI pipe 2.5m long pipe and 19mm dia B class GI pipe of .3 mts long connectd with reducer providing of stggred holes of 16 Nos of 12 mm dia to earth electrode, enclosed in in a CC chamber of (400X400X400) mm with suitable reinforced RCC slab cover duly filling with betonite powder and clay in (1:6) prop from bottom of pipe to bottom of CC chamber giving earth connection from the electrode throuh necessary GI strip of 25X6X200 mm length provided with suitable size o 14 Nos holes GI washers nuts and bolts and all labour charges etc complete. | earthing | earthing | As per relevent standard specification | 5345 | EA | 5345
58 |  | 40 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)a)15.90mm OD Pipe - SDR 11 | 15.90mm OD CPVC pipes & fittings | 15.90mm OD CPVC pipes & fittings | As per relevent standard specification | 239 | M | 9560
59 |  | 80 | b) 22.20mm OD Pipe - SDR 11 | 22.20mm OD CPVC pipes & fittings | 22.20mm OD CPVC pipes & fittings | As per relevent standard specification | 313 | M | 25040
60 |  | 90 | c) 28.60mm OD Pipe - SDR 11 | 28.60mm OD CPVC pipes & fittings | 28.60mm OD CPVC pipes & fittings | As per relevent standard specification | 410 | M | 36900
61 |  | 20 | S & F Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type a) 20 mm NB Size | 20mm Ball valve | 20mm Ball valve | As per relevent standard specification | 331 | EA | 6620
62 |  | 2 | b) 25 mm NB Size | 25mm Ball valve | 25mm Ball valve | As per relevent standard specification | 466 | EA | 932
63 |  | 20 | Supply and Fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand including cost and conveyance, labour charges of all materials etc. complete for finished item of work. | 110mm PVC/SWR pipe | 110mm PVC/SWR pipe | As per relevent standard specification | 462 | M | 9240
64 |  | 2 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) including cost and conveyance, labour charges of all materials etc. complete for finished item of work. | 110mm PVC/SWR Plain bend | 110mm PVC/SWR Plain bend | As per relevent standard specification | 96 | EA | 192
65 |  | 2 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) including cost and conveyance, labour charges of all materials etc. complete for finished item of work. | 110mm PVC/SWR door bend | 110mm PVC/SWR door bend | As per relevent standard specification | 128 | EA | 256
66 |  | 2 | Supply & fixing of Floor Trap (Bell Mouth ) 110 mm - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) including cost and conveyance, labour charges of all materials etc. complete for finished item of work. | 110mm PVC/SWR floor trap | 110mm PVC/SWR floor trap | As per relevent standard specification | 269 | EA | 538
67 |  | 2 | Supply&fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) including cost and conveyance, labour charges of all materials etc. complete for finished item of work. | 4" Nahany trap | 4" Nahany trap | As per relevent standard specification | 134 | EA | 268
68 |  | 1 | Constructing 457.2 mm x 457.2 mm (1'6"x1'6") brick in CM 1:6 prop. Masonry. Inspection chamber up to 914.4 mm (3'0") and fitted with light weight 457.2 mm x 457.2 mm (1'6"x1'6") C.I frame and cover of 20 Kg. | (1'6"x1'6") brick inspection chamber | (1'6"x1'6") brick inspection chamber | As per relevent standard specification | 4610 | EA | 4610
69 |  | 1 | Supplying and Fixing European Water Closet of 1st quality conforming to IS:2556-Part-2-1973 of Hindustan / Neycer or Parryware make white glazed with 'S' trap including cost and conveyance, labour charges etc complete. | European Water Closet | European Water Closet | As per relevent standard specification | 2228 | EA | 2228
70 |  | 2 | Supplying and fixing of best indian make plastic seat and lid for European water closets and buffers as per IS 2548-1963 | plastic seat and lid for EWC | plastic seat and lid for EWC | As per relevent standard specification | 1324 | EA | 2648
71 |  | 2 | Supply and fixing of PV low level system parryware/slim line with internal component and short bend of 10 lits capacity with choice color etc., complete. | PVC low level tank | PVC low level tank | As per relevent standard specification | 2032 | EA | 4064
72 |  | 2 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Hand wash basin | Hand wash basin | As per relevent standard specification | 1717 | EA | 3434
73 |  | 2 | Suplying and fixing of angle stop cock 12.7mm dia fisrt quality indian make seiko or equivalent. | 12.7mm stop cock | 12.7mm stop cock | As per relevent standard specification | 721 | EA | 1442
74 |  | 2 | Suplying and fixing of bib tap 12.7mm dia fisrt quality indian make seiko or equivalent. | 12.7mm bib tap | 12.7mm bib tap | As per relevent standard specification | 298 | EA | 596
75 |  | 1000 | Providing and placing on terrace (at all floor levels) Sintex /Aqua tech or equivalent Polyethylene water storage tank double layer conforming to ISI 12701/96 mark with lid and suitable locking arraqngments and making necessary holes for inlet and outleta and over flow pipes labour charges etc complete for finished item of work. | PVC Sintex tank | PVC Sintex tank | As per relevent standard specification | 10 | L | 10000
76 |  | 1 | Suplying and fixing of 31.75mm PVC waste pipe for wash basin including cost and conveyance of all materials and labour charges et complete | PVC waste pipe | PVC waste pipe | As per relevent standard specification | 33 | EA | 33
77 |  | 1 | Supplying and fixing of TV shape mirror with plastic size 609mmX 457.2 m | TV shape mirror | TV shape mirror | As per relevent standard specification | 564 | EA | 564
78 |  | 1 | Constructing 1220.0 mm (4’0”) dia Septic tank with CC collars/rings including excavating pit up to a depth of 1800 mm (6'-0") in all sorts of soils (excluding rock), laying cement concrete (1:4:8) 150 mm thick using 40mm HBG Metal, Plastering 20mm thick for jointing CC collars and Providing M-20(Nominal mix) grade 3" thick RCC cover and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site and all incidental and operational, labour charges etc., complete for finished item of work as directed by the Engineer in charge. | 4’0” dia Septic tank | 4’0” dia Septic tank | As per relevent standard specification | 8215 | EA | 8215
79 |  | 1 | Constructing 1220.0 mm (4’0”) dia Soak pit with reinforced brick masonary(honey-comb wall) including excavating pits up to a depth of 1500 mm (5'-0") in all sorts of soils (excluding rock) as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site and all incidental and operational, labour charges etc., complete for finished item of work as as directed by the Engineer in charge. | 4’0” dia Soak pit | 4’0” dia Soak pit | As per relevent standard specification | 5560 | EA | 5560
80 |  | 1 | FURNITURE AND NAME BOARDSSupply of steel table of size 4'x2.'x30" with 18 mm plywood fixed with rubber beeding with drawers on right side with automatic locking arrangements etc copmlete. | steel table | steel table | As per relevent standard specification | 7800 | Each | 7800
81 |  | 2 | supply of 'S' type chair with arms teakwood frame with seat back 's' type on G.I pipe.(Make: Godraj) | S type chairs | S type chairs | As per relevent standard specification | 3650 | Each | 7300
82 |  | 2 | Supply of P V C chairs of approved quality & make incldg cost etc complete | PVC Chairs | PVC Chairs | As per relevent standard specification | 1150 | Each | 2300
83 |  | 15 | S&F ACP Vinyl Sign Board with MS Frame | Name boards | Name boards | As per relevent standard specification | 584 | FT2 | 8760
84 |  | 1.62 | Supply and Fixing of Substation name board of size 6'x3' iron sheet with angle frame and channel supports of size 75x40mm, 8' height including concreting of channel supports and painting with enamel paint complete. | Name boards | Name boards | As per relevent standard specification | 4326 | Sqm | 7008.12
85 |  | 1650 | Hard rock (blasting prohibited)-Upto 3 m depth using Air compressor etc., including cost & convenyance all of all machinery and labour chargers etc., complete for finished item of work. | Hard Rock (Blasting prohibited) | Hard Rock (Blasting prohibited) | As per relevent standard specification | 1440 | Cum | 2376000
86 |  | 1650 | Carting away of dismantled materials Complete for finished item of work as directed by the Engineer in charge of the work. | Carting away | Carting away | As per relevent standard specification | 270 | Cum | 445500
87 |  | 73.07 | Seigniorage Charges - Sand | Seigniorage Charges | Seigniorage Charges |  | 40 | M3 | 2922.8
88 |  | 73.07 | Seigniorage Charges -M Sand | Seigniorage Charges | Seigniorage Charges |  | 97.5 | M4 | 7124.325
89 |  | 408.13 | Seigniorage Charges - Metal | Seigniorage Charges | Seigniorage Charges |  | 97.5 | M3 | 39792.675
90 |  | 1020.4 | Seigniorage Charges - Garvel | Seigniorage Charges | Seigniorage Charges |  | 30 | M3 | 30612
[8 empty] | Civl total | 8472255.08
[7 empty] | Civil & electrical total |  | 47414093.49

## 15. Shambipur SS
Shambipur Electrical work Schedule (WBS No.S-1665-07-06-01-03-001)
E-Procurement Schedule for Estimate for "Erection of new 33/11kV Outdoor substation at Shambipur village with 2x12.5 MVA PTRs in operation Bowrampet section of Jeedimetla sub-division in Construction Division of Medchal circle under T&D improvement works- Under T&D PTR augmentation works (Summer Action plan works-2024).
S.No | SAP Code | Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item Short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | Rate INR upto 2 Decimals | Amount INR (Upto 2 Decimals)
1 | SWR10205 | 16 | LOADING of LINE MATERIALS R.S. Joists 150 x 150mm / Rail poles | LOADING Work | LOADING of Work | As per relevent standard specification | 176 | EA | 2816
2 | SWR10132 | 5.76 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S.Channels etc., by lorries. (excluding of loading & unloading) Above 10 KM and upto 20 KM | Transport Work | Transport of Work | As per relevent standard specification | 412.08 | TO | 2373.5808
3 | SWR10523 | 16 | LOADING of LINE MATERIALS of R.S. Joists 150 x 150mm / Rail poles | LOADING Work | LOADING of Work | As per relevent standard specification | 107 | EA | 1712
4 | SWR10112 | 8 | Excavation of pits in hard rock requiring blasting. (other than SS)0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Excavation Work | Excavation of Work | As per relevent standard specification | 1770 | EA | 14160
5 | SWR10868 | 5.76 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RSJoist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Fabrication Work | Fabrication of Work | As per relevent standard specification | 6852 | TO | 39467.52
6 | SMR40009 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Supply of material cost for First coat of 1st Grade Aluminium Paint,brushes etc. | Painting Work | Painting of Work | As per relevent standard specification | 2181 | TO | 12562.56
7 | SWR10877 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Labour charges for painting including scratching and cleaning of Substation structures of 1st coat of Aluminium | Painting Work | Painting of Work | As per relevent standard specification | 851 | TO | 4901.76
8 | SMR40010 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied(*)Supply of material cost for Second coat of 1st Grade Aluminium Paint,brushes, etc. | Painting Work | Painting of Work | As per relevent standard specification | 1293 | TO | 7447.68
9 | SWR10879 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied(*) Labour charges for painting including scratching and cleaning of Substation structures of 2nd coat of Aluminium . | Painting Work | Painting of Work | As per relevent standard specification | 482 | TO | 2776.32
10 | SWR10867 | 5.76 | Fabrication & erection of Channels Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles,Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Fabrication Work | Fabrication of Work | As per relevent standard specification | 1470 | TO | 8467.2
11 | SWR10348 | 16 | R.S. Joists 150 x 150 mm Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Erection Work | Erection of Work | As per relevent standard specification | 1952.61 | EA | 31241.76
12 | SWR10356 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc.Including the cost of cement | Erection Work | Erection of Work | As per relevent standard specification | 6579 | M3 | 116829.882
13 | SWR10862 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Erection Work | Erection of Work | As per relevent standard specification | 373 | M2 | 3446.52
14 | SWR11089 | 16 | Painting of poles coping with 2 coats of white cement incl cost of paints etc. | Painting Work | Painting of Work | As per relevent standard specification | 48 | EA | 768
15 | SWR10204 | 4 | LOADING of LINE MATERIALS of R.S. Joists 175 x 85 mm | LOADING Work | LOADING of Work | As per relevent standard specification | 76 | EA | 304
16 | SWR10132 | 1 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S.Channels etc., by lorries. (excluding of loading & unloading )Above 10 KM and upto 20 KM | Transport Work | Transport of Work | As per relevent standard specification | 412.08 | TO | 412.08
17 | SWR10522 | 4 | UNLOADING of LINE MATERIALS of R.S. Joists 175 x 85 mm | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 50 | EA | 200
18 | SMR40009 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Supply of material cost for First coat of 1st Grade Aluminium Paint,brushes etc. | Painting Work | Painting of Work | As per relevent standard specification | 2181 | TO | 2181
19 | SWR10877 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Labour charges for painting including scratching and cleaning of Substation structures of 1st coat of Aluminium | Painting Work | Painting of Work | As per relevent standard specification | 851 | TO | 851
20 | SMR40010 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Sup Material for 2nd coat Al. Painting.(*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Painting Work | Painting of Work | As per relevent standard specification | 1293 | TO | 1293
21 | SWR10879 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied (*) Labour charges for painting including scratching and cleaning of Substation structures of 2nd coat of Aluminium .. | Painting Work | Painting of Work | As per relevent standard specification | 482 | TO | 482
22 | SWR20863 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of 5 Mts RS Joist (Bit) Pole including fixing of Pole Mounted Box | Erection Work | Erection of Work | As per relevent standard specification | 1044.23 | EA | 2088.46
23 | SWR10356 | 1.44 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Erection Work | Erection of Work | As per relevent standard specification | 6579 | M3 | 9473.76
24 | SWR10862 | 1.155 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Erection Work | Erection of Work | As per relevent standard specification | 373 | M2 | 430.815
25 | SWR11089 | 2 | Painting of poles coping with 2 coats of white cement incl cost of paints etc. | Painting Work | Painting of Work | As per relevent standard specification | 48 | EA | 96
26 | SWR10206 | 5.063 | LOADING of LINE MATERIALS of MS Channel,Angles,Flats&Rods | LOADING Work | LOADING of Work | As per relevent standard specification | 221 | TO | 1118.923
27 | SWR10132 | 5.063 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S.Channels etc., by lorries. (excluding of loading & unloading )Above 10 KM and upto 20 KM | Transport Work | Transport of Work | As per relevent standard specification | 412.08 | TO | 2086.361
28 | SWR10524 | 5.063 | UNLOADING of LINE MATERIALS of MS Channel,Angles,Flats&Rod | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 185 | TO | 936.655
29 | SWR10868 | 5.063 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RSJoist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Fabrication Work | Fabrication of Work | As per relevent standard specification | 6852 | TO | 34691.676
30 | SMR40009 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Supply of material cost for First coat of 1st Grade Aluminium Paint,brushes etc. | Painting Work | Painting of Work | As per relevent standard specification | 2181 | TO | 11042.403
31 | SWR10877 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Labour charges for painting including scratching and cleaning of Substation structures of 1st coat of Aluminium | Painting Work | Painting of Work | As per relevent standard specification | 851 | TO | 4308.613
32 | SMR40010 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Sup Material for 2nd coat Al. Painting.(*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Painting Work | Painting of Work | As per relevent standard specification | 1293 | TO | 6546.459
33 | SWR10879 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied (*) Labour charges for painting including scratching and cleaning of Substation structures of 2nd coat of Aluminium .. | Painting Work | Painting of Work | As per relevent standard specification | 482 | TO | 2440.366
34 | SWR10867 | 5.063 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles,Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Fabrication Work | Fabrication of Work | As per relevent standard specification | 1470 | TO | 7442.61
35 | SWR10239 | 12 | LOADING of LINE MATERIALS of 33 KV AB SWCH Con 400/800 A | LOADING Work | LOADING of Work | As per relevent standard specification | 126 | EA | 1512
36 | SWR11861 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Above 10 Km and upto 20 Km with Lorry for each trip | Transport Work | Transport of Work | As per relevent standard specification | 3299.7 | EA | 6599.4
37 | SWR10557 | 12 | UNLOADING of LINE MATERIALS of 33 KV AB SWCH Con 400/800 A | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 79 | EA | 948
38 | SWR10392 | 12 | Erection of AB Switch and aligment completeErection of 33 KV AB Switch including alignment and earthing | Erection Work | Erection of Work | As per relevent standard specification | 4500 | EA | 54000
39 | SWR10881 | 32 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Painting Work | Painting of Work | As per relevent standard specification | 142 | EA | 4544
40 | SWR12331 | 32 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Earthing Work | Earthing of Work | As per relevent standard specification | 146.63 | EA | 4692.16
41 | SWR10200 | 6 | LOADING of LINE MATERIALS of 33/11 KV CTs/ PTs | LOADING Work | LOADING of Work | As per relevent standard specification | 165 | EA | 990
42 | SWR11861 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Above 10 Km and upto 20 Km with Lorry for each trip | Transport Work | Transport of Work | As per relevent standard specification | 3299.7 | EA | 3299.7
43 | SWR10518 | 6 | UNLOADING of LINE MATERIALS of 33/11 KV CTs/ PTs | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 128 | EA | 768
44 | SWR10401 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV single phase PTs | Erection Work | Erection of Work | As per relevent standard specification | 1079 | SET | 2158
45 | SWR10266 | 12 | LOADING of LINE MATERIALS of 33 KV10 KA LAs Station type | LOADING Work | LOADING of Work | As per relevent standard specification | 41 | EA | 492
46 | SWR11861 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Above 10 Km and upto 20 Km with Lorry for each trip | Transport Work | Transport of Work | As per relevent standard specification | 3299.7 | EA | 3299.7
47 | SWR10584 | 12 | UNLOADING of LINE MATERIALS of 33 KV10 KA LAs Station type | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 35 | EA | 420
48 | SWR10396 | 4 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | Erection Work | Erection of Work | As per relevent standard specification | 880 | SET | 3520
49 | SWR10198 | 2 | LOADING of LINE MATERIALS of 33 KV VCBs&Panel boards | LOADING Work | LOADING of Work | As per relevent standard specification | 1024 | EA | 2048
50 | SWR11861 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Above 10 Km and upto 20 Km with Lorry for each trip | Transport Work | Transport of Work | As per relevent standard specification | 3299.7 | EA | 3299.7
51 | SWR10516 | 2 | UNLOADING of LINE MATERIALS of 33 KV VCBs&Panel boards | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 1044.48 | EA | 2088.96
52 | SWR23224 | 12.584 | SS-WORKS Excavate-Pit for 33KV VCB | Erection Work | Erection of Work | As per relevent standard specification | 331 | M3 | 4165.304
53 | SWR20685 | 14.52 | SS-WORKS Cement concrete with 40MM metal VCB plin | Erection Work | Erection of Work | As per relevent standard specification | 5160 | M3 | 74923.2
54 | SWR10460 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | Erection Work | Erection of Work | As per relevent standard specification | 12500 | EA | 25000
55 | SWR10614 | 2 | LOADING of LINE MATERIALS of 12.5 MVA PTR | LOADING Work | LOADING of Work | As per relevent standard specification | 12044.93 | EA | 24089.86
56 | SWR10855 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading )12.5MVA power transformer | Transport Work | Transport of Work | As per relevent standard specification | 27431 | EA | 54862
57 | SWR10628 | 2 | UNLOADING of LINE MATERIALS of 12.5 MVA PTR | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 12044.93 | EA | 24089.86
58 | SMR22718 | 700 | S/o rail poles 90/105lb (250x2N) | Erection Work | Erection of Work | As per relevent standard specification | 47.27 | KG | 33089
59 | SWR10344 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Rail pole 90 lbs | Erection Work | Erection of Work | As per relevent standard specification | 3510 | EA | 14040
60 | SWR21321 | 2 | Erection of 33/11KV 8 MVA PTR as per spec | Erection Work | Erection of Work | As per relevent standard specification | 49480.2 | EA | 98960.4
61 | SMR11915 | 24 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing | Supply Work | Supply of Work | As per relevent standard specification | 2055 | SET | 49320
62 | SMR22473 | 24 | Supply of various Clamps Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy Supply of I Bolts | Supply Work | Supply of Work | As per relevent standard specification | 294 | EA | 7056
63 | SMR40011 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . | Supply Work | Supply of Work | As per relevent standard specification | 299 | EA | 13455
64 | SWR21240 | 4 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt) | Stringing Work | Stringing of Work | As per relevent standard specification | 781 | EA | 3124
65 | SWR10404 | 185 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) | Stringing Work | Stringing of Work | As per relevent standard specification | 327.68 | M | 60620.8
66 | SWR10884 | 30 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including,cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Stringing Work | Stringing of Work | As per relevent standard specification | 224 | EA | 6720
67 | SWR10917 | 69 | Labour for Fixing of all types of clamps | Erection Work | Erection of Work | As per relevent standard specification | 65 | EA | 4485
68 | SWR10205 | 25 | LOADING of LINE MATERIALS of RSJoists150 x 150 mm/RailPole | LOADING Work | LOADING of Work | As per relevent standard specification | 176 | EA | 4400
69 | SWR10132 | 8.68 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S.Channels etc., by lorries. (excluding of loading & unloading )Above 10 KM and upto 20 KM | Transport Work | Transport of Work | As per relevent standard specification | 412.08 | TO | 3576.8544
70 | SWR10523 | 25 | UNLOADING of LINE MATERIALS of RSJoists150 x150 mm/RailPol | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 107 | EA | 2675
71 | SWR10112 | 25 | Excavation of pits in hard rock requiring blasting. (other than SS)0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Excavation Work | Excavation of Work | As per relevent standard specification | 1770 | EA | 44250
72 | SWR10868 | 8.68 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RSJoist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Fabrication Work | Fabrication of Work | As per relevent standard specification | 6852 | TO | 59475.36
73 | SMR40009 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Supply of material cost for First coat of 1st Grade Aluminium Paint,brushes etc. | Painting Work | Painting of Work | As per relevent standard specification | 2181 | TO | 18931.08
74 | SWR10877 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Labour charges for painting including scratching and cleaning of Substation structures of 1st coat of Aluminium | Painting Work | Painting of Work | As per relevent standard specification | 851 | TO | 7386.68
75 | SMR40010 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Sup Material for 2nd coat Al. Painting.(*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Painting Work | Painting of Work | As per relevent standard specification | 1293 | TO | 11223.24
76 | SWR10879 | 8.68 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied (*) Labour charges for painting including scratching and cleaning of Substation structures of 2nd coat of Aluminium .. | Painting Work | Painting of Work | As per relevent standard specification | 482 | TO | 4183.76
77 | SWR10867 | 8.68 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles,Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Erection Work | Erection of Work | As per relevent standard specification | 1470 | TO | 12759.6
78 | SWR10348 | 25 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, R.S. Joists 150 x 150 mm | Erection Work | Erection of Work | As per relevent standard specification | 1952.61 | EA | 48815.25
79 | SWR10356 | 27.75 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Mass concreting Work | Mass concreting of Work | As per relevent standard specification | 6579 | M3 | 182567.25
80 | SWR10862 | 14.44 | Plastering 2 Coats,20/16mm(1:6)(1:4) | Erection Work | Erection of Work | As per relevent standard specification | 373 | M2 | 5386.12
81 | SWR11089 | 25 | Paint of coping with 2 coats of white cement incl cost of paints etc. | Painting Work | Painting of Work | As per relevent standard specification | 48 | EA | 1200
82 | SWR10206 | 4.642 | LOADING of LINE MATERIALS M.S.Channels, Angles, Flats & Rods etc., | LOADING Work | LOADING of Work | As per relevent standard specification | 221 | TO | 1025.882
83 | SWR10132 | 4.642 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Upto 10 KM | Transport Work | Transport of Work | As per relevent standard specification | 412.08 | TO | 1912.8754
84 | SWR10524 | 4.642 | UN-LOADING of LINE MATERIALS M.S.Channels, Angles, Flats & Rods etc., | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 185 | TO | 858.77
85 | SWR10868 | 4.642 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RSJoist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Fabrication Work | Fabrication of Work | As per relevent standard specification | 6852 | TO | 31806.984
86 | SMR40009 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be appliedSupply of material cost for First coat of 1st Grade Aluminium Paint,brushes etc. | Painting Work | Painting of Work | As per relevent standard specification | 2181 | TO | 10124.202
87 | SWR10877 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be appliedLabour charges for painting including scratching and cleaning of Substation structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Painting Work | Painting of Work | As per relevent standard specification | 851 | TO | 3950.342
88 | SMR40010 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be appliedSupply of material cost for Second coat of 1st Grade Aluminium Paint,brushes, etc. | Painting Work | Painting of Work | As per relevent standard specification | 1293 | TO | 6002.106
89 | SWR10879 | 4.642 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be appliedLabour for 2nd coat Al. Painting. Labour charges for painting including scratching and cleaning of Substation structures of 2nd coat of Aluminium . | Painting Work | Painting of Work | As per relevent standard specification | 482 | TO | 2237.444
90 | SWR10867 | 4.642 | Fabrication & erection of Channels Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles,Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Fabrication Work | Fabrication of Work | As per relevent standard specification | 1470 | TO | 6823.74
91 | SWR10238 | 20 | LOADING of LINE MATERIALS 11KV AB Switch Conventional type | LOADING Work | LOADING of Work | As per relevent standard specification | 80 | EA | 1600
92 | SWR11861 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Transport of Cond Drum,VCBs >10 & <20Km | Transport Work | Transport of Work | As per relevent standard specification | 3299.7 | EA | 6599.4
93 | SWR10556 | 20 | UNLOADING of LINE MATERIALS11KV AB Switch Conventional type | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 80 | EA | 1600
94 | SWR21277 | 17 | Earth pit renovation Ere 11KV 800A double throw AB Switches | Erection Work | Erection of Work | As per relevent standard specification | 3500 | EA | 59500
95 | SWR10393 | 3 | Erection of AB Switch and aligment complete Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Erection Work | Erection of Work | As per relevent standard specification | 3200 | EA | 9600
96 | SWR10201 | 2 | LOADING of LINE MATERIALS of 11 KV CT - PT Sets | LOADING Work | LOADING of Work | As per relevent standard specification | 190 | EA | 380
97 | SWR11861 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Above 10 Km and upto 20 Km with Lorry for each trip | Transport Work | Transport of Work | As per relevent standard specification | 3299.7 | EA | 3299.7
98 | SWR10519 | 2 | UNLOADING of LINE MATERIALS of 11 KV CT - PT Sets | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 101 | EA | 202
99 | SWR10402 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV three phase PTs | Erection Work | Erection of Work | As per relevent standard specification | 800 | SET | 1600
100 | SWR10264 | 24 | LOADING of LINE MATERIALS of 11 KV,10 KA LAs Station type | LOADING Work | LOADING of Work | As per relevent standard specification | 32 | EA | 768
101 | SWR11861 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Above 10 Km and upto 20 Km with Lorry for each trip | Transport Work | Transport of Work | As per relevent standard specification | 3299.7 | EA | 3299.7
102 | SWR10582 | 24 | UNLOADING of LINE MATERIALS of 11 KV,10 KA LAs Station typ | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 32 | EA | 768
103 | SWR10397 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV LAS station type including earthing | Erection Work | Erection of Work | As per relevent standard specification | 559 | SET | 1118
104 | SWR10398 | 6 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV LAS line type including earthing | Erection Work | Erection of Work | As per relevent standard specification | 505 | SET | 3030
105 | SWR10199 | 8 | LOADING of LINE MATERIALS of 11 KV VCBs&Panel boards | LOADING Work | LOADING of Work | As per relevent standard specification | 1024 | EA | 8192
106 | SWR11861 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Above 10 Km and upto 20 Km with Lorry for each trip | Transport Work | Transport of Work | As per relevent standard specification | 3299.7 | EA | 13198.8
107 | SWR10517 | 8 | UNLOADING of LINE MATERIALS of 11 KV VCBs&Panel boards | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 1044.48 | EA | 8355.84
108 | SWR23224 | 41.6 | Excavate-Pit for 33KV VCB | Excavation Work | Excavation of Work | As per relevent standard specification | 331 | M3 | 13769.6
109 | SWR20685 | 48 | Cement concrete with 40MM metal VCB plin | Excavation Work | Excavation of Work | As per relevent standard specification | 5160 | M3 | 247680
110 | SWR10461 | 8 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV VCB with Control Panel | Erection Work | Erection of Work | As per relevent standard specification | 12000 | EA | 96000
111 | SMR11915 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Supply Work | Supply of Work | As per relevent standard specification | 2055 | SET | 24660
112 | SMR22473 | 12 | Supply of various Clamps Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy Supply of I Bolts | Supply Work | Supply of Work | As per relevent standard specification | 294 | EA | 3528
113 | SMR40011 | 45 | Supply of various Clamps Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . | Supply Work | Supply of Work | As per relevent standard specification | 299 | EA | 13455
114 | SWR10884 | 45 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Erection Work | Erection of Work | As per relevent standard specification | 224 | EA | 10080
115 | SWR10917 | 57 | Labour for Fixing of all types of clamps | Erection Work | Erection of Work | As per relevent standard specification | 65 | EA | 3705
116 | SWR10206 | 5.711 | LOADING of LINE MATERIALS of MS Channel,Angles,Flats&Rods | LOADING Work | LOADING of Work | As per relevent standard specification | 221 | TO | 1262.131
117 | SWR10132 | 5.711 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S.Channels etc., by lorries. (excluding of loading & unloading )Above 10 KM and upto 20 KM | Transport Work | Transport of Work | As per relevent standard specification | 412.08 | TO | 2353.3889
118 | SWR10524 | 5.711 | UNLOADING of LINE MATERIALS of MS Channel,Angles,Flats&Rod | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 185 | TO | 1056.535
119 | SWR10920 | 584 | Laying of earth mat including excavation of trenches of depth 600mm,welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication.75x 8mm MS Flat / GI Flat. | Excavation Work | Excavation of Work | As per relevent standard specification | 65 | RMT | 37960
120 | SWR10919 | 1010 | Fabrication and connecting to risers from earth mat to structures, equipment,marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Fabrication Work | Fabrication of Work | As per relevent standard specification | 41 | RMT | 41410
121 | SMR11482 | 36 | Supply of earthing pipe with materials iii)Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Supply Work | Supply of Work | As per relevent standard specification | 3486 | EA | 125496
122 | SWR10357 | 36 | Providing of earthing with excavation of earth pit (0.6x0.6x2.4 Mts.) duly filling with bentonite, earth ,running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.6M dia x 0.5 M height | Excavation Work | Excavation of Work | As per relevent standard specification | 1234.2 | EA | 44431.2
123 | SWR10359 | 36 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Earthing Work | Earthing of Work | As per relevent standard specification | 386 | EA | 13896
124 | SMR40033 | 4 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. | Supply Work | Supply of Work | As per relevent standard specification | 4725 | EA | 18900
125 | SWR11892 | 4 | Providing of earthing with various types of earth lectrodes.Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm. | Earthing Work | Earthing of Work | As per relevent standard specification | 1323 | EA | 5292
126 | SWR22093 | 80 | Providing of cable trench as per DATA-IX | Earthing Work | Earthing of Work | As per relevent standard specification | 3148 | RMT | 251840
127 | SWR11879 | 3074 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Excavation Work | Excavation of Work | As per relevent standard specification | 27 | M | 82998
128 | SWR12510 | 270 | L-Cable Termination to Switchgear | Erection Work | Erection of Work | As per relevent standard specification | 27 | EA | 7290
129 | SMR40048 | 4 | Supply of FRP PT Marshalling Box | Supply Work | Supply of Work | As per relevent standard specification | 4463 | EA | 17852
130 | SWR10940 | 4 | Erection of Marshalling boxes | Erection Work | Erection of Work | As per relevent standard specification | 374.85 | EA | 1499.4
131 | SWR11166 | 1 | LOADING of LINE MATERIALS220 V Battery with Charger | LOADING Work | LOADING of Work | As per relevent standard specification | 1612 | SET | 1612
132 | SWR11861 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Above 10 Km and upto 20 Km with Lorry for each trip | Transport Work | Transport of Work | As per relevent standard specification | 3299.7 | EA | 3299.7
133 | SWR11147 | 1 | UNLOADING of LINE MATERIALS 220 V Battery with Charger | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 1024 | SET | 1024
134 | SWR12350 | 1 | Erection of 220 V, 200 AH battery in complete shape fit for charging .Conventional lead acid | Erection Work | Erection of Work | As per relevent standard specification | 7666 | EA | 7666
135 | SMR40044 | 1 | Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. | Supply Work | Supply of Work | As per relevent standard specification | 42500 | EA | 42500
136 | SMR40045 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU,metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. | Supply Work | Supply of Work | As per relevent standard specification | 42000 | EA | 42000
137 | SWR20025 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | Supply Work | Supply of Work | As per relevent standard specification | 7871.85 | SET | 15743.7
138 | SMR40051 | 8 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Supply Work | Supply of Work | As per relevent standard specification | 13913 | EA | 111304
139 | SMR11594 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE /CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LEDMAKE: PHILIPS MILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty 90W LED fixture set | Supply Work | Supply of Work | As per relevent standard specification | 8200 | EA | 65600
140 | SWR10112 | 8 | Excavation of pits in hard rock requiring blasting. (other than SS)0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Excavation Work | Excavation of Work | As per relevent standard specification | 1770 | EA | 14160
141 | SWR10955 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE /CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LEDMAKE: PHILIPS MILEDS/CREE/NICHIA/OSRAM/SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty Errection of tubular poles | Supply Work | Supply of Work | As per relevent standard specification | 1379 | EA | 11032
142 | SWR10356 | 6.1 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc.Including the cost of cement | Erection Work | Erection of Work | As per relevent standard specification | 6579 | M3 | 40131.9
143 | SWR10956 | 8 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Erection Work | Erection of Work | As per relevent standard specification | 1268 | EA | 10144
144 | SWR10860 | 45 | Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | Supply Work | Supply of Work | As per relevent standard specification | 2113 | M3 | 95085
145 | SWR10204 | 3 | LOADING of LINE MATERIALS of R.S. Joists 175 x 85 mm | LOADING Work | LOADING of Work | As per relevent standard specification | 76 | EA | 228
146 | SWR10132 | 0.75 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S.Channels etc., by lorries. (excluding of loading & unloading )Above 10 KM and upto 20 KM | Transport Work | Transport of Work | As per relevent standard specification | 412.08 | TO | 309.06
147 | SWR10522 | 3 | UNLOADING of LINE MATERIALS of R.S. Joists 175 x 85 mm | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 50 | EA | 150
148 | SWR10112 | 2 | Excavation of pits in hard rock requiring blasting. (other than SS)0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Excavation Work | Excavation of Work | As per relevent standard specification | 1770 | EA | 3540
149 | SMR40009 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Supply of material cost for First coat of 1st Grade Aluminium Paint,brushes etc. | Painting Work | Painting of Work | As per relevent standard specification | 2181 | TO | 1635.75
150 | SWR10877 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Labour charges for painting including scratching and cleaning of Substation structures of 1st coat of Aluminium | Painting Work | Painting of Work | As per relevent standard specification | 851 | TO | 638.25
151 | SMR40010 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint,brushes, etc. | Painting Work | Painting of Work | As per relevent standard specification | 1293 | TO | 969.75
152 | SWR10879 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied (*) Labour charges for painting including scratching and cleaning of Substation structures of 2nd coat of Aluminium . | Painting Work | Painting of Work | As per relevent standard specification | 482 | TO | 361.5
153 | SWR11267 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-12Meter Box pole | Erection Work | Erection of Work | As per relevent standard specification | 3901.37 | EA | 7802.74
154 | SWR10356 | 1.97 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Erection Work | Erection of Work | As per relevent standard specification | 6579 | M3 | 12960.63
155 | SWR10862 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Erection Work | Erection of Work | As per relevent standard specification | 373 | M2 | 432.68
156 | SWR11089 | 2 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | Electrical Work | Painting of Work | As per relevent standard specification | 48 | EA | 96
157 | SWR21844 | 1 | RCC Column type DTR Plinth of size 1'X1'X13',topslab 5'x9'x9" & beam size 5'X9'X9" | Erection Work | Erection of Work | As per relevent standard specification | 25092 | EA | 25092
158 | SWR10195 | 1 | LOADING of LINE MATERIALS of 50,63,75&100kva DTR | LOADING Work | LOADING of Work | As per relevent standard specification | 350 | EA | 350
159 | SWR11861 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following ratesAbove 10 Km and upto 20 Km with Lorry for each trip | Transport Work | Transport of Work | As per relevent standard specification | 3299.7 | EA | 3299.7
160 | SWR10513 | 1 | UNLOADING of LINE MATERIALS of 50,63,75&100kva DTR | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 280 | EA | 280
161 | SWR20905 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc Erection of 3 Phase DTRs 63,75 & 100 KVA | Erection Work | Erection of Work | As per relevent standard specification | 1650 | EA | 1650
162 | SWR12406 | 1 | LOADING of LINE MATERIALS of 11 KV AB SWCH T.T.200/400 A | LOADING Work | LOADING of Work | As per relevent standard specification | 80 | EA | 80
163 | SWR12425 | 1 | UNLOADING of LINE MATERIALS of 11 KV AB SWCH T.T.200/400 A | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 80 | EA | 80
164 | SWR20102 | 1 | Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Erection Work | Erection of Work | As per relevent standard specification | 1813.49 | EA | 1813.49
165 | SWR10231 | 1 | LOADING of LINE MATERIALS of 11 KV HG Fuse Sets | LOADING Work | LOADING of Work | As per relevent standard specification | 18 | EA | 18
166 | SWR10549 | 1 | UNLOADING of LINE MATERIALS of 11 KV HG Fuse Sets | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 18 | EA | 18
167 | SWR10395 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV HG Fuse set including earthing | Erection Work | Erection of Work | As per relevent standard specification | 740.52 | SET | 740.52
168 | SWR11920 | 40 | Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-SR 11KV 3x185sqmm UG Cb HG/BC/CC/BT 11KV 3x185 Sqmm Cable | Laying Work | Laying of Work | As per relevent standard specification | 465.46 | M | 18618.4
169 | SWR11956 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)11 KV 3x185 Sqmm Cable | Raising Work | Raising of Work | As per relevent standard specification | 126.23 | M | 2524.6
170 | SWR10390 | 2 | Making of Outdoor/Indoor End Termination 11 KV 3x185 Sqmm Cable | End Termination Work | End Termination of Work | As per relevent standard specification | 2370.63 | EA | 4741.26
171 | SWR10674 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc | Erection Work | Erection of Work | As per relevent standard specification | 1594.67 | EA | 1594.67
172 | SWR11923 | 85 | Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.LT 3 1/2 x 185 Sqmm Cable | Laying Work | Laying of Work | As per relevent standard specification | 377.63 | M | 32098.55
173 | SWR11959 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)LT 3 1/2 x 185 Sqmm Cable | Raising Work | Raising of Work | As per relevent standard specification | 85.43 | M | 1281.45
174 | SMR40140 | 2 | Making of Outdoor/Indoor End Termination Supply of 31/2x185Sqmm UG O/D end term kits | End Termination Work | End Termination of Work | As per relevent standard specification | 550 | EA | 1100
175 | SWR10765 | 2 | Making of Outdoor/Indoor End Termination Supply of 31/2x185Sqmm UG O/D end term kits | End Termination Work | End Termination of Work | As per relevent standard specification | 968.9 | EA | 1937.8
176 | SWR20032 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard | Supply Work | Supply of Work | As per relevent standard specification | 1654 | EA | 1654
177 | SWR22090 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Supply Work | Supply of Work | As per relevent standard specification | 2205 | EA | 2205
178 | SWR10873 | 750 | Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field | Supply Work | Supply of Work | As per relevent standard specification | 83 | KG | 62250
179 | SMR40059 | 1 | Supply of Wall clock standard make | Supply Work | Supply of Work | As per relevent standard specification | 578 | EA | 578
180 | SMR12378 | 1 | S-10ft Aluminium Ladder | Supply Work | Supply of Work | As per relevent standard specification | 1654 | EA | 1654
181 | SMR40062 | 1 | Sup Alluminium Ladder for indoor works | Supply Work | Supply of Work | As per relevent standard specification | 4410 | EA | 4410
182 | SWR10963 | 30 | T&P Painting of Name Plates for any equipmen | Supply Work | Supply of Work | As per relevent standard specification | 122 | EA | 3660
183 | SMR40063 | 1 | T&P Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8”with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 -1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579-1985 Grade:II handle yellow/green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. | Supply Work | Supply of Work | As per relevent standard specification | 4925 | SET | 4925
184 | SMR40064 | 1 | T&P Sup Rechargeable LED torch light. | Supply Work | Supply of Work | As per relevent standard specification | 1733 | EA | 1733
185 | SMR40061 | 1 | T&P Sup Steel almarah(61/2 X 3ft) Godrej | Supply Work | Supply of Work | As per relevent standard specification | 9818 | EA | 9818
186 | SMR40057 | 1 | T&P Supply of Table (3x6ft) Godrej | Supply Work | Supply of Work | As per relevent standard specification | 6050 | EA | 6050
187 | SMR40058 | 4 | T&P Supply of S type chairs (Godrej) | Supply Work | Supply of Work | As per relevent standard specification | 924 | EA | 3696
188 | SMR40060 | 1 | T&P Sup Angle racks(18x36.6inches) Godrej | Supply Work | Supply of Work | As per relevent standard specification | 1733 | EA | 1733
189 | SMR40065 | 1 | T&P Supply of Hack saw (12 inches) | Supply Work | Supply of Work | As per relevent standard specification | 289 | EA | 289
190 | SMR40066 | 4 | Earth rods with (1) reputed make ISI PVC pipe of 5 feet length, 3 mm thickness, 32 mm dia inside cane wood stick closed both top & bottom ends with caps, (2) reputed make ISI (Finolex/ Polycab/Havells) first quality flexible PVC wire of 6 Sq.mm multi-strand copper 10 Mtrs length one side crimped with a suitable copper lug, other side fixed with a lug, bolt & nut to a suitable 3 inch long copper heavy duty crocodile clip having insulated sleeves, (3) Copper flat of size 25 mm width 3 mm thick 250 mm length make hook shape fixed to the PVC pipe with 2 No.s 6 mm dia 65 mm length hot dip galvanized bolts triple nuts with a 2 mm thick spring washer and 1 mm thick 4 flat washers and fixing of the copper wire to the bolts with lugs. Sup Earth Rods (8ft) Screw & clamp type | Supply Work | Supply of Work | As per relevent standard specification | 578 | EA | 2312
191 | SMR40067 | 2 | Supply of Hand Gloves | Supply Work | Supply of Work | As per relevent standard specification | 289 | SET | 578
192 | SMR40068 | 12 | SupRubber mats( 6’x3’)size for indoorSS | Supply Work | Supply of Work | As per relevent standard specification | 1386 | EA | 16632
193 | SMR40069 | 1 | Sup Stand basic cell phone with charger | Supply Work | Supply of Work | As per relevent standard specification | 1386 | EA | 1386
194 | SMR40070 | 14 | Supply of Danger boards with clamps | Supply Work | Supply of Work | As per relevent standard specification | 116 | EA | 1624
195 | SMR40088 | 2 | Sup Fire Buckets Stand with Buckets | Supply Work | Supply of Work | As per relevent standard specification | 1386 | SET | 2772
196 | SMR40089 | 2 | Sup Fire Extinguisher for Control Room | Supply Work | Supply of Work | As per relevent standard specification | 4620 | EA | 9240
197 | SMR40087 | 4 | Sup TrollyMounted Co2 Cylinders(IS-2878) | Supply Work | Supply of Work | As per relevent standard specification | 9240 | EA | 36960
198 | SMR40071 | 6 | Supply of Safety Helmet of standard make | Supply Work | Supply of Work | As per relevent standard specification | 231 | EA | 1386
199 | SMR40072 | 8 | Supply of LC Boards | Supply Work | Supply of Work | As per relevent standard specification | 116 | EA | 928
200 | SMR40073 | 4 | Supply of Gum Boots | Supply Work | Supply of Work | As per relevent standard specification | 693 | EA | 2772
201 | SMR40074 | 1 | Supply of 5000v megger | Supply Work | Supply of Work | As per relevent standard specification | 13860 | EA | 13860
202 | SMR40075 | 1 | Supply of Earth megger (1000v) | Supply Work | Supply of Work | As per relevent standard specification | 8085 | EA | 8085
203 | SMR40076 | 1 | Supply of Digital clamp meter. | Supply Work | Supply of Work | As per relevent standard specification | 2888 | EA | 2888
204 | SMR40086 | 1 | Sup 33/11kv S.S Permanent name board | Supply Work | Supply of Work | As per relevent standard specification | 10238 | EA | 10238
205 | SMR12488 | 800 | S-Hot dip gal./Zinc bolts & nuts washer | Supply Work | Supply of Work | As per relevent standard specification | 90 | KG | 72000
206 | SWR11039 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Excavation Work | Excavation of Work | As per relevent standard specification | 928 | EA | 7424
207 | SWR21241 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Stringing Work | Stringing of Work | As per relevent standard specification | 507 | EA | 1014
208 | SWR10204 | 16 | LOADING of LINE MATERIALS of R.S. Joists 175 x 85 mm | LOADING Work | LOADING of Work | As per relevent standard specification | 76 | EA | 1216
209 | SWR10132 | 4 | TRANSPORT OF STEEL 10 TO 20KM | TRANSPORTWork | TRANSPORT of Work | As per relevent standard specification | 412.08 | TO | 1648.32
210 | SWR10522 | 16 | UNLOADING of LINE MATERIALS of R.S. Joists 175 x 85 mm | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 50 | EA | 800
211 | SWR10112 | 8 | Excavation of pits in hard rock requiring blasting. (other than SS)0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Excavation Work | Excavation of Work | As per relevent standard specification | 1770 | EA | 14160
212 | SMR40009 | 4 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Supply of material cost for First coat of 1st Grade Aluminium Paint,brushes etc. | sub-station Work | sub-station of Work | As per relevent standard specification | 2181 | TO | 8724
213 | SWR10877 | 4 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Labour charges for painting including scratching and cleaning of Substation structures of 1st coat of Aluminium. | sub-station Work | sub-station of Work | As per relevent standard specification | 851 | TO | 3404
214 | SMR40010 | 4 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint,brushes, etc. | sub-station Work | sub-station of Work | As per relevent standard specification | 1293 | TO | 5172
215 | SWR10879 | 4 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied (*) Labour charges for painting including scratching and cleaning of Substation structures of 2nd coat of Aluminium . | sub-station Work | sub-station of Work | As per relevent standard specification | 482 | TO | 1928
216 | SWR10356 | 5.292 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc.Including the cost of cement | Erection Work | Erection of Work | As per relevent standard specification | 6579 | M3 | 34816.068
217 | SWR10862 | 4.62 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | sub-station Work | sub-station of Work | As per relevent standard specification | 373 | M2 | 1723.26
218 | SWR11089 | 8 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | sub-station Work | sub-station of Work | As per relevent standard specification | 48 | EA | 384
219 | SWR10881 | 20 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be appliedPainting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | sub-station Work | sub-station of Work | As per relevent standard specification | 142 | EA | 2840
220 | SWR12331 | 20 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Earthing Work | Earthing of Work | As per relevent standard specification | 146.63 | EA | 2932.6
221 | SWR20769 | 1.44 | Earth work excavation of pits in hard rock requiring blasting. | Earthing Work | Earthing of Work | As per relevent standard specification | 1012.35 | M3 | 1457.784
222 | SWR11702 | 4 | LOADING of LINE MATERIALS - LT AB Cb 3x16+25sqmm | LOADING Work | LOADING of Work | As per relevent standard specification | 200 | DR | 800
223 | SWR11861 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 10 Km and upto 20 Km with Lorry for each trip | TRANSPORTWork | TRANSPORT of Work | As per relevent standard specification | 3299.7 | EA | 3299.7
224 | SWR11713 | 4 | UNLOADING of LINE MATERIALS-LT AB Cb 3x16+25sqmm | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 204 | DR | 816
225 | SWR11267 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Box pole 12 Mtr | Erection Work | Erection of Work | As per relevent standard specification | 3901.37 | EA | 31210.96
226 | SMR12302 | 5760 | Supply of Materials, RS Joist girder Poles (150X150mm | Supply Work | Supply of Work | As per relevent standard specification | 59.25 | KG | 341280
227 | SMR12303 | 1000 | Supply of Materials RS Joist Poles (175X85mm) | Supply Work | Supply of Work | As per relevent standard specification | 60.75 | KG | 60750
228 | SMR22745 | 5063 | Supply of Materials,MS Channel 100X50mm | Supply Work | Supply of Work | As per relevent standard specification | 57.45 | KG | 290869.35
229 | SMR12315 | 12 | Supply of Materials, Supply of 33 kV 800 A Double break AB switch | Supply Work | Supply of Work | As per relevent standard specification | 40658.78 | EA | 487905.36
230 | SMR12302 | 8680 | Supply of Materials, RS Joist girder Poles (150X150mm | Supply Work | Supply of Work | As per relevent standard specification | 59.25 | KG | 514290
231 | SMR22745 | 4642 | Supply of Materials,MS Channel 100X50mm | Supply Work | Supply of Work | As per relevent standard specification | 57.45 | KG | 266682.9
232 | SMR12316 | 17 | Supply of Materials 11 kV 800 A Double break AB switch | Supply Work | Supply of Work | As per relevent standard specification | 30847.46 | EA | 524406.82
233 | SMR25211 | 3 | Supply of Materials 11 kV 400 A Conv AB switch with insulator. | Supply Work | Supply of Work | As per relevent standard specification | 11754 | EA | 35262
234 | SMR12303 | 750 | Supply of Materials RS Joist Poles (175X85mm) | Supply Work | Supply of Work | As per relevent standard specification | 60.75 | KG | 45562.5
235 | SMR12318 | 1 | Supply of Materials 11 kV 200 A Tilting type AB switchr. | Supply Work | Supply of Work | As per relevent standard specification | 8991 | EA | 8991
236 | SMR12324 | 1 | Supply of Materials 11 kV HG Fuse Set for Station Transformer. | Supply Work | Supply of Work | As per relevent standard specification | 1974 | EA | 1974
237 | SMR25200 | 1 | Supply of Materials LT Distribution Box(SMC). | Supply Work | Supply of Work | As per relevent standard specification | 7797 | EA | 7797
238 | SMR25201 | 2 | Supply of Materials 3x185 Heat Shble O/d End Term Kit | Supply Work | Supply of Work | As per relevent standard specification | 1182.97 | EA | 2365.94
239 | SMR25203 | 40 | Supply of Materials LT XLPE Cable 1C 150sqmm | Supply Work | Supply of Work | As per relevent standard specification | 114.83 | M | 4593.2
240 | SMR25204 | 100 | Supply of Materials LT XLPE Cable 31/2 C 185 sqmm | Supply Work | Supply of Work | As per relevent standard specification | 547 | M | 54700
241 | SMR12321 | 3045 | Supply of Materials MS Flat 75x8mm | Supply Work | Supply of Work | As per relevent standard specification | 56.42 | KG | 171798.9
242 | SMR12322 | 2666 | Supply of Materials MS Flat 50x6mm | Supply Work | Supply of Work | As per relevent standard specification | 56.5 | KG | 150629
243 | SMR12303 | 4000 | Supply of Materials RS Joist Poles (175X85mm) | Supply Work | Supply of Work | As per relevent standard specification | 60.75 | KG | 243000
244 | SWR10191 | 7 | LOADING of LINE MATERIALS of Conductor drums | LOADING Work | LOADING of Work | As per relevent standard specification | 202 | EA | 1414
245 | SWR11861 | 7 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 10 Km and upto 20 Km with Lorry for each trip | TRANSPORTWork | TRANSPORT of Work | As per relevent standard specification | 3299.7 | EA | 23097.9
246 | SWR10509 | 7 | UNLOADING of LINE MATERIALS of Conductor drums | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 100 | EA | 700
247 | SWR10704 | 4 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location.100 Sqmm Double Circuit (6 Conductors) | Stringing Work | Stringing Work | As per relevent standard specification | 26255.98 | KM | 105023.92
248 | SWR10366 | 3 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location.100 Sqmm Single Circuit (3 Conductors) | Stringing Work | Stringing of Work | As per relevent standard specification | 13856.7 | KM | 41570.1
249 | SWR10981 | 20 | Formation of Cut point for 33 KV Single Circuit line excluding pole erection and stays | Formation Work | Formation of Work | As per relevent standard specification | 1791.12 | EA | 35822.4
250 | SWR11230 | 4 | LOADING of LINE MATERIALS-11/33KV XLPE UG Cable for all sizes | LOADING Work | LOADING of Work | As per relevent standard specification | 1024 | DR | 4096
251 | SWR11231 | 4 | UNLOADING of LINE MATERIALS-11/33KV XLPE UG Cable all sizes | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 1024 | DR | 4096
252 | SWR25024 | 4 | Transport-33KV 3x400sqmm Cb Drum to 50km | Electrical Work | Transportation of work | As per relevent standard specification | 21423 | EA | 85692
253 | SWR10382 | 12 | UG Cables Joints :Making of Straight through joints 33 KV 3x400 Sqmm Cable | Electrical Work | Electrical Work | As per relevent standard specification | 5700.78 | EA | 68409.36
254 | SWR10387 | 12 | Making of Outdoor/Indoor End Termination 33 KV 3x400 Sqmm Cable | Electrical Work | Electrical Work | As per relevent standard specification | 2764.76 | EA | 33177.12
255 | SWR25089 | 6 | S&E-Smart RFID marker | Electrical Work | Electrical Work | As per relevent standard specification | 2745 | EA | 16470
256 | SWR11801 | 1000 | Consultation charges for pursuing with various Departments for obtaining required permissions for Road cutting and submission of necessry Documents, Drawings etc. | Electrical Work | Electrical Work | As per relevent standard specification | 38.25 | M | 38250
257 | SWR10239 | 1 | LOADING of LINE MATERIALSof 33 KV AB SWCH Con 400/800 A | LOADING Work | LOADING of Work | As per relevent standard specification | 126 | EA | 126
258 | SWR10557 | 1 | UNLOADING of LINE MATERIALS of 33 KV AB SWCH Con 400/800 A | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 79 | EA | 79
259 | SWR10881 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical Work | Painting of Work | As per relevent standard specification | 142 | EA | 142
260 | SWR12331 | 1 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Earthing Work | Earthing of Work | As per relevent standard specification | 146.63 | EA | 146.63
261 | SWR10204 | 4 | LOADING of LINE MATERIALS of R.S. Joists 175 x 85 mm | LOADING Work | LOADING of Work | As per relevent standard specification | 76 | EA | 304
262 | SWR10132 | 1 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Transportationwork | Transportation work | As per relevent standard specification | 412.08 | TO | 412.08
263 | SWR10522 | 4 | UNLOADING of LINE MATERIALS of R.S. Joists 175 x 85 mm | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 50 | EA | 200
264 | SMR40009 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Sup Material for 1st coat Al. Painting. | Electrical Work | Painting of Work | As per relevent standard specification | 2181 | TO | 2181
265 | SWR10877 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be appliedLabour for 1st coat Al. Painting. Labour charges for painting including scratching and cleaning of Substation structures of 1st coat of Aluminium | Electrical Work | Painting of Work | As per relevent standard specification | 851 | TO | 851
266 | SMR40010 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be appliedSup Material for 2nd coat Al. Painting. | Electrical Work | Painting of Work | As per relevent standard specification | 1293 | TO | 1293
267 | SWR10879 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Labour for 2nd coat Al. Painting. | Electrical Work | Painting of Work | As per relevent standard specification | 482 | TO | 482
268 | SWR11037 | 50 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)Ex of Hard pit w/o blast 0.76X0.76X1.52M | Electrical Work | Excavation of Work | As per relevent standard specification | 793 | EA | 39650
269 | SWR10356 | 1.323 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Mass concreting of supports incl. cement | Electrical Work | Painting of Work | As per relevent standard specification | 6579 | M3 | 8704.017
270 | SWR10862 | 1.155 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Electrical Work | Painting of Work | As per relevent standard specification | 373 | M2 | 430.815
271 | SWR11089 | 2 | Paint of coping with 2 coats of white cement incl cost of paints etc. | Electrical Work | Painting of Work | As per relevent standard specification | 48 | EA | 96
272 | SWR10206 | 0.264 | LOADING of LINE MATERIALS of MS Channel,Angles,Flats&Rods | LOADING Work | LOADING of Work | As per relevent standard specification | 220.98 | TO | 58.3387
273 | SWR10524 | 0.264 | UNLOADING of LINE MATERIALS of MS Channel,Angles,Flats&Rod | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 185 | TO | 48.84
274 | SMR40009 | 0.264 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Sup Material for 1st coat Al. Painting. | Electrical Work | Painting of Work | As per relevent standard specification | 2180.98 | TO | 575.7787
275 | SWR10877 | 0.264 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be appliedLabour for 1st coat Al. Painting. | Electrical Work | Painting of Work | As per relevent standard specification | 850.98 | TO | 224.6587
276 | SMR40010 | 0.264 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding Sup Material for 2nd coat Al. Painting. | Electrical Work | Painting of Work | As per relevent standard specification | 1292.99 | TO | 341.3494
277 | SWR10879 | 0.264 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be appliedLabour for 2nd coat Al. Painting. | Electrical Work | Painting of Work | As per relevent standard specification | 482.01 | TO | 127.2506
278 | SWR10392 | 1 | Erection of 33 KV AB Switch including alignment and earthing | Electrical Work | Erection of Work | As per relevent standard specification | 4500 | EA | 4500
279 | SWR23200 | 2500 | Cut-Tree Branch(LT/11/33)&Trnsprt Debris | Electrical Work | Cutting of Work | As per relevent standard specification | 4 | EA | 10000
280 | SMR40081 | 60 | S-6" B Class GI pipe 5mm thck 20Kg/M | Electrical Work | Supply of Work | As per relevent standard specification | 1044 | M | 62640
281 | SWR10108 | 100 | Excavation of pits 0.75 M x 0.9 M x 1.95 M in all soils except hard rock requiring blasting | Electrical Work | Excavation of Work | As per relevent standard specification | 629.85 | EA | 62985
282 | SWR10109 | 40 | Excavation of pits (3.0" x 3.0" x 7.6") in all soils except hard rock requiring blasting | Electrical Work | Excavation of Work | As per relevent standard specification | 842.78 | EA | 33711.2
283 | SWR10350 | 150 | Erection of Spun poles 12.5 Mtrs / 12.9Mtrs PSCC pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Electrical Work | Excavation of Work | As per relevent standard specification | 4521.66 | EA | 678249
284 | SWR11185 | 150 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading) | Electrical Work | Sub-transport of work | As per relevent standard specification | 771.38 | EA | 115707
285 | SWR20308 | 40 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | Electrical Work | Sub-transport of work | As per relevent standard specification | 407.29 | EA | 16291.6
286 | SWR10354 | 20 | Assembly and erection of stay set 33kv including fixing of guy insulators, clamps etc., on the pole and fixing stay wire and binding securely on either side as per standards, transport of material from road side to location and back filling with earth ramming | Electrical Work | Erection of work | As per relevent standard specification | 684.53 | SET | 13690.6
287 | SWR10988 | 900 | Laying of the cable along the footpath through 225mm dia GI pipe for 33KV, 150mm dia GI pipe for 11KV (excluding the cost of GI pipe) Lay-2nd Cable in Excavated Trench | Electrical Work | Excavation of Work | As per relevent standard specification | 204.1 | M | 183690
288 | SWR10978 | 40 | Erection of 11 M pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. | Electrical Work | Erection of work | As per relevent standard specification | 4336.85 | EA | 173474
289 | SWR10356 | 81 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc incl.Including the cost of cement | Electrical Work | Erection of work | As per relevent standard specification | 6579 | M3 | 532899
290 | SMR22223 | 12 | Supply of materials 33KV 3x400 sqmm Straight thr kit | Supply Work | Supply of Work | As per relevent standard specification | 24151 |  | 289812
291 | SMR22222 | 12 | Supply of materials 33KV 3x400 sqmm O/D End Kit | Supply Work | Supply of Work | As per relevent standard specification | 4554 |  | 54648
292 | SMR12315 | 1 | Supply of materials 33KV 800A DB Break AB Switch | Supply Work | Supply of Work | As per relevent standard specification | 40658.78 | EA | 40658.78
293 | SMR12303 | 1000 | Supply of Materials RS Joist Poles (175X85mm) | Supply Work | Supply of Work | As per relevent standard specification | 60.75 |  | 60750
294 | SMR22745 | 3000 | Supply of Materials MS Channel 100x50mm | Supply Work | Supply of Work | As per relevent standard specification | 57.45 |  | 172350
295 | SMR12322 | 500 | Supply of Materials MS Flat 50x6 mm | Supply Work | Supply of Work | As per relevent standard specification | 56.5 |  | 28250
296 | SMR12321 | 875 | Supply of Materials MS Flat 75x8mm | Supply Work | Supply of Work | As per relevent standard specification | 56.42 |  | 49367.5
297 | SMR25236 | 40 | Supply of Materials PSCC 11Mtr 365kg | Supply Work | Supply of Work | As per relevent standard specification | 5399 |  | 215960
298 | SMR25238 | 150 | Supply of Materials PSCC Spun Pole 12.5Mtr | Supply Work | Supply of Work | As per relevent standard specification | 15635.59 |  | 2345338.5
299 | SWR11954 | 150 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) 33 KV 3x400 Sqmm Cable | Electrical Work | Raising of work | As per relevent standard specification | 135.66 |  | 20349
300 | SWR12019 | 450 | Laying of XLPE UG cable Triple or more Run including excavation of trench of size 1000mm wide to 750mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.33 KV 3x400 Sqmm Cable | Electrical Work | Laying of work | As per relevent standard specification | 1731.45 |  | 779152.5
301 | SWR12413 | 3 | LOADING of LINE MATERIALS of 11 KV AB Cable (XLPE) 3 Core | LOADING Work | LOADING of Work | As per relevent standard specification | 584 | DR | 1752
302 | SWR12431 | 3 | UNLOADING of LINE MATERIALS of 11 KV AB Cable (XLPE) 3 Cor | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 438 | DR | 1314
303 | SWR11861 | 2 | Transport of conductor drums, cable drums, fragile materialVCBs >10 & <20Km such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) | Transport work | Transport of work | As per relevent standard specification | 3299.7 | EA | 6599.4
304 | SWR24971 | 2 | Supply and erection of T-Branch kit | Supply and erection work | Supply and erection of work | As per relevent standard specification | 3215 | EA | 6430
305 | SWR10671 | 2 | Erection of Assemble Kit for 'T' Branche | Erection work | Erection of work | As per relevent standard specification | 1800 | EA | 3600
306 | SMR11485 | 150 | Supply of earthing pipe GI flat 25x3 with materials | Supply of Earthing work | Supply of Earthing work | As per relevent standard specification | 105 | KG | 15750
307 | SWR10366 | 4.1 | Paving out and stringing of conductor 100sqmm 33/11kv Line 3 Cond SC by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location | Stringing work | Stringing of work | As per relevent standard specification | 13856.7 | KM | 56812.47
308 | SWR10704 | 1.1 | Paving out and stringing of conductor 100sqmm 33/11kv Line 6 Cond DC by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location. | Stringing work | Stringing of work | As per relevent standard specification | 26255.98 | KM | 28881.578
309 | SWR10191 | 3 | LOADING of LINE MATERIALS of Conductor drums | LOADING Work | LOADING of Work | As per relevent standard specification | 202 | EA | 606
310 | SWR11861 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, >10 & <20Km control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) | Transport work | Transport of work | As per relevent standard specification | 3299.7 | EA | 3299.7
311 | SWR10509 | 6 | UNLOADING of LINE MATERIALS of Conductor drums | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 100 | EA | 600
312 | SWR10653 | 20 | Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays | Formation Work | Formation of Work | As per relevent standard specification | 1435.81 | EA | 28716.2
313 | SWR10188 | 40 | LOADING of LINE MATERIALS of 9.1M PSCC POLE | LOADING Work | LOADING of Work | As per relevent standard specification | 182 | EA | 7280
314 | SWR10506 | 40 | UNLOADING of LINE MATERIALS of 9.1M PSCC POLE | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 91 | EA | 3640
315 | SWR10343 | 40 | Erection of pole in 9.1M position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Erection work | Erection of work | As per relevent standard specification | 2400 | EA | 96000
316 | SWR10393 | 12 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Erection work | Erection of work | As per relevent standard specification | 3200 | EA | 38400
317 | SWR10238 | 6 | LOADING of LINE MATERIALS of 11 KV AB SWCH Con 200/400 A | LOADING Work | LOADING of Work | As per relevent standard specification | 80 | EA | 480
318 | SWR10556 | 6 | UNLOADING of LINE MATERIALS of 11 KV AB SWCH Con 200/400 A | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 80 | EA | 480
319 | SWR11861 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) >10 & <20Km | Transport work | Transport of work | As per relevent standard specification | 3299.7 | EA | 6599.4
320 | SWR10881 | 6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be appliedPainting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical Work | Painting of Work | As per relevent standard specification | 142 | EA | 852
321 | SWR12331 | 6 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Earthing Work | Earthing of Work | As per relevent standard specification | 146.63 | EA | 879.78
322 | SWR10391 | 12 | Making of Straight through joints of Outdoor/Indoor End Termination 11kv 3x300 xlpe | End Termination Work | End Termination of Work | As per relevent standard specification | 2370.63 | EA | 28447.56
323 | SWR10386 | 12 | Making of Straight through joints 11kv 3x300 xlpe | End Termination Work | End Termination of Work | As per relevent standard specification | 3725.45 | EA | 44705.4
324 | SWR11230 | 5 | LOADING of LINE MATERIALS-11/33KV XLPE UG Cable for all sizes | LOADING Work | LOADING of Work | As per relevent standard specification | 1024 | DR | 5120
325 | SWR11231 | 5 | UNLOADING of LINE MATERIALS-11/33KV XLPE UG Cable all sizes | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 1024 | DR | 5120
326 | SWR11861 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) >10 & <20Km | Transport work | Transport of work | As per relevent standard specification | 3299.7 | EA | 16498.5
327 | SWR11172 | 4 | LOADING of LINE MATERIALS 11/33KV Straight thr jointkit | LOADING Work | LOADING of Work | As per relevent standard specification | 8 | EA | 32
328 | SWR11153 | 4 | UNLOADING of LINE MATERIALS 11/33KV Straight thr jointkit | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 4 | EA | 16
329 | SWR10206 | 2.89 | LOADING of LINE MATERIALS of MS Channel,Angles,Flats&Rods | LOADING Work | LOADING of Work | As per relevent standard specification | 221 | TO | 638.69
330 | SWR10524 | 2.89 | UNLOADING of LINE MATERIALS of MS Channel,Angles,Flats&Rod | UNLOADING Work | UNLOADING of Work | As per relevent standard specification | 185 | TO | 534.65
331 | SWR10132 | 2.89 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )10 TO 20KM | Transport work | Transport of work | As per relevent standard specification | 412.08 | TO | 1190.9112
332 | SMR40009 | 2.89 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Electrical Work | Painting of Work | As per relevent standard specification | 2181 | TO | 6303.09
333 | SWR10877 | 2.89 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be appliedLabour charges for painting including scratching and cleaning of Substation structures of 1st coat of Aluminium | Electrical Work | Painting of Work | As per relevent standard specification | 851 | TO | 2459.39
334 | SMR40010 | 2.89 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Electrical Work | Painting of Work | As per relevent standard specification | 1293 | TO | 3736.77
335 | SWR10879 | 2.89 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Labour charges for painting including scratching and cleaning of Substation structures of 2nd coat of Aluminium . | Electrical Work | Painting of Work | As per relevent standard specification | 482 | TO | 1392.98
336 | SWR23200 | 3000 | Cut-Tree Branch(LT/11/33)&Trnsprt Debris | Transport work | Transport of work | As per relevent standard specification | 4 | EA | 12000
337 | SMR40080 | 210 | S-4" BClass GI pipe 3.65mm thck 12.2Kg/M | Transport work | Transport of work | As per relevent standard specification | 740 | M | 155400
338 | SWR10988 | 900 | Laying of the 2nd Cable in Excavated Trench along the footpath through 225mm dia GI pipe for 33KV, 150mm dia GI pipe for 11KV (excluding the cost of GI pipe)Lay-2nd Cable in Excavated Trench | Laying Work | Laying of Work | As per relevent standard specification | 204.1 | M | 183690
339 | SWR11039 | 135 | Excavation of pits w/o blast 0.76X0.76X1.83M in hard rock not requiring blasting. (In hard murram / rock boulders) | Excavation Work | Excavation of Work | As per relevent standard specification | 928 | EA | 125280
340 | SWR10921 | 100 | Laying of earth mat GI Flat 25 x 3 mm (including material) including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication. | Laying Work | Laying of Work | As per relevent standard specification | 68 | RMT | 6800
341 | SWR12104 | 1 | Submission of auto CAD Drawing as per pole schedule (Detailed survey and sketch CAD Drawing per pole upto 10KM | Survey Work | Survey of Work | As per relevent standard specification | 6000 | LS | 6000
342 | SWR10110 | 40 | Excavation of pits 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum in hard rock requiring blasting. | Excavation Work | Excavation of Work | As per relevent standard specification | 1514 | EA | 60560
343 | SWR11180 | 135 | Sub-transport of poles 11M PSCC Pole incl. L&U upto Workspot upto 10KM (Including loading and unloading) | Sub-transport Work | Sub-transport of Work | As per relevent standard specification | 431.97 | EA | 58315.95
344 | SWR20308 | 40 | Sub-transport of 9M PSCC Poles incl. L&UL Workspot upto 10KM (Including loading and unloading) | Sub-transport Work | Sub-transport of Work | As per relevent standard specification | 407.29 | EA | 16291.6
345 | SWR10978 | 135 | Erection of 11 M long PSCC pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Erection work | Erection of work | As per relevent standard specification | 4336.85 | EA | 585474.75
346 | SWR10356 | 72 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. | Mass concreting work | Mass concreting of work | As per relevent standard specification | 6579 | M3 | 473688
347 | SWR10320 | 175 | Fabrication of materials including 2 coats of Red oxide painting Fab Back clamps with 50 x 6 mm MS Flat | Fabrication Work | Fabrication of Work | As per relevent standard specification | 15 | EA | 2625
348 | SWR10313 | 175 | Fabrication of materials including 2 coats of Red oxide painting 1.07 mt. V. Cross arms with 75 x 40 mm MS Channel | Fabrication Work | Fabrication of Work | As per relevent standard specification | 114.09 | EA | 19965.75
349 | SMR12322 | 470 | Supply of materials Ms Flat 50x6mm | Supply Work | Supply of Work | As per relevent standard specification | 56.5 | KG | 26555
350 | SMR25211 | 12 | Supply of materials 11KV 400A Conv AB Switch with insulators | Supply Work | Supply of Work | As per relevent standard specification | 11754 | EA | 141048
351 | SMR22475 | 330 | Supply of materials Ms Channel 100x50mm | Supply Work | Supply of Work | As per relevent standard specification | 57.45 | KGS | 18958.5
352 | SMR25207 | 90 | Supply of materials MsAngle 65x65x6 | Supply Work | Supply of Work | As per relevent standard specification | 57.25 | KG | 5152.5
353 | SMR25205 | 1500 | Supply of materials Ms Channel 75x40 mm | Supply Work | Supply of Work | As per relevent standard specification | 58.45 | KG | 87675
354 | SMR25209 | 12 | Supply of materials11KV 3x300Heat Shble I/D End Ter Kit | Supply Work | Supply of Work | As per relevent standard specification | 1459.83 | EA | 17517.96
355 | SMR25210 | 12 | Supply of materials11KV 3x300Heat Shble Straight thr joint kit | Supply Work | Supply of Work | As per relevent standard specification | 4110.17 | EA | 49322.04
356 | SMR25236 | 135 | Supply of materials PSCC Pole 11Mtr 365KG | Supply Work | Supply of Work | As per relevent standard specification | 5399 | EA | 728865
357 | SMR25233 | 40 | Supply of materials PSCC Pole9.1 Mtr 280KG | Supply Work | Supply of Work | As per relevent standard specification | 3109.41 | EA | 124376.4
358 | SWR11955 | 400 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)11 KV 3x300 Sqmm Cable | Electrical Work | Raising of work | As per relevent standard specification | 144.08 | M | 57632
359 | SWR12042 | 400 | Laying of XLPE UG cable Triple or more Run including excavation of trench of size 1000mm wide to 750mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.33 KV 3x400 Sqmm Cable | Electrical Work | Laying of work | As per relevent standard specification | 2033.63 | M | 813452
|  |  | Total Schedule Cost. (Excluding GST) | [5 empty] | 17466445.1618
1 |  | 1 | Geophysical investigation charges | Geophysical investigation | Geophysical investigation | As per relevent standard specification | 5000 | EA | 5000
2 |  | 90 | Drilling of 6.5" dia bore well from ground level in all formations including cost and conveyance of all materials labour charges etc., complete for finished item of work. Drilling-165mm Bore Well 0 to 90M | Drilling borewell | Drilling borewell | As per relevent standard specification | 336 | M | 30240
3 |  | 30 | Drill-165mm Bore Well 90M to 120M | Drilling borewell | Drilling borewell | As per relevent standard specification | 369 | M | 11070
4 |  | 30 | Drill-165mm Bore Well 120 M to 150M | Drilling borewell | Drilling borewell | As per relevent standard specification | 394 | M | 11820
5 |  | 30 | Drill-165mm Bore Well 150M to 180M | Drilling borewell | Drilling borewell | As per relevent standard specification | 492 | M | 14760
6 |  | 20 | Suppy & fixing of 180 mm dia. 6 kg/cm2 PVC casing pipe including cost and conveyance of all materials labour charges etc complete for finished item of work. | PVC Casing | PVC Casing | As per relevent standard specification | 883 | M | 17660
7 |  | 160 | Supply and fixing of HDPE pipe 40mm dia. including cost and conveyance of all materials labour charges etc complete for finished item of work. | HDPE Pipe | HDPE Pipe | As per relevent standard specification | 180 | M | 28800
8 |  | 1 | Supply and Fixing of 1.5HP Texmo/Kirloskar make motor of single phase submersible of multiple stage including all materials and labour charges complete for finished item. | 1.5HP submersbile pump | 1.5HP submersbile pump | As per relevent standard specification | 29047 | EA | 29047
9 |  | 215 | Supply and fixing of 2.5mm single core copper cable complete for finished item. | Copper cable | Copper cable | As per relevent standard specification | 192 | M | 41280
10 |  | 1 | Supply and Fixing of Flange Clamps including cost and conveyance of all materials | Flange Clamps | Flange Clamps | As per relevent standard specification | 182 | EA | 182
11 |  | 1 | Supply and erecting D.O.L Starter 250V, Single phase, 50Hz with SS enclouser comprising of contactor with bi-metallic relay with necessary push buttons, transportation and all labour charges etc. complete. | Single phase starter | Single phase starter | As per relevent standard specification | 1040 | EA | 1040
12 |  | 30 | Hiring of JCB for site levelling and cleaning | Hiring of JCB | Hiring of JCB | As per relevent standard specification | 2165 | H | 64950
13 |  | 254.1 | Earth Work Mass Excavation to a depth as directed, in soils such as Mixture of Gravel and Soft Disintegrated Rock like Shales, Ordinary Gravel, Stoney Earth and Earth Mixed with Fair Sized Boulders and in all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water (either sub soil water, storm water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete | Earth Work Mass Excavation | Earth Work Mass Excavation | As per relevent standard specification | 486 | M3 | 123492.6
14 |  | 11 | Back Filling the foundation Columns, for lift wells ,Staircase foundation ,U.G Sump Septic tank, Road work ,storm water drain ,cable trench,soak pit and outside of hte reataining wall with the useful avilable excavated earth ,in layers not exceeding 150mm thick, conslidating each deposited layer by eatering and ramming including cost and conveyance of all materials labour chargess,hire charges of T&P,all leads and lifts etc,complete for finished item of work | Back Filling | Back Filling | As per relevent standard specification | 34 | M3 | 374
15 |  | 42.8 | Providing and laying Plain Cement concrete of (1:4:8) for levelling course using 40mm size hard broaken Granite stone including cost and conveyance of all materials, se HBG metal for foundations and leveling course, including cost and conveyance of all materials,seignorage, water, labour charges, hire charges of nachinery, at all levels, depths,heights and floors consolidation by watering ,ramming in layers,bailing of water if any, and removal of form work after completion of work curing for reqired number of days,all incidental charges etc complete for finished item of work. | PCC (1:4:8) 40mm metal | PCC (1:4:8) 40mm metal | As per relevent standard specification | 4887 | M3 | 209163.6
16 |  | 6.8 | Providing and laying Plain Cement Concrete of (1:2:4) with well graded machine crushed granite metal of 20mm nominal size from approved quarry for Bed Blocks, Hold Fasts including cost and conveyance of all materials, labour charges,hire charges of machnery,with all leads and lifts, for all floors curing for required number of days, all incidental charges etc complete for finished item work | PCC (1:2:4) 20mm metal | PCC (1:2:4) 20mm metal | As per relevent standard specification | 6304 | M3 | 42867.2
17 |  | 248.5 | CRS masonry in CM(1:6) using Hard Granite Stones including cost and conveyance of all materials, seignorage charges, labour charge for construction and for dressing stones to required size and shape, dewatering,scaffolding,cutting for all leads and lifts, all incidental charges etc .complete for finished item of work | CRS Masonary | CRS Masonary | As per relevent standard specification | 5158 | M3 | 1281763
18 |  | 947.5 | Supplying and filling with borrowed gravel, watering, ramming, consolidating thoroughly complying with the standard specification including cost and conveyance of all materials, labour charges,hire charges of machnery,with all leads and incidental charges etc complete for finished item work | filling with gravel | filling with gravel | As per relevent standard specification | 640 | M3 | 606400
19 |  | 5.6 | Reinforced Cement concerete M20 GRADE Nominal Mix for footings , columns, Beams and Slab using 12mm to 20mm size graded HBG machine crushed metal from approvaed quary giving cube crushing strenth of 20 N /sqmm and a minimum of 400 kgs of cement for 1 cum of concrete including cost and conveyance charges for cement and all other materials to site, scaffolding charge , seignorage charges, centering, shuttering, machine mixing,laying concrete, curing for specified number of days vibrating etc compaction by pen vibrator or needle vibrator supplemented by hand spreeding rodding and tamping ,all incident and operational charges , all leads and lifts and for all leaving gaps and pockets etc complete, but excuding cost of ssteel and its fabrication,all incidental charges etc .complete for finshed item of workA)Ground floor a)Footings | RCC Footings | RCC Footings | As per relevent standard specification | 9357 | M3 | 52399.2
20 |  | 3.7 | b)Columns | RCC Columns | RCC Columns | As per relevent standard specification | 12579 | M3 | 46542.3
21 |  | 2.2 | c)Plinth beams | RCC Plinth beams | RCC Plinth beams | As per relevent standard specification | 12002 | M3 | 26404.4
22 |  | 2.8 | d)Roof beams | RCC Roof beams | RCC Roof beams | As per relevent standard specification | 11965 | M3 | 33502
23 |  | 0.6 | e)Lintels | RCC Lintels | RCC Lintels | As per relevent standard specification | 12573 | M3 | 7543.8
24 |  | 3.4 | f)Sun shade 0.6m width 3" thick | RCC Sunshades | RCC Sunshades | As per relevent standard specification | 1306 | M2 | 4440.4
25 |  | 16.8 | g)Slab | RCC Slab | RCC Slab | As per relevent standard specification | 11035 | M3 | 185388
26 |  | 146.7 | Brick masonry for wall in superstructure (230mm thick) in CM 1:6 using traditional Local madeSecound Class Bricks from approved sourse and quality having crushing strength of not less than 100 Kg/sq cm and water absorption not exceeding 20% by weight including cost and conveyance of all mateerials, seigniorage charge, all labour charges, curing for number of days as specified, for all leads, lifts scaffolding chargess, at all heght levels and floors all incidental charges etc completed item of work. A)Ground floor | Brick masonary | Brick masonary | As per relevent standard specification | 8182 | M3 | 1200299.4
27 |  | 2.6 | Providing High Yield Strength Deformed (HYSD)/ Thermo Mechanically Treated (TMT) / Mild steel (MS) steel bars (Fe 415/ Fe 500 grade as per IS 1786-1979) of different diameters for RCC works , including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying including sales and other taxes on all materials etc.,complete for finished item of work | HYSD Steel | HYSD Steel | As per relevent standard specification | 78657 | MT | 204508.2
28 |  | 1644.5 | Providing plastering of 20mm thick to all uneven faces of walls and ceiling of superstructure in two coats with base coat in CM 1:5of 16mm thick and top coat in Cm 1:3 4mm thick with dubara sponge finish including cost and conveyance of all materials . water. all labour charges, curing for specified number of days, cutting grooves, at allheghits, level and floro, all leads, lifts and scaffolding charges, all incidental and scaffolding charges, seigniorage charges, all incidental charges etc. complete for finished item of work A)Ground floor | Plastering 20mm thick | Plastering 20mm thick | As per relevent standard specification | 498 | M2 | 818961
29 |  | 607.4 | Raised pointing in CM(1:3) including curing, cost and conveyance of all materials and labour charges for complete item of work. | Raised pointing | Raised pointing | As per relevent standard specification | 113 | M2 | 68636.2
30 |  | 64.1 | Providing impervious coat over RCC roof slab surfaces to requried slopes with 20mm thick in CM 1:3 pro mixed with approved brand of water proofing compound as the rate of 1 kg per bag of cement including cost and conveyance of all materials, water, all labour charges, chemicals, curing for specifed number of days,rounding off junctions of wall and slab, all leads, lifts, heights,levels and floors etc.complete for finished item of work. | impervious coat | impervious coat | As per relevent standard specification | 524 | M2 | 33588.4
31 |  | 15 | Providing Reinforced cement Drop Walls in CM 1:2 of 40mm thick over rabbit wire mesh including cost and conveyance of all meterials, labour charges, curing for specified number of days,at all levels, floors, height, leads and lifts, seignioage charges all incidental charges etc . complete, but excluding cost of steel as per the approved drawing for finished item of work | RCM Drop Walls | RCM Drop Walls | As per relevent standard specification | 2953 | M2 | 44295
32 |  | 6 | Supply and fixing of doors with the frames of the door shall be made well seasoned MT wood of cross section 100x75mm. The shutter shall be made ISI mark flushed door with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary on both sides with 3 no 150mm hinges, 1 no door stoper, 1 no 250mm aldrop, 1 no 300 mm tower bolts, 2 no 150mm door handlers of MS Powder coated, including cost and conveyance of the meterials,fixing,labour carges,tools,handles,locking arrangementts and other fixtures & fittings for finished item work | MT Wood Doors Shutter with frame | MT Wood Doors Shutter with frame | As per relevent standard specification | 7314 | M2 | 43884
33 |  | 5.8 | S&F-UPVC Sliding Windows of approved make including cost and coveyance of all mateirals with all leads and lifts, labour charges, painting charges complete for finished item of work | UPVC Sliding Windows | UPVC Sliding Windows | As per relevent standard specification | 6063 | M2 | 35165.4
34 |  | 6.8 | Supplying and fixing of MS safety grill with peripheral frame of ISA 25x25x4mm and 8mm square rods at 100mm c/c both in horizontal & vertical direction including cost and coveyance of all mateirals with all leads and lifts, labour charges, painting charges complete for finished item of work | MS safety grill | MS safety grill | As per relevent standard specification | 2990 | M2 | 20332
35 |  | 3.7 | Flooring with ceramic tiles of 1st class quality of approved brand shade and design of different size laid over a floor bed of CM 1:3 of 12 mm thick base coat and neat grey cement slurry of honey like consistancy spread at the ratet of 3.3 kg of cement per sqm and pointed to full deapth, (joints must be flushed) with white cement paste mixed with pigment when requied including cost and conveyance of cement and all materials ,labour charges, at all levels, heights and floors,curing etc. complete for finished item of work. | ceramic tiles flooring | ceramic tiles flooring | As per relevent standard specification | 844 | M2 | 3122.8
36 |  | 14.4 | Providing skirting to internal walls to 15 cm height/risers of steps with ceramic tile length equal to floor tile, set over base coat of CM (1:3) 12 mm thick with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointed with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like Shahabad stone, cement, sand and water etc., complete for finished item of work | ceramic tiles dadoing | ceramic tiles dadoing | As per relevent standard specification | 979 | M2 | 14097.6
37 |  | 40 | #REF! | Polished Shabad stone flooring | Polished Shabad stone flooring | As per relevent standard specification | 730 | M2 | 29200
38 |  | 5.3 | #REF! | Polished Shabad stone Skirting | Polished Shabad stone Skirting | As per relevent standard specification | 808 | M2 | 4282.4
39 |  | 106 | Painting in all floors as specified with two coats of Plastic emulation paint of approved colour make and shade over one coat of white primer including cost and conveyance of all materials, labour charges at all leads, lifts, hights, levels and floors,all incidental charges etc. complete for finished item of work . | Plastic emulsion | Plastic emulsion | As per relevent standard specification | 155 | M2 | 16430
40 |  | 1452 | Painting to External Faces of walls(outside) in all floors as specified with two coats of ACE or equivalent quality paint of approved colour make and shade over one coat of white cement primer including cost and conveyance of all materials, labour charges at all leads, lifts, hights, levels and floors,all incidental charges etc. complete for finished item of work . | ACE painting | ACE painting | As per relevent standard specification | 259 | Sqm | 376068
41 |  | 2 | Conducting of DGPS & Total Staion Survey and Providing of maps including preparation of boundary and contour levels with 2 Nos hard copies and soft copies complete for finished items of work as directed by the Engineer in charge of the work. | Total Station Survey | Total Station Survey | As per relevent standard specification | 5000 | EA | 10000
42 |  | 67 | Supply&Spreading ofHBG metal 20 mm size of 80mm thick including cost&conveyance labour charges etc complete for finished item of work | 20mm HBG metal | 20mm HBG metal | As per relevent standard specification | 1672 | Cum | 112024
43 |  | 120 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 1") of 2.8mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) including cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work. | MS Security fencing | MS Security fencing | As per relevent standard specification | 2310 | Sqm | 277200
44 |  | 7.5 | Supply&Fixing of R.C.C hume pipe of 450 mm dia including cost & conveyance of all materials labour charges etc complete for finished item of work. | RCC hume pipes | RCC hume pipes | As per relevent standard specification | 1474 | Rmt | 11055
45 |  | 40 | Supply and fixing 25mm dia 1.5mm thick recessed( concealed) PVC pipe alog with reinforcement to be laid in slab including No 14 SWG GI wire for earth contunity, cost of pipe, binding wire and all labour charges etc complete | concealed PVC casing | concealed PVC casing | As per relevent standard specification | 97 | M | 3880
46 |  | 30 | Supplying and fixing of 25mm dia 1.5mm thick PVC conduit pipe conceald in wall with all required accessories with No 14 SWG wire for earth conitunity including chisiling the wall whereever necessary, including masonary work and all labour charges complete. | concealed PVC casing | concealed PVC casing | As per relevent standard specification | 108 | M | 3240
47 |  | 15 | Wiring with 2X1.0 Sqm(14/.3mm) PVC insulated flexiable copper cable in the existing metalic/Non metalic conduit pipe with 6A modular SP switch, mounted on metalic box covereds with appropriate front plate modules etc ceiling rose including cot and conveyance of all mateials, labour charges complete for light points, bell points exhaust fan points in non residential builsing except circuit moving finished in all types masonary as directed by department (Anchor Roma/GM/HAVELLS/FINOLEX) | light points | light points | As per relevent standard specification | 642 | EA | 9630
48 |  | 6 | Supplying and erection of approved make 6 Amps one modular SP switch with 6 Amps 6 pin mudular type plug socket mounted on metallic box covered with appropriate front plate as including all labour and material charges etc., complete for finished item of work. | 6 A sockets | 6 A sockets | As per relevent standard specification | 542 | EA | 3252
49 |  | 30 | supplying and run of 2 of 14/0.3 mm(1.0 sqmm) PVC insulated flexiable copper cable in existing conduit pipe for run of mains including all labour charges and materials chages etc. complete. (FINOLEX/HAVELS) | 1.0 sqmm wiring | 1.0 sqmm wiring | As per relevent standard specification | 56 | M | 1680
50 |  | 120 | supplying and run of 2 of 28/0.3 mm(2.5 sqmm) PVC insulated flexiable copper cable in existing conduit pipe for run of mains including all labour charges and materials chages etc. complete. (FINOLEX/HAVELS) | 2.5 sqmm wiring | 2.5 sqmm wiring | As per relevent standard specification | 103 | M | 12360
51 |  | 1 | Supply and fixing of 12 way SPN Distribution board with IP-20 protection suitable for single phase 40A DP Isolator/ELCB/RCCB as incomer and 10kA-6-32A SP MCBs 6Nos as out going including connections and all labour charges concealed in wall by chiseling and masonaqry work etc complete. | 12 way SPN Distribution | 12 way SPN Distribution | As per relevent standard specification | 6394 | EA | 6394
52 |  | 8 | Supply and erecting of approved make crom/bajaj make as directed by department 1x40W patty type fluorscent fitting made of CRCA sheet,completed with polyster filled 40W.choke,starter and side holders etc.complete with 40W tube all lobour charges etc complete (PHILIPS/CROMPTON) | tube lights | tube lights | As per relevent standard specification | 755 | EA | 6040
53 |  | 4 | Supply and fixing of batten holder/slanting holder in lieu of ceiling rose of light point complete with all connections and all labour charges with 11 to CF2 etc complete.(PHILIPS/CROMPTON) | batten holder | batten holder | As per relevent standard specification | 141 | EA | 564
54 |  | 2 | Supply and errection ceiling fan of selected colour and delux model high breeze with 3 blades and double ball bearing and with condenser AC 250 V 50 C/S of 48" 600 mm sweep completed erected in position with resistance type regulator, canopy down rod upto 304.8 mm in length is provided with hook/clamps nuts and bolts and 24/0.2 flexible copper wire etc.,complete and pointed with lettering by enamel paint the Sr.No and date of erection including cost and conveyance of all labour charges (Almonard/CG/Khaitan/Bajaj) and as per the direction of Engineer in charge. | ceiling fan | ceiling fan | As per relevent standard specification | 2277 | EA | 4554
55 |  | 2 | Supply and fixing of Electronic Regulator of Modular of GM / Legrand Myrius / L & T / North West / Indo Simon / ABB /Schneider ZEN celo including cost and conveyance of all labour charges and as per the direction of Engineer in charge. | Regulator for ceiling fan | Regulator for ceiling fan | As per relevent standard specification | 589 | EA | 1178
56 |  | 1 | Providing independent earthing for sophisticated equipment like computer, medical equipment electronic gadgets etc with 600X600X3.15mm thick copper plate rigidly fixed to the 40mm dia GI pipe 2.5m long pipe and 19mm dia B class GI pipe of .3 mts long connectd with reducer providing of stggred holes of 16 Nos of 12 mm dia to earth electrode, enclosed in in a CC chamber of (400X400X400) mm with suitable reinforced RCC slab cover duly filling with betonite powder and clay in (1:6) prop from bottom of pipe to bottom of CC chamber giving earth connection from the electrode throuh necessary GI strip of 25X6X200 mm length provided with suitable size o 14 Nos holes GI washers nuts and bolts and all labour charges etc complete. | earthing | earthing | As per relevent standard specification | 5345 | EA | 5345
57 |  | 40 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)a)15.90mm OD Pipe - SDR 11 | 15.90mm OD CPVC pipes & fittings | 15.90mm OD CPVC pipes & fittings | As per relevent standard specification | 239 | M | 9560
58 |  | 80 | b) 22.20mm OD Pipe - SDR 11 | 22.20mm OD CPVC pipes & fittings | 22.20mm OD CPVC pipes & fittings | As per relevent standard specification | 313 | M | 25040
59 |  | 90 | c) 28.60mm OD Pipe - SDR 11 | 28.60mm OD CPVC pipes & fittings | 28.60mm OD CPVC pipes & fittings | As per relevent standard specification | 410 | M | 36900
60 |  | 20 | S & F Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type a) 20 mm NB Size | 20mm Ball valve | 20mm Ball valve | As per relevent standard specification | 331 | EA | 6620
61 |  | 2 | b) 25 mm NB Size | 25mm Ball valve | 25mm Ball valve | As per relevent standard specification | 466 | EA | 932
62 |  | 20 | Supply and Fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand including cost and conveyance, labour charges of all materials etc. complete for finished item of work. | 110mm PVC/SWR pipe | 110mm PVC/SWR pipe | As per relevent standard specification | 462 | M | 9240
63 |  | 2 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) including cost and conveyance, labour charges of all materials etc. complete for finished item of work. | 110mm PVC/SWR Plain bend | 110mm PVC/SWR Plain bend | As per relevent standard specification | 96 | EA | 192
64 |  | 2 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) including cost and conveyance, labour charges of all materials etc. complete for finished item of work. | 110mm PVC/SWR door bend | 110mm PVC/SWR door bend | As per relevent standard specification | 128 | EA | 256
65 |  | 2 | Supply & fixing of Floor Trap (Bell Mouth ) 110 mm - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) including cost and conveyance, labour charges of all materials etc. complete for finished item of work. | 110mm PVC/SWR floor trap | 110mm PVC/SWR floor trap | As per relevent standard specification | 269 | EA | 538
66 |  | 2 | Supply&fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) including cost and conveyance, labour charges of all materials etc. complete for finished item of work. | 4" Nahany trap | 4" Nahany trap | As per relevent standard specification | 134 | EA | 268
67 |  | 1 | Constructing 457.2 mm x 457.2 mm (1'6"x1'6") brick in CM 1:6 prop. Masonry. Inspection chamber up to 914.4 mm (3'0") and fitted with light weight 457.2 mm x 457.2 mm (1'6"x1'6") C.I frame and cover of 20 Kg. | (1'6"x1'6") brick inspection chamber | (1'6"x1'6") brick inspection chamber | As per relevent standard specification | 4610 | EA | 4610
68 |  | 1 | Supplying and Fixing European Water Closet of 1st quality conforming to IS:2556-Part-2-1973 of Hindustan / Neycer or Parryware make white glazed with 'S' trap including cost and conveyance, labour charges etc complete. | European Water Closet | European Water Closet | As per relevent standard specification | 2228 | EA | 2228
69 |  | 2 | Supplying and fixing of best indian make plastic seat and lid for European water closets and buffers as per IS 2548-1963 | plastic seat and lid for EWC | plastic seat and lid for EWC | As per relevent standard specification | 1324 | EA | 2648
70 |  | 2 | Supply and fixing of PV low level system parryware/slim line with internal component and short bend of 10 lits capacity with choice color etc., complete. | PVC low level tank | PVC low level tank | As per relevent standard specification | 2032 | EA | 4064
71 |  | 2 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Hand wash basin | Hand wash basin | As per relevent standard specification | 1717 | EA | 3434
72 |  | 2 | Suplying and fixing of angle stop cock 12.7mm dia fisrt quality indian make seiko or equivalent. | 12.7mm stop cock | 12.7mm stop cock | As per relevent standard specification | 721 | EA | 1442
73 |  | 2 | Suplying and fixing of bib tap 12.7mm dia fisrt quality indian make seiko or equivalent. | 12.7mm bib tap | 12.7mm bib tap | As per relevent standard specification | 298 | EA | 596
74 |  | 1000 | Providing and placing on terrace (at all floor levels) Sintex /Aqua tech or equivalent Polyethylene water storage tank double layer conforming to ISI 12701/96 mark with lid and suitable locking arraqngments and making necessary holes for inlet and outleta and over flow pipes labour charges etc complete for finished item of work. | PVC Sintex tank | PVC Sintex tank | As per relevent standard specification | 10 | L | 10000
75 |  | 1 | Suplying and fixing of 31.75mm PVC waste pipe for wash basin including cost and conveyance of all materials and labour charges et complete | PVC waste pipe | PVC waste pipe | As per relevent standard specification | 33 | EA | 33
76 |  | 1 | Supplying and fixing of TV shape mirror with plastic size 609mmX 457.2 m | TV shape mirror | TV shape mirror | As per relevent standard specification | 564 | EA | 564
77 |  | 1 | Constructing 1220.0 mm (4’0”) dia Septic tank with CC collars/rings including excavating pit up to a depth of 1800 mm (6'-0") in all sorts of soils (excluding rock), laying cement concrete (1:4:8) 150 mm thick using 40mm HBG Metal, Plastering 20mm thick for jointing CC collars and Providing M-20(Nominal mix) grade 3" thick RCC cover and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site and all incidental and operational, labour charges etc., complete for finished item of work as directed by the Engineer in charge. | 4’0” dia Septic tank | 4’0” dia Septic tank | As per relevent standard specification | 8215 | EA | 8215
78 |  | 1 | Constructing 1220.0 mm (4’0”) dia Soak pit with reinforced brick masonary(honey-comb wall) including excavating pits up to a depth of 1500 mm (5'-0") in all sorts of soils (excluding rock) as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site and all incidental and operational, labour charges etc., complete for finished item of work as as directed by the Engineer in charge. | 4’0” dia Soak pit | 4’0” dia Soak pit | As per relevent standard specification | 5560 | EA | 5560
79 |  | 1 | Supply of steel table of size 4'x2.'x30" with 18 mm plywood fixed with rubber beeding with drawers on right side with automatic locking arrangements etc copmlete. | steel table | steel table | As per relevent standard specification | 7800 | Each | 7800
80 |  | 2 | supply of 'S' type chair with arms teakwood frame with seat back 's' type on G.I pipe.(Make: Godraj) | S type chairs | S type chairs | As per relevent standard specification | 3650 | Each | 7300
81 |  | 2 | Supply of P V C chairs of approved quality & make incldg cost etc complete | PVC Chairs | PVC Chairs | As per relevent standard specification | 1150 | Each | 2300
82 |  | 2.7 | S&F Glow Sign Board | Name boards | Name boards | As per relevent standard specification | 3553 | Sqm | 9593.1
83 |  | 1.62 | Supply and Fixing of Substation name board of size 6'x3' iron sheet with angle frame and channel supports of size 75x40mm, 8' height including concreting of channel supports and painting with enamel paint complete. | Name boards | Name boards | As per relevent standard specification | 4326 | Sqm | 7008.12
84 |  | 82.29 | Seigniorage Charges - Sand | Seigniorage Charges | Seigniorage Charges |  | 40 | M3 | 3291.6
85 |  | 82.29 | Seigniorage Charges -M Sand | Seigniorage Charges | Seigniorage Charges |  | 97.5 | M4 | 8023.275
86 |  | 413.75 | Seigniorage Charges - Metal | Seigniorage Charges | Seigniorage Charges |  | 97.5 | M3 | 40340.625
87 |  | 947.5 | Seigniorage Charges - Garvel | Seigniorage Charges | Seigniorage Charges |  | 30 | M3 | 28425
|  |  | Net-Total |  |  |  | Civil total |  | 6504417.62
[7 empty] | Electrical & Civil total |  | 23970862.7818